SECTION 01514 - NEGATIVE PRESSURE ENCLOSURE - LEAD-BASED PAINT

PART

1  - GENERAL

1.1	RELATED DOCUMENTS:

A.	Drawings and general provisions of the Contract, including

General and Supplementary Conditions and other Division-1 Specification Sections, apply to work of this section.

B.	Heating and cooling requirements are set forth in Section 01504 Construction Facilities and Temporary Controls - Lead Based Paint.

1.2	MONITORING

A.	Continuously monitor and record the pressure differential between the Work Area and the building outside of the Work Area with a monitoring device incorporating a continuous recorder such as a strip chart or other graphic recorder.

1.3	SUBMITTALS

A.	Before Start of Work:  Submit design of pressure differential system to the Designer for review.  Do not begin work until submittal is returned with the Designer's action stamp indicating that the submittal is returned for unrestricted use.  Include in the submittal at a minimum:

1.	Number of HEPA filtered fan units required and the calculations necessary to determine the number of machines

2.	Description of projected air flow within Work Area and methods required to provide adequate air flow in all portions of the work area

3.	Anticipated pressure differential across Work Area enclosures

4.	Description of methods of testing for correct air flow and pressure differentials

5.	Manufacturer's product data on the HEPA filtered fan units to be used

6.	Location of the machines in the Work Area

7.	Method of supplying adequate power to the machines and designation of building electrical panel(s) which will be supplying the power

8.	Description of work practices to insure that airborne dust travels away from workers

9.	Manufacturer's product data on equipment used to monitor pressure differential between inside and outside of Work Area

10.	Manufacturer's product data on auxiliary generator to be used

11.	Manufacturer's product data on auxiliary power switch to be used

12.	Schematic diagram of power and auxiliary power supply to  HEPA filtered fan units

B.	On a weekly basis:  Submit printout from pressure differential monitoring equipment.  Mark printout with date and start of time for each day.  Use printout paper that indicates elapsed time in intervals no greater than hours.  Indicate on each day=s record times of starting and stopping abatement work, type of work in progress, breaks for lunch or other purposes, periods of stop work, and filter changes.  Cut printout into segments by day, attach to 8 2" by 11" paper.  Label with project name, contractors name and date.

1.4	QUALITY ASSURANCE:

A.	Monitor pressure differential at Personnel and Equipment Decontamination Units with a differential pressure meter equipped with a continuous recorder.  Meter shall be equipped with a warning buzzer which will sound if pressure differential drops below 0.01" of water (2.49 Pa).

PART 2 - PRODUCTS

2.1	HEPA FILTERED FAN UNITS:

A.	General: Supply the required number of HEPA filtered fan units to the site in accordance with these specifications.  Use units that meet the following requirements.

B.	Cabinet: Constructed of durable materials able to withstand damage from rough handling and transportation.  The width of the cabinet should be less than 30 inches to fit through standard-size doorways.  Provide units whose cabinets are:

1.	Factory-sealed to prevent lead dust from being released during use, transport, or maintenance

2.	Arranged to provide access to and replacement of all air filters from intake end

3.	Mounted on casters or wheels

C.	Fans:  Rate capacity of fan according to usable air-moving capacity under actual operating conditions.

D.	HEPA Filters:  Provide units whose final filter is the HEPA type with the filter media (folded into closely  pleated panels) completely sealed on all edges with a  structurally rigid frame.

1.	Provide units with a continuous rubber gasket located between the filter and the filter housing to form a tight seal.

2.	Provide HEPA filters that are individually  tested and certified by the manufacturer to have  an efficiency of not less than 99.97 percent when challenged with  0.3 um dioctylphthalate (DOP) particles when tested in accordance with Military Standard Number 282 and Army  Instruction Manual 136-300-175A.  Provide filters that bear a UL586 label to indicate ability to perform under specified conditions.

3.	Provide filters that are marked with: the name of the manufacturer, serial number, air flow rating, efficiency and resistance, and the direction of test air flow.

E.	Prefilters, which protect the final filter by removing the larger particles, are required to prolong the operating life of the HEPA filter.  Two stages of prefiltration are required.  Provide units with the following prefilters:

1.	First-stage prefilter: low-efficiency type (e.g., for particles 100 um and larger)

2.	Second-stage (or intermediate) filter:  medium efficiency (e.g., effective for particles down to 5 um)

F.	Provide units with prefilters and intermediate filters installed either on or in the intake grid of the unit and held in place with special housings or clamps.

G.	Instrumentation:   Provide units equipped with:

1.	Manometer to measure the pressure drop across filters and indicate when filters have become loaded and need to be changed

2.	A table indicating the usable air-handling capacity for various static pressure readings on the manometer affixed near the gauge for reference, or the manometer reading indicating at what point the filters should be changed, noting Cubic Feet per Minute (CFM) air delivery at that point

3.	Elapsed time meter to show the total accumulated hours of operation

H.	Safety and Warning Devices:  Provide units with the following safety and warning devices:

1.	Electrical (or mechanical) lockout to prevent fan from operating without a HEPA filter

2.	Automatic shutdown system to stop fan in the event of a rupture in the HEPA filter or blocked air discharge

3.	Warning lights to indicate normal operation (green), too high a pressure drop across the filters (i.e., filter overloading) (yellow), and too low of a pressure drop (i.e., rupture in HEPA filter or obstructed discharge) (red)

4.	Audible alarm if unit shuts down due to operation of safety systems

I.	Electrical components:  Provide units with electrical components approved by the National Electrical Manufacturers Association (NEMA) and Underwriter's Laboratories (UL).  Each unit is to be equipped with overload protection sized for the equipment.  The motor, fan, fan housing, and cabinet are to be grounded.

J.	Manufacturers:  Subject to compliance with requirements, manufacturers offering products which may be incorporated in the work include, but are not limited to, the following:

K.	Manufacturer:  Subject to compliance with requirements, provide products of the following:

2.2	AUXILIARY GENERATOR:

A.	Auxiliary Generator:  Provide a gasoline-powered self-starting generator with the capacity to power at least 2 or  50% (whichever is greater) of the HEPA filtered fan units in operation at any time during the work.

B.	Auxiliary Power Switch:  Provide a switching relay which will automatically start auxiliary generator and switch over power supplied to HEPA filtered fan units to auxiliary generator.

PART 3 - EXECUTION

3.1	PRESSURE DIFFERENTIAL ISOLATION

A.	Isolate the Work Area from all adjacent areas or systems of the building with a Pressure Differential that will cause a movement of air from outside to inside at any breach in the physical isolation of the Work Area.

B.	Relative Pressure in Work Area:  Continuously maintain the work area at an air pressure that is lower than that in any surrounding space in the building, or at any location in the immediate proximity outside of the building envelope. This pressure differential when measured across any physical or critical barrier must equal or exceed a static pressure of:

1.	0.01 inches of water (2.49 Pa).

2.	0.02 inches of water (4.98 Pa).

3.	0.03 inches of water (7.47 Pa).

4.	0.04 inches of water (9.96 Pa).

5.	0.05 inches of water (12.45 Pa).

6.	0.10 inches of water (24.9 Pa).

C.	Accomplish the pressure differential by exhausting a sufficient number of HEPA filtered fan units from the work area.  The number of units required will depend on machine characteristics, the seal at barriers, and required air circulation. The number of units will increase with increased make-up air or leaks into the Work Area.  Determine the number of units required for pressure isolation by the following procedure:

1.	Establish required air circulation in the work area, personnel and equipment decontamination units.

2.	Begin operation of any positive pressure seals that are going to be used.  Establish the elevated pressure in any adjacent area that are going to be maintained at a higher pressure.

3.	Exhaust a sufficient number of units from the work area to develop the required pressure differential.

D.	The required number of units is the number determined above plus one additional unit.

E.	Vent HEPA filtered fan units to outside of building unless authorized in writing by Designer.

F.	Vent each HEPA filtered fan unit to inlet of second unit.  Vent second unit to a controlled area in the building.  Insure that controlled area is isolated from balance of building by critical barriers at all times that units are in operation.

1.	Mount units to exhaust directly or through disposable ductwork.

2.	Use only new ductwork except for sheet metal connections and elbows.

3.	Use ductwork and fittings of same diameter or larger than discharge connection on fan unit.

4.	Use inflatable, disposable plastic ductwork in lengths not greater than 100 feet.

5.	Use spiral wire-reinforced flex duct in lengths not greater than 50 feet.

6.	Arrange exhaust as required to inflate duct to a rigidity sufficient to prevent flapping.

7.	If direction of discharge from fan unit is not aligned with duct use sheet metal elbow to change direction.  Use six feet of spiral wire reinforced flex duct at each direction change.

G.	Isolation of elevators, stair towers, and return air intakes:  Erect seals with an air space at doors to elevators and stair towers.  Pressurize this space with clean or outside air or air that has been filtered by a HEPA filter so that it is at a pressure greater than either the Work Area elevator shaft or stair tower.

1.	Fabricate seal by first sealing door with duct tape and 6 mil polyethylene.  Construct a barrier from 2" (13mm) gypsum board supported by 3-5/8" (92mm) 25 gauge metal studs at 16" (408mm) on centers.  Space face of barrier a minimum of 3" (76mm) from face of door.  Seal barrier with flame resistant 6 mil sheet plastic and duct tape.

2.	Fabricate seal by first sealing door with duct tape and 6 mil polyethylene.  Construct a barrier from 2" (13mm) CDX plywood supported by 2" X 4" (51 x 102mm) wood studs at 16" (408mm) on centers.  Space face of barrier a minimum of 3" (76mm) from face of door.  Seal barrier with 6 mil sheet plastic and duct tape.

a.	Use plywood and framing lumber that is treated to be fire resistant.

3.	Pressurize space with clean air from outside the work area with a small fan (such as a bathroom exhaust fan) or a HEPA filtered fan unit.  Continuously maintain a pressure differential with this space a minimum of 0.02 inches of water (4.98 Pa) higher in static pressure than any adjacent space.

4.	Locate exhaust fan or HEPA filtered fan unit outside of work area.  Fabricate a manifold as required to distribute air to individual spaces to be isolated.  Provide relief venting at unit as required to prevent shut down due to low air flow while still maintaining required air pressure.

H.	Isolation of chases and enclosed stairs:  Pressurize chases and enclosed stairs with air filtered through a HEPA filter so that chase is at a pressure greater than any adjacent work area.

1.	Pressurize space with clean or outside air with a small fan (such as a bathroom exhaust fan) or with a HEPA filtered fan unit.  Continuously maintain a pressure differential with this space a minimum of 0.02 inches of water higher in static pressure than any adjacent work area.

I.	Isolation of chases and enclosed stairs:  Pressurize chases and enclosed stairs so that they are at a pressure greater than any adjacent work area.

1.	Pressurize space with centrifugal-type fans.  Axial type fans are not to be used for this purpose.  Continuously maintain a pressure differential in this space a minimum of 0.02 inches of water (4.98 Pa) higher in static pressure than any adjacent work area.

J.	Isolation of return air ductwork:  Return air duct work which must be kept operating is located in the Work Area.  This duct work is to be isolated from the Work Area by an enclosure forming an annular space around the duct which is positively pressurized with HEPA filtered air.

1.	Wrap the duct with 6 mil polyethylene.  Seal all polyethylene seams with spray glue and duct tape.

2.	Enclose wrapped duct with two separate layers of polyethylene that form a continuous space around duct.  Fabricate inner layer from 6 mil polyethylene with all seams sealed with spray glue and duct tape.  Arrange outer layer to support inner layer.  Fabricate out of reinforced sheet plastic with seams sealed with spray glue and duct tape and reinforced with staples.  Support outer layer with a frame work fabricated from 2" x 4"s (51 x 102mm) at 24" (610mm) on center.  Enclosures less than 2'-6' (762mm) in diameter may be reinforced with box strapping in lieu of wood framing.

3.	Pressurize space with clean air from outside the work area with a small fan (such as a bathroom exhaust fan) or a HEPA filtered fan unit.  Continuously maintain a pressure differential with this space a minimum of 0.02 inches of water (4.98 Pa) higher in static pressure than any adjacent space.

4.	Locate exhaust fan or HEPA filtered fan unit outside of work area.  Fabricate a manifold as required to distribute air to individual spaces to be isolated.  Provide relief venting at unit as required to prevent shut down due to low air flow while still maintaining required air pressure.

3.2	AUXILIARY GENERATOR

A.	Provide auxiliary gasoline-powered generator located outside of the building in a location protected from the weather.  Arrange so that if a power failure occurs the generator automatically starts and supplies power to at least 2 or 50% (whichever is greater) of the total number of HEPA filtered fan units in operation.

3.3	AIR CIRCULATION IN THE WORK AREA:

A.	Air Circulation:  For purposes of this section air circulation refers to either the introduction of outside air to the Work Area or the circulation and cleaning of air within the Work Area.

B.	Air circulation in the Work Area is a minimum requirement intended to help maintain airborne dust levels that do not significantly challenge the work area isolation measures.  The Contractor may also use this air circulation as part of the engineering controls in his worker protection program.

C.	Determining the air circulation requirements:  Provide a fully operational air circulation system supplying a minimum of the following air circulation rate:

1.	4 air changes per hour

2.	12 air changes per hour

3.	20 air changes per hour

D.	Determine number of units needed to achieve required air circulation according to the following procedure:

1.	Determine the volume of the work area in cubic feet by multiplying floor area by ceiling height.  Determine total air circulation requirement in cubic feet per minute (CFM) for the work area by multiplying this volume by the air change rate and dividing by 60.

2.	Calculate air circulation required in cubic feet of air per minute (CFM) by the following formula:

CFM required = Volume of work area (cu. ft.) X   Number of air changes per hour     									     60 (minutes per hour)

3.	Divide the air circulation requirement (CFM) above by capacity of HEPA filtered fan unit(s) used.  Capacity of a unit for purposes of this section is the capacity in cubic feet per minute with fully loaded filters (pressure differential which causes loaded filter warning light to come on) in the machine's labeled operating characteristics.

Number of Units Needed =        air circulation requirement(CFM)

Capacity of Unit with Loaded Filters

4.	Add one (1) additional unit as a backup in case of equipment failure or machine shutdown for filter changing.

3.4	EXHAUST SYSTEM:

A.	Pressure differential isolation and air circulation in the Work Area are to be accomplished by an exhaust system as described below.

B.	Exhaust all units from the Work Area to meet air circulation requirement of this section.

C.	Location of HEPA Filtered Fan Units:   Locate fan unit(s) so that makeup air enters work area primarily through decontamination facilities and traverses Work Area as much as possible.  This may be accomplished by positioning the HEPA filtered fan unit(s) at a maximum distance from the worker access opening or other makeup air sources.

D.	Place end of unit, its intake duct or its exhaust duct through an opening in the plastic barrier or wall covering.  Seal plastic around the unit or duct with tape.

E.	Vent to outside of building, unless authorized in writing by the Designer.

F.	Decontamination Units:  Arrange Work Area and decontamination units so that the majority of make up air comes through the Decontamination Units.  Use only personnel or equipment Decontamination Unit at any time and seal the other so that make up air passes through unit in use.

G.	Supplemental Makeup Air Inlets:  Provide where required for proper air flow through the Work Area in location approved by the Designer by making openings in the plastic sheeting that allow air from outside the building into the Work Area.  Locate auxiliary makeup air inlets as far as possible from the fan unit(s) (e.g., on an opposite wall), off the floor (preferably near the ceiling), and away from barriers that separate the Work Area from occupied clean areas.  Cover with flaps to reseal automatically if the pressure differential system should shut down for any reason.  Spray flap and around opening with spray adhesive so that if flap closes meeting surfaces are both covered with adhesive.  Use adhesive that forms contact bond when dry.

3.5	RECIRCULATION SYSTEM:

A.	Pressure differential isolation and air circulation in the Work Area are to be accomplished by a recirculation system as described below.

B.	Recirculate air in the Work Area through HEPA filtered fan units to accomplish air circulation requirements of this section.

C.	Location of Fan Units:  Locate HEPA filtered fan units so that air is circulated through all parts of the Work Area, and so that required pressure is maintained at all parts of Work Area geometry.  Move units as necessary so that in any location where lead-based paint is being disturbed, the discharge from one HEPA filtered fan unit is blowing contamination away from workers.  Direct air flow in these locations so that it is predominantly toward workers' backs at the breathing zone elevation.

3.6	AIR CIRCULATION IN DECONTAMINATION UNITS:

A.	Pressure Differential Isolation:  Continuously maintain the pressure differential required for the work area in the:

1.	Personnel Decontamination Unit:  Across the Shower Room with the Equipment Room at a lower pressure than the Clean room.

2.	Equipment Decontamination Unit:  Across the Holding Room with the Wash Room at a lower pressure than the Clean Room.

B.	Air Circulation:  Continuously maintain air circulation in Decontamination Units at same level as required for Work Area.

C.	Air Movement:  Arrange air circulation through the Personnel Decontamination Unit so that it produces a movement of air from the Clean Room through the Shower Room into the Equipment Room.  Maintain continuous minimum velocities of Sixty (60) feet per minute (0.305 m/s) in the breathing zone area of the shower and thirty (30) feet per minute (0.15 m/s) in all other locations of the shower.

3.7	USE OF THE PRESSURE DIFFERENTIAL AND AIR CIRCULATION SYSTEM:

A.	General:  Each unit shall be serviced by a dedicated minimum  115V-20A circuit with ground fault circuit interrupter (GFCI) supplied from temporary power supply installed under requirements of Section 01504 "Construction Facilities & Temporary Controls."  Do not use existing branch circuits to power fan units.

B.	Testing the System:   Test pressure differential system before any lead-based paint is disturbed.  After the Work Area has been prepared, the decontamination facility set up, and the fan unit(s) installed, start the unit(s) (one at a time).  Demonstrate operation and testing of pressure differential system to Designer.

C.	Demonstrate condition of equipment for each HEPA filtered fan unit and pressure differential monitoring equipment including proper operation of the following:

1.	Squareness of HEPA Filter;

2.	Condition of seals;

3.	Proper operation of all lights;

4.	Proper operation of automatic shut down if exhaust is blocked;

5.	Proper operation of alarms;

6.	Proper operation of manometer ;

7.	Proper operation and calibration of pressure monitoring equipment.

D.	Demonstrate Operation of the pressure differential system to the Designer.  This demonstration is to include, but is not be limited to, the following:

1.	Plastic barriers and sheeting move lightly in toward Work Area;

2.	Curtain of decontamination units move lightly in toward Work Area;

3.	There is a noticeable movement of air through the Decontamination Unit;

4.	Use smoke tube to demonstrate air movement from Clean Room through Shower Room to Equipment Room;

5	Use smoke tubes to demonstrate a definite motion of air across all areas in which work is to be performed;

6	Use a differential pressure meter or manometer to demonstrate the required pressure differential at every barrier separating the Work Area from the balance of the building, equipment, ductwork or outside;

7	Modify the Pressure Differential System as necessary to demonstrate successfully the above.

E0	Use of System During Abatement Operations:

1	Start fan units before beginning work (before any lead-based paint is disturbed).  After abatement work has begun, run units continuously to maintain a constant pressure differential and air circulation until decontamination of the work area is complete.  Do not turn off units at the end of the work shift or when abatement operations temporarily stop.

2	Do not shut down air  pressure differential system during encapsulating procedures, unless authorized by the Designer in writing.  Supply sufficient pre-filters to allow frequent changes.

3	Start abatement work at a location farthest from the fan units and proceed toward them.  If an electric power failure occurs, immediately stop all abatement work and do not resume until power is restored and fan units are operating again.

4	At completion of abatement work, allow fan units to run as specified under section 01711, to remove airborne dust that may have been generated during abatement work and cleanup and to purge the Work Area with clean makeup air.  The units may be required to run for a longer time after decontamination, if very finely divided lead dust was generated by the work

F0	Dismantling the System:

1	When a final inspection and the results of final air tests indicate that the area has been decontaminated, fan units may be removed from the Work Area.  Before removal from the Work Area, remove and properly dispose of pre-filter, decontaminate exterior of machine and seal intake to the machine with 6 mil polyethylene to prevent environmental contamination from the filters.  Wrap entire machine including unit housing, caster wheels, instrument face, etc. in 6 mil plastic.

END OF SECTION  - 01514