SECTION 27 05 33  
RACEWAYS AND BOXES FOR COMMUNICATIONS SYSTEMS

SPEC WRITER NOTES:

1. Edit this specification section between //\_\_\_\_//, to fit project, or delete if not applicable.

2. Contact VA’s AHJ, Spectrum Management and COMSEC Service (SMCS 005OP2H3), (202-461-5310) for all technical assistance.

3. Included throughout this specification are references to system’s interface capability and various related features. System designer must verify availability of this system and coordinate associated requirements and subsequent interfaces.

1. GENERAL
   1. DESCRIPTION
      1. This section specifies conduit, fittings, and boxes to form complete, coordinated, raceway systems. Raceways are required for communications cabling unless shown or specified otherwise.
   2. RELATED WORK
      1. Bedding of conduits: Section 31 20 00, EARTH MOVING.
      2. Mounting board for Telecommunication Rooms: Section 06 10 00, ROUGH CARPENTRY.
      3. Sealing around penetrations to maintain integrity of fire rated construction: Section 07 84 00, FIRESTOPPING.
      4. Fabrications for deflection of water away from building envelope at penetrations: Section 07 60 00, FLASHING AND SHEET METAL.
      5. Sealing around conduit penetrations through building envelope to prevent moisture migration into building: Section 07 92 00, JOINT SEALANTS.
      6. Identification and painting of conduit and other devices: Section 09 91 00, PAINTING.
      7. Requirements for personnel safety and to provide a low impedance path for possible ground fault currents: Section 27 05 26, GROUNDING AND BONDING FOR COMMUNICATIONS SYSTEMS.
   3. SUBMITTALS
      1. In accordance with Section 27 50 11, REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS, submit the following:
         1. Size and location of cabinets, splice boxes and pull boxes.
         2. Layout of required conduit penetrations through structural elements.
         3. Catalog cuts marked with specific item proposed and area of application identified.
      2. Certification: Provide letter prior to final inspection, certifying material is in accordance with construction documents and properly installed.
2. PRODUCTS
   1. MATERIAL

SPEC WRITER NOTE:

1. Coordinate with Section 27 10 00, STRUCTURED CABLING.

* + 1. Minimum Conduit Size: 19 mm (3/4 inch).
    2. Conduit:
       1. Rigid Galvanized Steel: Conform to UL 6, ANSI C80.1.
       2. Rigid Aluminum: Conform to UL 6A, ANSI C80.5.
       3. Rigid Intermediate Steel Conduit (IMC): Conform to UL 1242, ANSI C80.6.
       4. Electrical Metallic Tubing (EMT):
          1. Maximum Size: 105 mm (4 inches).
          2. Install only for cable rated 600 volts or less.
          3. Conform to UL 797, ANSI C80.3.
       5. Flexible Galvanized Steel Conduit: Conform to UL 1.
       6. Liquid-tight Flexible Metal Conduit: Conform to UL 360.
       7. Direct Burial Plastic Conduit: Conform to UL 651 and UL 651A, heavy wall PVC, or high density polyethylene (HDPE).
       8. Surface Metal Raceway: Conform to UL 5.
       9. Wireway, Approved “Basket”: Provide "Telecommunications Service” rated with approved length way partitions and cable straps to prevent wires and cables from changing from one partitioned pathway to another.
    3. Conduit Fittings:
       1. Rigid Galvanized Steel and Rigid Intermediate Steel Conduit Fittings:
          1. Provide fittings meeting requirements of UL 514B and ANSI/ NEMA FB 1.
          2. Sealing: Provide threaded cast iron type. Use continuous drain type sealing fittings to prevent passage of water and vapor. In concealed work, install sealing fittings in flush steel boxes with blank cover plates having same finishes as other electrical plates in room.
          3. Standard Threaded Couplings, Locknuts, Bushings, and Elbows: Only steel or malleable iron materials are acceptable. Integral retractable type IMC couplings are also acceptable.
          4. Locknuts: Bonding type with sharp edges for digging into metal wall of an enclosure.
          5. Bushings: Metallic insulating type, consisting of an insulating insert molded or locked into metallic body of fitting. Bushings made entirely of metal or nonmetallic material are not permitted.
          6. Erickson (union-type) and Set Screw Type Couplings:

Couplings listed for use in concrete are permitted for use to complete a conduit run where conduit is installed in concrete.

Use set screws of case hardened steel with hex head and cup point to seat in conduit wall for positive ground. Tightening of set screws with pliers is prohibited.

* + - * 1. Provide OEM approved fittings.
      1. Rigid Aluminum Conduit Fittings:
         1. Standard Threaded Couplings, Locknuts, Bushings, and Elbows: Malleable iron, steel or aluminum alloy materials; Zinc or cadmium plate iron or steel fittings. Aluminum fittings containing more than 0.4 percent copper are not permitted.
         2. Locknuts and Bushings: As specified for rigid steel and IMC conduit.
         3. Set Screw Fittings: Not permitted for use with aluminum conduit.
      2. Electrical Metallic Tubing Fittings:
         1. Conform to UL 514B and ANSI/ NEMA FB1; only steel or malleable iron materials are acceptable.
         2. Couplings and Connectors: Concrete tight and rain tight, with connectors having insulated throats.

Use gland and ring compression type couplings and connectors for conduit sizes 50 mm (2 inches) and smaller.

Use set screw type couplings with four set screws each for conduit sizes over 50 mm (2 inches).

Use set screws of case-hardened steel with hex head and cup point to seat in wall of conduit for positive grounding.

* + - * 1. Indent type connectors or couplings are not permitted.
        2. Die-cast or pressure-cast zinc-alloy fittings or fittings made of "pot metal" are not permitted.
        3. Provide OEM approved fittings.
      1. Flexible Steel Conduit Fittings:
         1. Conform to UL 514B; only steel or malleable iron materials are acceptable.
         2. Provide clamp type, with insulated throat.
         3. Provide OEM approved fittings.
      2. Liquid-tight Flexible Metal Conduit Fittings:
         1. Conform to UL 514B and ANSI/ NEMA FB1; only steel or malleable iron materials are acceptable.
         2. Fittings must incorporate a threaded grounding cone, a steel or plastic compression ring, and a gland for tightening.
         3. Provide connectors with insulated throats to prevent damage to cable jacket.
         4. Provide OEM approved fittings.
      3. Direct Burial Plastic Conduit Fittings: Provide fittings meeting requirements of UL 514C and NEMA TC3, and as recommended by conduit manufacturer.
      4. Surface Metal Raceway: Conform to UL 5 and “telecommunications service” rated with approved length-way partitions and cable straps to prevent wires and cables from changing from one partitioned pathway to another.
      5. Surface Metal Raceway Fittings: As recommended by raceway manufacturer.
      6. Expansion and Deflection Couplings:
         1. Conform to UL 467 and UL 514B.
         2. Accommodate 19 mm (3/4 inch) deflection, expansion, or contraction in any direction, and allow 30 degree angular deflections.
         3. Include internal flexible metal braid sized to ensure conduit ground continuity and fault currents in accordance with UL 467, and NEC code tables for ground conductors.
         4. Jacket: Flexible, corrosion-resistant, watertight, moisture and heat resistant molded rubber material with stainless steel jacket clamps.
      7. Rigid Aluminum Fittings:
         1. Provide malleable iron, steel or aluminum alloy materials; zinc or cadmium plate iron or steel fittings. Aluminum fittings containing more than 0.4 percent copper are prohibited.
         2. Locknuts and Bushings: As specified for rigid steel and IMC conduit.
         3. Set Screw Fittings: Not permitted for use with aluminum conduit.
         4. Indent type connectors or couplings are prohibited.
         5. Die-cast or pressure-cast zinc-alloy fit-tings or fittings made of “pot metal” are not permitted.
         6. Provide OEM approved fittings.
      8. Wireway Fittings: As recommended by wireway OEM.
    1. Conduit Supports:
       1. Parts and Hardware: Provide zinc-coat or equivalent corrosion protection.
       2. Individual Conduit Hangers: Designed for the purpose, having a pre-assembled closure bolt and nut, and provisions for receiving a hanger rod.
       3. Multiple Conduit (Trapeze) Hangers: Minimum 38 mm by 38 mm (1-1/2 by 1-1/2 inch), 2.78 mm (12 gage) steel, cold formed, lipped channels; with minimum 9 mm (3/8 inch) diameter steel hanger rods.
       4. Solid Masonry and Concrete Anchors: Self-drilling expansion shields, or machine bolt expansion.
    2. Outlet, Splice, and Pull Boxes:
       1. Conform to UL-50 and UL-514A.
       2. Cast metal where required by NEC or shown, and equipped with rustproof boxes.
       3. Sheet Metal Boxes: Galvanized steel, except where otherwise shown.
       4. Install flush mounted wall or ceiling boxes with raised covers so that front face of raised cover is flush with wall.
       5. Install surface mounted wall or ceiling boxes with surface style flat or raised covers.
    3. Wireways: Equip with hinged covers, except where removable covers are shown.
    4. Warning Tape: Standard, 4-Mil polyethylene 76 mm (3 inch) wide tape detectable type, red with black letters, and imprinted with “CAUTION BURIED COMMUNICATIONS CABLE BELOW”.
    5. Flexible Nonmetallic Communications Raceway (Innerduct) and Fittings:
       1. General: Provide UL 910 listed plenum, riser, and general purpose corrugated pliable communications raceway for optical fiber cables and communications cable applications; select in accordance with provisions of NEC Articles 770 and 800.
       2. Provide Communications Raceway with a factory installed 567 kg (1250 lb.) tensile pre-lubricated pull tape.
       3. Use only metallic straps, hangers and fittings to support raceway from building structure. Cable ties are not permitted for securing raceway to building structure.
       4. Provide fittings to be installed in spaces used for environmental air made of materials that do not exceed flammability, smoke generation, ignitibility, and toxicity requirements of environmental air space.
       5. Size: Metric Designator 53 (trade size 2) or smaller.
       6. Outside Plant: Plenum-rated where each interduct is 75 mm (3 inches) and larger.
       7. Inside Plant: Listed and marked for installation in plenum airspaces and minimum 25 mm (1 inch) inside diameter.
       8. Plenum: Non-metallic communications raceway.
          1. Constructed of low smoke emission, flame retardant PVC with corrugated construction.
          2. UL 94 V-O rating for flame spreading limitation.
       9. Provide innerduct reel lengths as necessary to ensure ducts are continuous; one piece runs from ENTR to MH; MH to MH; DEMARC to MCR/TER; TR to TR. Innerduct connectors are not permitted between rooms.
       10. Provide pulling accessories used for innerduct including but not limited to, inner duct lubricants, spreaders, applicators, grips, swivels, harnesses, and line missiles (blown air) compatible with materials being pulled.
    6. Outlet Boxes:
       1. Flush wall mounted minimum 11.9 cm (4-11/16 inches) square, 9.2 cm (3-5/8 inches) deep pressed galvanized steel.
       2. //Flush wall mounted 12.7 cm (5 inches) square x 7.3 cm (2-7/8 inches); deep pressed galvanized steel.//
       3. 2-Gang Tile Box:
          1. Flush backbox type for installation in block walls.
          2. Minimum 92 mm (3-5/8 inches) deep.
    7. Weatherproof Outlet Boxes: Surface mount two gang, 67 mm (2-5/8 inches) deep weatherproof cast aluminum with powder coated finish internal threads on hubs 19 mm (3/4 inch) minimum.
    8. Cable Tray:
       1. Provide wire basket type of sizes indicated; with all required splicing and mounting hardware.
       2. Materials and Finishes:
          1. Electro-plated zinc galvanized (post plated) made from carbon steel and plated to ASTM B 633, Type III, SC-1.
          2. Remove soot, manufacturing residue/oils, or metallic particles after fabrication.
          3. Rounded edges and smooth surfaces.
       3. Provide continuous welded top side wire to protect cable insulation and installers.
       4. High strength steel wires formed into a 50 x 100 mm (2 inches by 4 inches) wire mesh pattern with intersecting wires welded together.
       5. Wire Basket Sizes:
          1. Wire Diameter: 5 mm (0.195 inch) minimum on all mesh sections.
          2. Usable Loading Depth: 105 mm (4 inch) // 150 mm (6 inches) // .
          3. Width: 300 mm (12 inches) // 450 mm (18 inches) // 600 mm (24 inches) // .
       6. Fittings: Field-formed, from straight sections, in accordance with manufacturer’s instructions.
       7. Provide accessories to protect, support and install wire basket tray system.
    9. Cable Duct: Equip with hinged covers, except where removable covers are accepted by COR.
    10. Cable Duct Fittings: As recommended by cable duct OEM.

1. EXECUTION
   1. EQUIPMENT INSTALLATION AND REQUIREMENTS
      1. Raceways typically required for cabling systems unless otherwise indicated:

| System | Specification Section | Installed Method |
| --- | --- | --- |
| Grounding | 27 05 26 | Conduit Not Required |
| Control, Communication and Signal Wiring | 27 10 00 | Complete Conduit Allowed in Non-Partitioned Cable Tray or Cable Ladders |
| Communications  Structured Cabling | 27 15 00 | Conduit to Cable Tray Partitioned Cable Tray |
| Master Antenna Television Equipment and Systems | 27 41 31 | Conduit to Cable Tray, Partitioned Cable Tray |
| Public Address and Mass Notification Systems | 27 51 16 | Complete conduit |
| Intercommunications and Program systems | 27 51 23 | Conduit to Cable Tray, Partitioned Cable Tray |
| Nurse Call | 27 52 23 | Complete Conduit |
| Security Emergency Call, Duress Alarm, and Telecommunications | 27 52 31 | Conduit to Cable Tray, Partitioned Cable Tray |
| Miscellaneous Medical Systems | 27 52 41 | Complete Conduit |
| Distributed Radio Antenna Equipment and System | 27 53 19 | Conduit to Cable Tray, Partitioned Cable Tray |
| Grounding and Bonding for Electronic Safety and Security | 28 05 26 | Conduit Not Required Unless Required by Code |
| Physical Access Control System | 28 13 00 | Conduit to Cable Tray Partitioned Cable Tray |
| Physical Access Control System and Database Management | 28 13 16 | Conduit to Cable Tray Partitioned Cable Tray |
| Security Access Detection | 28 13 53 | Complete Conduit |
| Intrusion Detection System | 28 16 00 | Conduit to Cable Tray, Partitioned Cable Tray |
| Video Surveillance | 28 23 00 | Complete Conduit |
| Electronic Personal Protection System | 28 26 00 | Conduit to Cable Tray, Partitioned Cable Tray |
| Fire Detection and Alarm | 28 31 00 | Complete Conduit |

* + 1. Penetrations:
       1. Cutting or Holes:
          1. Locate holes in advance of installation. Where they are proposed in structural sections, obtain approval of structural engineer and COR prior to drilling through structural sections.
          2. Make holes through concrete and masonry in new // and existing // structures with a diamond core drill or concrete saw. Pneumatic hammer, impact electric, hand or manual hammer type drills are not permitted; COR may grant limited permission by request, in condition of limited working space.
          3. Fire Stop: Where conduits, wireways, and other communications raceways pass through fire partitions, fire walls, smoke partitions, or floors, install a fire stop that provides an effective barrier against spread of fire, smoke and gases as specified in Section 07 84 00, FIRESTOPPING.

Fill and seal clearances between raceways and openings with fire stop material.

Install only retrofittable, non-hardening, and reusable firestop material that can be removed and reinstalled to seal around cables inside conduits.

SPEC WRITER NOTES:

1. Verify that roof penetration details are shown on architectural drawings.

2. Delete // \_\_\_ // for existing; modify for new and existing.

* + - * 1. Waterproofing at Floor, Exterior Wall, and Roof Conduit Penetrations:

Seal clearances around conduit and make watertight as specified in Section 07 92 00, JOINT SEALANTS // or directed by waterproofing manufacturer. //

// Where work to be performed by \_\_\_\_\_ . //

* + 1. Conduit Installation:
       1. Minimum conduit size of 19 mm (3/4 inch), but not less than size required for 40 percent fill.
       2. Install insulated bushings on all conduit ends.
       3. Install pull boxes after every 180 degrees of bends (two 90 degree bends). Size boxes per TIA 569.
       4. Extend vertical conduits/sleeves through floors minimum 75 mm (3 inches) above floor and minimum 75 mm (3 inches) below ceiling of floor below.
       5. Terminate conduit runs to and from a backboard in a closet or interstitial space at top or bottom of backboard. Install conduits to enter telecommunication rooms next to wall and flush with backboard.
       6. Where drilling is necessary for vertical conduits, locate holes so as not to affect structural sections.
       7. Seal empty conduits located in telecommunications rooms or on backboards with a standard non-hardening putty compound to prevent entrance of moisture and gases and to meet fire resistance requirements.
       8. Minimum radius of communication conduit bends:

| Sizes of Conduit  Trade Size | Radius of Conduit Bends  mm, Inches |
| --- | --- |
| 3/4 | 150 (6) |
| 1 | 230 (9) |
| 1-1/4 | 350 (14) |
| 1-1/2 | 430 (17) |
| 2 | 525 (21) |
| 2-1/2 | 635 (25) |
| 3 | 775 (31) |
| 3-1/2 | 900 (36) |
| 4 | 1125 (45) |

* + - 1. Provide 19 mm (3/4 inch) thick fire retardant plywood specified in Section 06 10 00, ROUGH CARPENTRY on wall of communication closets where shown on drawings. Mount plywood with bottom edge 300 mm (12 inches) above finished floor and top edge 2.74 m (9 feet) A.F.F.
      2. Provide pull wire in all empty conduits; sleeves through floor are exceptions.
      3. Complete each entire conduit run installation before pulling in cables.
      4. Flattened, dented, or deformed conduit is not permitted.
      5. Ensure conduit installation does not encroach into ceiling height head room, walkways, or doorways.
      6. Cut conduit square with a hacksaw, ream, remove burrs, and draw tight.
      7. Install conduit mechanically continuous.
      8. Independently support conduit at 2.44 m (8 feet) on center; do not use other supports (i.e., suspended ceilings, suspended ceiling supporting members, luminaires, conduits, mechanical piping, or mechanical ducts).
      9. Support conduit within 300 mm (1 foot) of changes of direction, and within 300 mm (1 foot) of each enclosure to which connected.
      10. Close ends of empty conduit with plugs or caps to prevent entry of debris, until cables are pulled in.
      11. // Conduit installations under fume and vent hoods are prohibited. //
      12. Attach conduits to cabinets, splice cases, pull boxes and outlet boxes with bonding type locknuts. For rigid and IMC conduit installations, provide a locknut on inside of enclosure, made up wrench tight. Do not make conduit connections to box covers.
      13. Do not use aluminum conduits in wet locations.
      14. Unless otherwise indicated on drawings or specified herein, conceal conduits within finished walls, floors and ceilings.
      15. Conduit Bends:
          1. Make bends with standard conduit bending machines; observe minimum bend radius for cable type and outside diameter.
          2. Conduit hickey is permitted only for slight offsets, and for straightening stubbed conduits.
          3. Bending of conduits with a pipe tee or vise is not permitted.
      16. Layout and Homeruns - Deviations: Make only where necessary to avoid interferences and only after drawings showing proposed deviations have been submitted and approved by COR.
    1. Concealed Work Installation:

SPEC WRITER NOTE:

1. EMT is not permitted in concrete. DOUBLE Check USE OF IMC.

* + - 1. In Concrete:
         1. Conduit: Rigid steel or IMC.
         2. Align and run conduit in direct lines.
         3. Install conduit through concrete beams only when the following occurs:

Where shown on structural drawings.

As accepted by COR prior to construction, and after submittal of drawing showing location, size, and position of each penetration.

* + - * 1. Installation of conduit in concrete that is less than 75 mm (3 inches) thick is prohibited.

Conduit outside diameter larger than 1/3 of slab thickness is prohibited.

Space between Conduits in Slabs: Approximately six conduit diameters apart, except one conduit diameter at conduit crossings.

Install conduits approximately in center of slab to ensure a minimum of 19 mm (3/4 inch) of concrete around conduits.

* + - * 1. Make couplings and connections watertight. Use thread compounds that are NRTL listed conductive type to ensure low resistance ground continuity through conduits. Tightening set screws with pliers is not permitted.
    1. Furred or Suspended Ceilings and in Walls:
       1. Rigid steel, //IMC// or rigid aluminum. Different type conduits mixed indiscriminately in same system is not permitted.
       2. Align and run conduit parallel or perpendicular to building lines.
       3. Tightening set screws with pliers is not permitted.
    2. Exposed Work Installation:
       1. Unless otherwise indicated on drawings, exposed conduit is only permitted in telecommunications rooms.
          1. Provide rigid steel, IMC or rigid aluminum.
          2. Different type of conduits mixed indiscriminately in system is not permitted.
       2. Align and run conduit parallel or perpendicular to building lines.
       3. Install horizontal runs close to ceiling or beams and secure with conduit straps.
       4. Support horizontal or vertical runs at not over 2400 mm (96 inches) intervals.
       5. Surface Metal Raceways: Use only where shown on drawings.
       6. Painting:
          1. Paint exposed conduit as specified in Section 09 91 00, PAINTING.
          2. Refer to Section 09 91 00, PAINTING for preparation, paint type, and exact color.
          3. Provide labels where conduits pass through walls and floors and at maximum 6000 mm (20 foot) intervals in between.
    3. Expansion Joints:
       1. Conduits 75 mm (3 inches) and larger, that are secured to building structure on opposite sides of a building expansion joint, require expansion and deflection couplings. Install couplings in accordance with manufacturer's recommendations.
       2. Provide conduits smaller than 75 mm (3 inches) with pull boxes on both sides of expansion joint. Connect conduits to expansion and deflection couplings as specified.
       3. Install expansion and deflection couplings where shown.

SPEC WRITER NOTE:

1. Include following paragraph for seismic areas only.

* + 1. Seismic Areas:
       1. In seismic areas, follow H-18-8 Seismic Design Requirements.
       2. Rigidly secure conduit to building structure on opposite sides of a building expansion joint with pull boxes on both sides of joint.
       3. Connect conduits to pull boxes with 375 mm (15 inches) of slack flexible conduit.
       4. Install green copper wire minimum #6 AWG in flexible conduit for bonding jumper.
    2. Conduit Supports, Installation:
       1. Select AC193 code listed mechanical anchors or fastening devices with safe working load not to exceed 1/4 of proof test load.
       2. Use pipe straps or individual conduit hangers for supporting individual conduits. Maximum distance between supports is 2.5 m (8 foot) on center.
       3. Support multiple conduit runs with trapeze hangers. Use trapeze hangers designed to support a load equal or greater than sum of the weights of the conduits, wires, hanger itself, and 90 kg (200 pounds). Attach each conduit with U-bolts or other accepted fasteners.
       4. Support conduit independent of pull boxes, luminaires, suspended ceiling components, angle supports, duct work, and similar items.
       5. Fastenings and Supports in Solid Masonry and Concrete:
          1. New Construction: Use steel or malleable iron concrete inserts set in place prior to placing concrete.
          2. Existing Construction:

Code AC193 listed wedge type steel expansion anchors minimum 6 mm (1/4 inch) bolt size and minimum 28 mm (1-1/8 inch) embedment.

Power set fasteners minimum 6 mm (1/4 inch) diameter with depth of penetration minimum 75 mm (3 inches).

Use vibration and shock resistant anchors and fasteners for attaching to concrete ceilings.

* + - 1. Fastening to Hollow Masonry: Toggle bolts are permitted.
      2. Fastening to Metal Structures: Use machine screw fasteners or other devices designed and accepted for application.
      3. Bolts supported only by plaster or gypsum wallboard are not acceptable.
      4. Attachment by wood plugs, rawl plug, plastic, lead or soft metal anchors, or wood blocking and bolts supported only by plaster is prohibited.
      5. Do not support conduit from chain, wire, or perforated strap.
      6. Spring steel type supports or fasteners are not permitted except horizontal and vertical supports/fasteners within walls.
      7. Vertical Supports:
         1. Install riser clamps and supports for vertical conduit runs in accordance with NEC.
         2. Provide supports for cable and wire with fittings that include internal wedges and retaining collars.
    1. Box Installation:
       1. Boxes for Concealed Conduits:
          1. Flush mounted.
          2. Provide raised covers for boxes to suit wall or ceiling, construction and finish.
       2. In addition to boxes shown, install additional boxes where needed to prevent damage to cables during pulling.
       3. Remove only knockouts as required and plug unused openings. Use threaded plugs for cast metal boxes and snap-in metal covers for sheet metal boxes.
       4. Stencil or install phenolic nameplates on covers of boxes identified on riser diagrams; for example "SIG-FA JB No. 1".
       5. Outlet boxes mounted back-to-back in same wall are not permitted. A minimum 600 mm (24 inches) center-to-center lateral spacing must be maintained between boxes.
    2. Flexible Nonmetallic Communications Raceway (Innerduct), Installation:
       1. Install supports from building structure for horizontal runs at intervals not to exceed 900 mm (3 feet) and at each end.
       2. Install supports from building structure for vertical runs at intervals not to exceed 1.2 m (4 feet) and at each side of joints.
       3. Install only in accessible spaces not subject to physical damage or corrosive influences.
       4. Make bends manually to assure internal diameter of tubing is not effectively reduced.
       5. Extend each segment of innerduct minimum 300 mm (12 inches) beyond end of service conduit tie or cable tray. Restrain innerduct ends with wall mount clamps and seal when cable is installed.
  1. TESTING
     1. Examine fittings and locknuts for secureness.
     2. Test RMC, IMC and EMT systems for electrical continuity.
     3. Perform simple continuity test after cable installation.

- - - E N D - - -