## Slide 1: Masonry Structures James Robert Harris, PE, PhD, and Fredrick R. Rutz, PE, PhD
Disclaimer
Edited by David Sommer, PE, SE
Includes materials originally developed by
Richard Klingner, PE, PhD
Notes: Title slide, consisting of an image of the cover of the data disk containing the 2015 NEHRP Recommended Seismic Provisions.
Title Slide for Masonry Structures

## Slide 2: SEISMIC DESIGN OF MASONRY STRUCTURES
Notes: In this first slide, we see examples of different applications of masonry : on the left, a low-rise bearing-wall building of reinforced masonry; in the center, a high-rise bearing-wall building of reinforced masonry; and on the right, stone and clay unit veneer over a frame structure.
Topic 13 deals with the seismic design of masonry structures.

## Slide 3: NEHRP Recommended Provisions Masonry Structures:
Shear wall in-plane design
Masonry walls out-of-plane
Overstrength concepts
Details
Simplified design for wall-type structures
Shear wall design example
Context in the Provisions
Reference standards
Masonry basics
Masonry behavior
Organization of TMS 402 Code
Types of shear walls
Notes: This slide presents an overview of the presentation.
This is a list of topics covered in this review module on masonry design according to the NEHRP Recommended Provisions, which is developed for the Federal Emergency Management Agency (FEMA) by the Building Seismic Safety Council (BSSC) of the National Institute of Building Sciences (NIBS).

## Slide 4: Objectives of Module
Basics of masonry behavior
The TMS 402 Building Code and TMS 602 Specification and the relationship of NEHRP Recommended Provisions documents to it
Earthquake design of masonry structures and components using the 2013 TMS 402 Code and TMS 602 Specification
Example of masonry shear wall design
Notes: This slide lists the objectives of the presentation.
Because many in the intended audience may not have studied masonry recently, the module begins with a review of the basic components of masonry and of the basic behavior of wall-type structures. It then addresses the specification of masonry units, mortar, grout, and accessory materials. It continues with the rudiments of the mechanical behavior of masonry. It then reviews The Masonry Society (TMS) Code and Specification, which is the fundamental technical resource behind the NEHRP Recommended Provisions. It concludes with the design and detailing of a reinforced masonry shear wall.

## Slide 5: NEHRP Recommended Provisions Masonry Design
Context in the Provisions
Design seismic loads
  Load combinations ASCE 7-16 Ch. 2 & 12
  Loads on structures ASCE 7-16 Ch. 12
  Loads on components
  & attachments Chap. 6 ASCE 7-16 Ch. 13
Design resistances ASCE 7-16 Ch. 14
  Strength design (mostly references TMS 402-13)
Notes: This slide lists sections referenced by the NEHRP provisions for the design of reinforced masonry.
This is a list of topics covered in this review module on masonry design according to the NEHRP Recommended Provisions, which is developed for the Federal Emergency Management Agency (FEMA) by the Building Seismic Safety Council (BSSC) of the National Institute of Building Sciences (NIBS).

## Slide 6: NEHRP Recommended Provisions Masonry Design
Basic Documents
NEHRP Recommended Provisions
ASCE 7-16, Minimum Design Loads for Buildings and Other Structures
TMS 402-13, Building Code Requirements for Masonry Structures
TMS 602-13, Specification for Masonry Structures
IBC 2015, International Building code
Notes: This slide lists references used for the design of reinforced masonry.
This is a list of topics covered in this review module on masonry design according to the NEHRP Recommended Provisions, which is developed for the Federal Emergency Management Agency (FEMA) by the Building Seismic Safety Council (BSSC) of the National Institute of Building Sciences (NIBS).

## Slide 7: NEHRP Recommended Provisions Masonry Design
Masonry Basics
Notes: This slide is the intro slide to the masonry basics section of the presentation.
This is a list of topics covered in this review module on masonry design according to the NEHRP Recommended Provisions, which is developed for the Federal Emergency Management Agency (FEMA) by the Building Seismic Safety Council (BSSC) of the National Institute of Building Sciences (NIBS).

## Slide 8: Review Masonry Basics
Basic terms
Units
Mortar
Grout
Accessory materials
  Reinforcement (may or may not be present), connectors, flashing, sealants
Typical details
Notes: This slide lists an overview of topics covered for the masonry basics section.
Let’s start by reviewing masonry basics. Masonry is made up of units, mortar, grout, and accessory materials. The mortar holds the units together as well as apart, compensating for their dimensional tolerances. The grout is a fluid concrete mixture used to fill voids in the masonry and to anchor deformed reinforcement.

## Slide 9: Basic Terms
Running bond
Stack bond
1/3 Running bond
Flemish bond
bed
joints
head
joints
Bond patterns (looking at wall):
Notes: This figure illustrates common types of masonry bond patterns, including running bond, stack bond, 1/3 running bond, and flemish bond.
Masonry units can be laid in different bond patterns. The most common of these is 1/2 running bond, often called simply “running bond.” Horizontal bed joints are continuous; vertical head joints alternate courses, and the head joint of one course aligns with the middle of the unit on the adjacent courses. In stack bond (referred to in TMS 402 and Specification as “other than running bond”), the head joints are continuous between adjacent courses.

## Slide 10: Masonry Units
Concrete masonry units (CMU):
  Specified by ASTM C 90
  Minimum specified compressive strength (net area) of 2000 psi (average)
  Net area is about 55% of gross area
  (varies with size)
  Nominal versus specified versus actual dimensions
  Type I and Type II designations no longer exist
Notes: This picture presents basics of concrete masonry units (CMU)
Masonry units have three basic systems of dimensions: nominal, specified, and actual.
Nominal dimensions are used to lay out a structure. A common size C90 unit has nominal dimensions of 8 by 8 by 16 inches.
Specified dimensions are nominal dimensions minus one-half the thickness of a joint on all sides of the unit. Since masonry joints are normally 3/8-in. thick, the specified dimensions of a nominal 8 x 8 x 16-in. unit are 7-5/8 by 7-5/8 by 15-5/8 inches.
Actual dimensions are what the unit actually measures and should lie within the specified dimensions, plus or minus the specified dimensional tolerance.

## Slide 11: Masonry Units
Clay masonry units:
  Specified by ASTM C 62 or C 216
  Usually solid, with small core holes for manufacturing purposes
  If cores occupy  25% of net area, units can be considered 100% solid
  Hollow units are similar to CMU - can be reinforced
Notes: This picture presents basics of brick masonry units
Clay masonry units are specified by ASTM C62 (building brick) or C216 (facing brick). They are usually solid and may have small core holes to facilitate drying and firing. Because clay masonry units usually have more than enough compressive strength, the core holes are ignored unless they occupy more than 25% of the area of the units.

## Slide 12: Masonry Mortar
Mortar for unit masonry is specified by ASTM C 270
Three cementitious systems
  Portland cement + lime + sand (“traditional”)
  Masonry cement mortar (lime is included in cement)
  Mortar cement mortar (lime is included in cement, higher air contents)
Notes: This slide introduces the basics of masonry mortar
Mortar for unit masonry is specified by ASTM C270. In specifying mortar, the designer must make three decisions:
The first decision involves the cementitious system to be used. Three cementitious systems are available: portland cement-lime mortar; masonry cement mortar; and mortar cement mortar.

## Slide 13: Masonry Mortar
Plastic mortar properties
  Workability Important for good bond
  Water retentivity
  Rate of hardening
Hardened mortar properties
  Bond Important, seldom specified
  Compressive strength
  Volume stability
  Durability
Notes: This slide lists desirable properties of masonry mortar
Mortar for unit masonry is specified by ASTM C270. In specifying mortar, the designer must make three decisions:
The first decision involves the cementitious system to be used. Three cementitious systems are available: portland cement-lime mortar; masonry cement mortar; and mortar cement mortar.

## Slide 14: Masonry Mortar
Within each cementitious system, mortar is specified by type (M a S o N w O r K):
  Going from Type K to Type M, mortar has an increasing volume proportion of portland cement. It sets up faster and has higher compressive and tensile bond strengths.
  As the volume proportion of portland cement increases, mortar is less able to deform when hardened.
  Types M and S are specified for modern structural masonry construction.
  Type N for non-loadbearing and for brick veneer
  Type O or K for historic masonry repairs
Notes: This slide lists the different types of mortar and their uses
Within each cementitious system, the designer must specify the mortar type. Mortar type describes the amount of cement in the mortar compared to the amount of other constituents.
The designations for mortar type were intentionally selected as alternating letters in the phrase “mason work,” avoiding the connotations that might be associated with designations such as “A,” “B,” “C,” and “D.”
Going from Type K to Type M, mortar has an increasing volume proportion of portland cement or other cements. It sets up faster and has higher compressive and tensile bond strengths. As the volume proportion of portland cement increases, mortar is less able to deform when hardened.
Types N and S are specified for modern masonry construction.

## Slide 15: Masonry Mortar
Under ASTM C270, mortar can be specified by proportion or by property.
If mortar is specified by proportion, compliance is verified only by verifying proportions. For example:
  Type S PCL mortar has volume proportions of 1 part cement to about 0.5 parts hydrated mason’s lime to about 4.5 parts mason’s sand
  Type N masonry cement mortar (single-bag) has one part Type N masonry cement and 3 parts mason’s sand
Notes: This slide lists the two ways of specifying mortar.
Under ASTM C270, mortar can be specified by proportion or by property. The proportion specification is the default.
When mortar is specified by proportion, a Type S PCL mortar has volume proportions of 1 part cement to about 0.5 parts hydrated mason’s lime to about 4.5 parts mason’s sand. A Type N masonry cement mortar (using the most common single-bag case) has one part Type N masonry cement and about 3 parts mason’s sand.
Note that the amount of water is not specified. This is because the water should be adjusted by the mason in the field to achieve good workability.

## Slide 16: Masonry Mortar
Under ASTM C270, mortar can be specified by proportion or by property:
  Proportion specification is simpler -- verify in the field that volume proportions meet proportion limits.
  Property specification is more complex: (1) establish the proportions necessary to produce a mortar that, tested at laboratory flow, will meet the required compressive strength, air content, and retentivity (ability to retain water) requirements and (2) verify in the field that volume proportions meet proportion limits.
Notes: This slide lists the two ways of specifying mortar.
“Flow” is a standard ASTM measurement of the workability of a mortar. Mortar in the field typically has a flow of 130 to 135. ASTM specifications have no requirements for the properties of mortar mixed to field flow. ASTM property specifications are based on mortar with a so-called “laboratory flow” of 110 representing the characteristics of mortar after some of the water has been absorbed from it by the surrounding units.
To specify mortar by proportion according to ASTM C270 is relatively simple. The required proportions are given in the specification, and compliance is verified by verifying that the mortar is being batched using those proportions.
To specify mortar by property according to ASTM C270, one must evaluate, at laboratory flow of 110, the compressive strength, air content, and retentivity of different mortars and then decide on volume proportions that will meet the required criteria. Finally, one must verify in the field that the mortar s being batched using those proportions.

## Slide 17: Masonry Mortar
The proportion specification is the default. Unless the property specification is used, no mortar testing is necessary.
The proportion of water is not specified. It is determined by the mason to achieve good productivity and workmanship.
Masonry units absorb water from the mortar decreasing its water-cement ratio and increasing its compressive strength. Mortar need not have high compressive strength.
Notes: This slide presents basics of specifying masonry mortar by proportion.
The proportion specification is the default. Unless the property specification is used, no mortar testing is necessary.
Some suggest that the words “by proportion” be added to the end of specifications to emphasize that compliance with proportion specifications involves no testing whatsoever.
The proportion of water is not specified. It is determined by the mason to achieve good productivity and workmanship.
Masonry units absorb water from the mortar decreasing its water-cement ratio and increasing its compressive strength. Mortar need not have high compressive strength.

## Slide 18: Grout
Grout for unit masonry is specified by ASTM C 476
Two kinds of grout:
  Fine grout (cement, sand, water)
  Coarse grout (cement, sand, pea gravel, water)
ASTM C 476 permits a small amount of hydrated lime, but does not require any. Lime is usually not used in plant – batched grout.
Notes: This slide introduces the basics of masonry grout.
Grout for unit masonry is specified by ASTM C 476, which addresses two kinds of grout: fine grout which is composed of cement, sand and water and coarse grout, which is composed of cement, sand, pea gravel and water. The fairly common practice of specifying grout as concrete is acceptable but only if the resulting mixture proportion conforms to C476.
ASTM C 476 permits a small amount of hydrated lime but does not require any. Lime is usually not used in plant-batched grout because lime is not available in such plants.

## Slide 19: Grout
Under ASTM C476, grout can be specified by proportion or by compressive strength:
  Proportion specification is simpler. It requires only that volume proportions of ingredients be verified.
  Specification by compressive strength is more complex. It requires compression testing of grout in a permeable mold (ASTM C 1019).
Notes: This slide lists the two ways of specifying grout.
Under ASTM C476, grout can be specified by proportion or by compressive strength.
The proportion specification is simpler. It requires only that volume proportions of ingredients be verified.
Specification by compressive strength is more complex. It requires compression testing of grout in a permeable mold (ASTM C 1019).

## Slide 20: Grout
If grout is specified by proportion, compliance is verified only by verifying proportions. For example:
  Fine grout has volume proportions of 1 part cement to about 3 parts mason’s sand.
  Coarse grout has volume proportions of 1 part cement to about 3 parts mason’s sand and about 2 parts pea gravel.
Unless the compressive-strength specification is used, no grout testing is necessary.
Notes: This slide lists basics of grout specification.
If grout is specified by proportion, compliance is verified only by verifying proportions.
For example, fine grout has volume proportions of 1 part cement to about 3 parts mason’s sand. Coarse grout has volume proportions of 1 part cement to about 3 parts mason’s sand and about 2 parts pea gravel.
Unless the compressive-strength specification is used, no grout testing is necessary.

## Slide 21: Grout
The proportion of water is not specified. The slump should be 8 to 11 in.
Masonry units absorb water from the grout decreasing its water-cement ratio and increasing its compressive strength. High-slump grout will still be strong enough.
Notes: This slide lists basics of grout in masonry.
The proportion of water in grout is not specified. The slump should be 8 to 11 inches.
Masonry units absorb water from the grout, decreasing its water-cement ratio and increasing its compressive strength. High-slump grout will still be strong enough.

## Slide 22: Role of fm
Concrete:
  Designer specifies value of fc
  Compliance is verified by compression tests on cylinders cast in the field and cured under ideal conditions
Masonry
  Designer specifies value of fm
  Compliance is verified by “unit strength method” or by “prism test method”
Notes: This slide compares the use of f’m in masonry to f’c in concrete.
In designing and specifying masonry according to TMS 402, the role of f’m is analogous to that of f’c for concrete.
For concrete, the designer states an assumed value of fc and compliance is verified by compression tests on cylinders cast in the field and cured under ideal conditions.
For masonry, the designer states an assumed value of fm and compliance is verified either by the “unit strength method,” or by the “prism test method.”

## Slide 23: Verify Compliance with Specified fm
Unit strength method (Spec 1.4.B.2):
  Compressive strengths from unit manufacturer
  Grout strength equals or exceeds fm,min = 2,000 psi
Prism test method (Spec 1.4.B.3):
  Pro -- can permit optimization of materials
  Con -- require testing, qualified testing lab, and procedures in case of non-complying results
Notes: This slide lists the two most common ways to very compliance with the specified f’m.
TMS 402 offers two ways of demonstrating compliance with the specified f’m. The simplest is the “unit strength method.” Using compressive strengths for standard ASTM units obtained by the unit manufacturer as part of production quality control, mortar meeting ASTM C270 and grout meeting ASTM C476 or having a compressive strength of at least 2000 psi, conservative values for f’m can be taken from Tables 1 and 2 of the Specification.
Alternatively, prisms can be constructed and tested by ASTM C1314.

## Slide 24: Example of Unit Strength Method (Specification Tables 1, 2)
Clay masonry units (Table 1)
  Example:
  Unit compressive strength  4150 psi
  Type N mortar
  Prism strength can be taken as 1500 psi
Concrete masonry units (Table 2)
  Example:
  Unit compressive strength  2000 psi
  Type S mortar
  Prism strength can be taken as 2000 psi
Notes: This picture shows a unit of clay brick and concrete block.
For example, in clay masonry, if units have a compressive strength of at least 4150 psi and ASTM C270 Type N mortar is used, the prism strength can be taken as 1500 psi.
In concrete masonry, if units have a compressive strength of at least 2000 psi (which happens to be the minimum for C90 units) and ASTM C270 Type S mortar is used, the prism strength can be taken as 2000 psi.
A specified prism strength of 2000 psi for concrete masonry is the typical minimum strength using commonly available materials. However, prior to the 2013 edition of the specification and the 2015 edition of ASTM C90, the most common strength value used for concrete masonry was 1500 psi.

## Slide 25: Application of Unit Strength Method (Specification Tables 1, 2)
Designer determines required material specification:
  Designer states assumed value of fm
  Specifier specifies units, mortar and grout that will satisfy “unit strength method”
  Compliance with fm can be verified with no tests on mortar, grout, or prisms (but need verification of units’ compressive strength)
Notes: This slide lists the procedure to comply with the specified f’m using the unit strength method.
If compliance with the specified f’m is verified by the unit strength method and compliance with ASTM C270 (mortar) and ASTM C476 (grout) is verified by proportion), no job-specific testing whatsoever is required.

## Slide 26: Comply with Specified Products and Execution
Products -- Specification Part 2:
  Units, mortar, grout, accessory materials
Execution -- Specification Part 3
  Inspection
  Preparation
  Installation of masonry units, mortar, reinforcement, grout, prestressing tendons
Notes: This slide lists items required to comply with specified products and execution per the TMS 602 Specification.
Finally, the TMS 602 Specification requires compliance with the specified products (Article 2), which means units, mortar, grout and accessory materials, and with the specified execution (Article 3), which means inspection, preparation and installation of masonry, reinforcement, grout and prestressing tendons.

## Slide 27: Procedure for Strength Design of Reinforced Masonry Shear Walls
Select trial design.
Compute factored design moments and shears for in- and out-of-plane loading. Include p-d for out-of-plane deflection and moment.
Design flexural reinforcement as controlled by out-of-plane loading.
Design flexural reinforcement as controlled by in-plane loading and revise design as necessary.
Check to ensure ductility.
Check shear capacity and revise if required.
Check detailing.
Notes: This slide lists the typical procedure for strength design of reinforced masonry shear walls.

## Slide 28: Accessory Materials
Weepholes
Shelf angle
Flashing
Sealant gap
~ 3 / 8 in.
Horizontally oriented expansion joint under shelf angle:
Notes: This slide shows a graphic of a horizontal expansion joint to avoid transferring load from the structure to the clay masonry veneer.
One of the most important details in a masonry building is the expansion joint under shelf angles in clay masonry veneer. Clay masonry expands over time; concrete and concrete masonry shrink. If the veneer is laid without the expansion joint, it will end up supporting the building even though it is not made to resist the resulting compression.

## Slide 29: Component Design Basics
Fully grouted wall:
Area assumed effective in longitudinal shear
Notes: Slide shows diagram of fully grouted wall with mortar in all cells.

## Slide 30: Component Design Basics
No grout in wall:
Face shells are the only area assumed effective in longitudinal shear.
Notes: Slide shows non-grouted wall. The webs are ordinarily not mortared.

## Slide 31: Component Design Basics
Partially grouted wall:
Area assumed effective in longitudinal shear includes grouted cells and adjacent webs.
Notes: Slide shows partially grouted wall. Note that the webs that are not adjacent to a grouted cell usually do not have any mortar.

## Slide 32: Component Design: Design of walls
Out-of-plane forces, Fp
Out-of-plane
bending and shear
Notes: This picture shows a wall subject to out of plane forces deflecting out in the direction of the force. The wall boundary conditions are shown acting as not restraining rotation.
This loading applies to all masonry walls, whether “participating” or not. If not participating, the connections at the top must allow relative motion in the plane of the wall.

## Slide 33: Component Design basics
T - beam section assumed to resist out-of-plane flexure
(Masonry laid in running bond)
beff = 6t < s < 72”
s s
- -
Notes: This slide shows Tee-beam design grouted wall.
Tee-beam design is much the same as in reinforced concrete.

## Slide 34: Component Design basics
Masonry can span horizontally
Notes: This slide shows walls subject to out of plane forces spanning horizontally between pilasters. The wall is shown deflecting freely at the top and bottom, with rotational restraint at the pilasters.
This style of construction was popular in the mid twentieth century.

## Slide 35: Component Design basics
Force distributed according to relative stiffness
In-plane force
Notes: This slide shows a wall subject to an in plane force distributed to wall segments of various length.
Basic concept of analysis for distribution of seismic forces; the unit force will be higher in the stiffer elements.

## Slide 36: NEHRP Recommended Provisions Masonry Design
Masonry Behavior
Notes: This slide is the introductory slide to the Masonry Behavior subject in the presentation.
This is a list of topics covered in this review module on masonry design according to the NEHRP Recommended Provisions, which is developed for the Federal Emergency Management Agency (FEMA) by the Building Seismic Safety Council (BSSC) of the National Institute of Building Sciences (NIBS).

## Slide 37: Masonry Behavior
On a local level, masonry behavior is nonisotropic, nonhomogeneous, and nonlinear.
On a global level, however, masonry behavior can be idealized as isotropic and homogeneous. Nonlinearity in compression is handled using an equivalent rectangular stress block as in reinforced concrete design.
A starting point for masonry behavior is to visualize it as very similar to reinforced concrete. Masonry capacity is expressed in terms of a specified compressive strength, fm, which is analogous to fc.
Notes: This slide lists basics of masonry behavior.
In the context of the TMS 402/602 Code and Specification as referenced by the NEHRP Recommended Provisions, masonry is composed of units held together by mortar. The masonry is usually reinforced (either by prescription or by design methodology), and the reinforcement is surrounded by grout. The result is an integral material very similar to reinforced concrete.

## Slide 38: ... typical materials in reinforced masonry
grout
steel reinforcing bars
units of concrete or fired clay
mortar
grout
Notes: This slide illustrates typical materials and construction of a reinforced hollow masonry wall. Modern reinforced masonry is commonly composed of hollow concrete or clay masonry units, jointed together by cementitious mortar. Deformed reinforcement is placed vertically and horizontally within voids in the masonry, which are then filled with grout, a fluid concrete-like mixture.

## Slide 39: Masonry Behavior prism failure mechanism
Unit fails in tension before
Mortar fails in comp
Mortar in triaxial comp.
Mortar expands laterally
Brick units in vertical comp.
Brick units in lateral tension
nmortar > n units
Notes: This slide illustrates the stress states in masonry units and mortar under compression load.
Emphasize that the failure of a masonry prism in compression usually occurs upon a tensile splitting failure, and the restraint of the lateral expansion of the mortar is what creates the tension in the masonry unit.

## Slide 40: Masonry Behavior Stress-Strain Curve for Prism Under Compression
Masonry unit
Prism
Mortar
strain
f unit
f prism
f mortar
Notes: This slide shows a prism of masonry subject to compression, and a plot of stress on the y-axis vs. strain on the x-axis [from lowest to highest strength] of mortar, the prism assemblage, and masonry units.
Compressive stress-strain behavior is evaluated using a masonry “prism” composed of units bonded by mortar and filled with grout (if it is intended to represent grouted construction). The individual behavior of units, mortar, and grout is not nearly as important as the behavior of the composite.

## Slide 41: Masonry Behavior
Running bond
- half units
Stacked bond
- only mortar
Head joint weakness
Notes: This slide shows three illustrations. The first is a plan view of a masonry wall. The second is an elevation of a wall with stack bond, and a section showing that head joints with mortar create a continuous vertical plane. The third is an elevation of a wall with running bond, and a section showing that head joints with mortar are interrupted by units in a vertical plane.
Head joints are weak because the mortar shrinks. In contrast to bed joints, there is no gravity action to maintain the contact.

## Slide 42: Masonry Behavior
Lack of ties between wythes
Notes: This slide shows a picture of a multi-wythe brick wall with no ties between wythes.
A multi-wythe wall may act as a composite wall, or it may act as a series of parallel thin walls.

## Slide 43: Masonry Behavior
Typical grout-block separation due to drying shrinkage
Notes: This slide shows a picture of a concrete block with grouted cells, where the grout has pulled away from the unit at the interface.
Slide shows photograph of grout-block separation.

## Slide 44: Masonry Behavior
Admixture
Vibrated
Vibrated
Admixture
Puddled
Puddled
Notes: This slide shows pictures of sections through grouted walls with grout consolidated by [from left to right] puddling, admixtures and puddling, vibration, and admixture and vibrations. The number of cracks in the grout decrease from left to right.
Slide shoes various defects in grouted wall.

## Slide 45: Masonry Behavior
Crowded cells make grout flow difficult
Notes: Slide shows cell with congested reinforcement making it difficult to flow grout into place.

## Slide 46: Masonry Behavior
Spalled face shells on solid grouted wall
Notes: Slide shows photo of masonry wall with spalled face shells.

## Slide 47: Masonry Behavior: Short Wall in plane
Unreinforced
With
horizontal
reinforcement
Truss analogy:
Notes: This slide shows illustrations of two masonry walls subject to in plane shear force. The unreinforced wall separates and slides in a stair-step pattern. The wall with horizontal reinforcing has distributed diagonal cracks. An illustration of a vertical truss with horizontal force applied is shown adjacent to the reinforced wall.
The truss analogy is that vertical and diagonal struts of masonry resist compression in conjunction with horizontal and vertical tension ties of rebar.

## Slide 48: Masonry Behavior: Tall Wall in-plane
RM
URM
Notes: This slide shows illustrations of tall unreinforced and reinforced wall piers subject to in plane shear force. The unreinforced wall is shown rocking as a rigid body. The reinforced wall is shown with high compressive stresses in the bottom corner of the wall and moment developed at the base.
If unreinforced masonry does not fail in shear or slide, it will rock (overturn). If the masonry is reinforced, the vertical steel forms a couple with masonry in compression to resist the overturning moment.

## Slide 49: Reinforced Masonry/Behavior in Flexure hysteresis
Notes: This slide shows hysteresis plots for an unconfined and a confined wall subject to flexure.
Reinforced masonry is relatively ductile in bending. The confinement figure is not particularly pertinent, as it is difficult to confine masonry.

## Slide 50: Masonry Behavior: out-of-plane
flexural
strength
anchorage
Notes: Slide shows possible out-of-plane failures (flexural strength and anchorage failures) in masonry walls, which includes a figure of masonry wall, a masonry all fail with flexural failure, and a masonry wall fail with anchorage failure.

## Slide 51: Masonry Behavior
Out-of-plane wall failure
Notes: Slide shows photo of house with out-of-plane masonry wall failures.

## Slide 52: Summary of Masonry Behavior
4-Way Composite Action
Units, mortar, reinforcement, grout
Compression
High strength
Brittle -- low ductility
Confinement difficult to achieve
Tension
Good strength when reinf. takes tension
Very little strength without reinf.
(continuous joints are a plane of weakness)
Notes: This slide lists a summary of masonry behavior.
Summary of Masonry Behavior

## Slide 53: Design Implications from Masonry Behavior
Unreinforced
Design as elastic / brittle material
R factors very low
Design force = EQ force
Reinforced
Design similar to reinforced concrete
Confinement, ductility difficult to achieve
R factors lower than concrete
Notes: This slide lists design implications for masonry structures
Design implications for masonry structures

## Slide 54: NEHRP Recommended Provisions Masonry Design
Organization of TMS 402 Code
Notes: This slide is the introduction slide to the section of the presentation on Organization of TMS 402 Code.
This is a list of topics covered in this review module on masonry design according to the NEHRP Recommended Provisions, which is developed for the Federal Emergency Management Agency (FEMA) by the Building Seismic Safety Council (BSSC) of the National Institute of Building Sciences (NIBS).

## Slide 55: Seismic Design for Masonry Hierarchy of Standards
NEHRP
Recommended
Provisions
ASCE7
ASCE/SEI
TMS 402
MSJC
IBC
ICC
Building Code
Local law
ASTM Standards
Material & Test Methods
TMS 602
MSJC
Project Documents
Dwgs & Specs
TMS 402
TMS 602
Notes: Slide is a diagram of design standards used for Masonry structures.

## Slide 56: What is the TMS 402 Code and TMS 602 Specification... ?
2013 TMS 402
Code and
TMS 602
Specification
ASCE
(ASCE 5-13)
(ASCE 6-13)
TMS
(TMS 402-13)
(TMS 602-13)
ACI
(ACI 530-13)
(ACI 530.1-13)
MSJC = Masonry Standards Joint Committee
One committee
One code
Three designations
Notes: This slide shows the different organizations that participate in developing the TMS 402 Code and TMS 602 Specification.
The NEHRP Recommended Provisions reference TMS 402 and 602. That document is developed under ANSI-consensus rules by the Masonry Standards Joint Committee, which is sponsored jointly by The Masonry Society, The American Concrete Institute, and The American Society of Civil Engineers.
Starting with the 2016 edition, The Masonry Society will be the sole sponsor of the document and the Masonry Standards Joint Committee will no longer exist. ACI 530 and ASCE 5 and 6 will no longer be current standards. For this reason, the code and specification will be referred to as TMS 402 and TMS 602 throughout this presentation.

## Slide 57: Organization of 2013 TMS 402 Code
Part 1, General
Chapters 1-3
Ch. 8,
Allowable
Stress
Design
Ch. 9, Strength Design
Ch. 10,
Pre-
stressed
Masonry
Ch. 12,
Veneer
Ch. 13,
Glass
Block
Ch. 14,
Partitions
8.1, General ASD
8.2, URM
8.3, RM
6.1, General
6.2, Anchored
6.3, Adhered
9.1, General SD
9.2, URM
9.3, RM
TMS 602
Specification
Ch. 11, AAC
Part 2, Design Requirements
Chapters 4-7 (Analysis and Design, Elements,
Reinforcement, Seismic)
Part 3, Engineered Design Methods
Chapters 8-11
Part 4, Prescriptive Design Methods
Chapters 12-14
Appendices
A, B, and C
Notes: This slide shows the organization of TMS 402.
This slide shows the organization of TMS 402. It is linked to the TMS 602 Specification.
TMS 402-13 has been significantly reorganized from previous editions. It is now divided into four main parts; General, Design Requirements, Engineered Design Methods, and Prescriptive Design Methods.

## Slide 58: Organization of 2013 TMS 602 Specification
TMS 402 Code
Part 1
General
Part 2
Products
Part 3
Execution
1.6 Quality
assurance
3.1 - Inspection
3.2 - Preparation
3.3 - Masonry erection
3.4 - Reinforcement
3.5 - Grout placement
3.6 - Prestressing
3.7 - Field quality control
3.8 - Cleaning
2.1- Mortar
2.2 - Grout
2.3 - Masonry Units
2.4 - Reinforcement
2.5 - Accessories
2.6 - Mixing
2.7 - Fabrication
TMS 602
Specification
Notes: This slide shows the organization of TMS 602.
TMS 602 is referenced by and linked to TMS 402. The Specification has three articles governing general provisions, products, and execution, respectively.

## Slide 59: Relation Between Code and Specification
Code:
  Design provisions are given in Chapters 1-14 and Appendices A, B, and C
  Section 1.4 invokes the specification by reference.
  Section 3.1 requires a QA program in accordance with the specification
Specification:
  Section 3.7 verify compliance with specified fm
  Comply with required level of quality assurance
  Comply with specified products and execution
Notes: This slide lists the connections between the code and the specification.
TMS 402 references and is intended to be used with TMS 602.
In the Code, design provisions are given in Chapters 1 through 14 and Appendices A, B, and C. Section 3.1 requires a QA program in accordance with the Specification. Section 1.4 invokes the Specification by reference.
The Specifications requires verification of compliance with specified fm; compliance with the required level of quality assurance; and compliance with the specified products and execution.

## Slide 60: Organization of TMS 402 Code Part 1 – General
Chapter 2
2.1 Notation
2.2 Definitions
Chapter 3
3.1 Quality assurance program
3.2 Construction
Chapter 1
1.1 Scope
1.2 Contract documents and calculations
1.3 Special systems
1.4 Reference standards
Notes: This slide lists the sections in Part 1 of TMS 402
Part 1 of TMS 402 gives general requirements, notation and definitions, and QA and Construction requirements. As with other slides, the sections marked in orange are emphasized in the slides that immediately follow.

## Slide 61: Code 3.1, Quality Assurance
Requires a quality assurance program in accordance with the TMS 602 Specification:
  Three levels of quality assurance (A, B, C)
  Compliance with specified fm
  Increasing levels of quality assurance require increasingly strict requirements for inspection, and for compliance with specified products and execution
Notes: This slide is a summary of the quality assurance provisions in TMS 402.
Section 3.1 of TMS 402 requires a quality assurance program in accordance with the Specification. The section contemplates three levels of quality assurance (A, B, C): compliance with specified fm, increasing levels of quality assurance with increasingly strict requirements for inspection, and for compliance with specified products and execution.

## Slide 62: Code 3.1, Quality Assurance
Minimum requirements for inspection, tests, and submittals:
  Empirically designed masonry, veneers, or glass unit masonry
    Table 3.1.1 for Risk Category I, II, and III facilities
    Table 3.1.2 for Risk Category IV facilities
  Engineered plain, reinforced, or prestressed masonry
    Table 3.1.2 for Risk Category I, II, and III facilities
    Table 3.1.3 for Risk Category IV facilities
Notes: This slide is a summary of the quality assurance provisions in TMS 402.
Section 3.1 of TMS 402 gives minimum requirements for inspection, tests, and submittals.

## Slide 63: Code 3.2, Construction
Minimum grout space (Table 3.2.1)
Embedded conduits, pipes, and sleeves:
  Consider effect of openings in design
  Masonry alone resists loads
Notes: This slide is a summary of the construction provisions in TMS 402.
That section specifies a minimum grout spacing (Table 3.2.1).
With respect to embedded conduits, pipes and sleeves, it requires that the effects of openings be considered in design and that masonry alone be considered effective in resisting loads.
With respect to anchorage of masonry to structural members, frames and other construction, it requires that the type, size, and location of connectors be shown on drawings.

## Slide 64: Organization of TMS 402 Code Part 2 – Design Requirements
Chapter 4
4.1 Loading
4.2 Material properties
4.3 Section properties
4.4 Connections to structural frames
4.5 Stack bond masonry
Chapter 5
5.1 Masonry assemblies
5.2 Beams
5.3 Columns
5.4 Pilasters
5.5 Corbels
Chapter 6
6.1 Details of reinforcement
6.2 Anchor bolts
Chapter 7
Seismic design requirements
Notes: This slide lists the sections in Part 2 of TMS 402
Part 2 of TMS 402 gives design requirements and criteria that apply independent of which analysis method is used.

## Slide 65: Code 4.2, Material Properties
Prescriptive modulus of elasticity:
  Em = 700 f’m for clay masonry
  Em = 900 f’m for concrete masonry
  or
  Chord modulus of elasticity from tests
Shear modulus, thermal expansion coefficients, and creep coefficients for clay, concrete, and AAC masonry
Moisture expansion coefficient for clay masonry
Shrinkage coefficients for concrete and AAC masonry
Notes: This slide is a summary of the material property provisions in TMS 402.
Code Section 4.2 deals with material properties to be used for design. It specifies the values of chord modulus of elasticity, shear modulus, thermal expansion coefficients, and creep coefficients for clay, concrete, and AAC masonry. It also gives moisture expansion coefficients to be used for clay masonry and shrinkage coefficients to be used for concrete and AAC masonry.

## Slide 66: Code 4.3, Section Properties
Use minimum (critical) area for computing member stresses or capacities
  Capacity is governed by the weakest section; for example, the bed joints of face-shell bedded hollow masonry
Notes:   The figure shows the bed joints of face-shell bedded hollow masonry.
TMS 402 uses two different ways of computing section properties. To compute member stresses or capacities, use the weakest section. For hollow unit masonry bedded on the outside only (face-shell bedding), this is the area of the face shells only.

## Slide 67: Code 4.3, Section Properties
Radius of gyration and member slenderness are better represented by the average section
For example, the net area of units rather than just the bed-joint area of face-shell bedded masonry
Notes:   This pictures shows a basic masonry unit.
This slide is a summary of the section property provisions in TMS 402.
For computing slenderness-related properties, use the average section (the net area of units of face-shell bedded masonry).

## Slide 68: Code 6.1, Details of Reinforcement
Reinforcing bars must be embedded in grout; joint reinforcement can be embedded in mortar
Placement of reinforcement
Protection for reinforcement
Standard hooks
Notes: This slide is a summary of the details of reinforcement provisions in TMS 402.
Reinforcing bars must be embedded in grout; joint reinforcement can be embedded in mortar. Minimum distances between reinforcement and the insides of cells or void spaces are specified as are minimum cover distances for protection of reinforcement from corrosion. Standard hooks are defined.

## Slide 69: Chapter 7, Seismic Design
Seismic requirements for masonry structures:
  Improves ductility of masonry members
  Improves connectivity in masonry structures
Not applicable to:
  Glass unit masonry
  Veneers
Notes: This slide is a summary of the seismic design provisions in TMS 402 and where they are applicable.
Chapter 7 applies to all masonry except glass unit masonry and veneers. It seeks to improve performance of masonry structures in earthquakes by improving the ductility of masonry members and the connectivity of masonry members.
Seismic requirements for autoclaved aerated concrete (AAC) masonry are somewhat different and are not addressed in this presentation.

## Slide 70: Chapter 7, Seismic Design
Define a structure’s Seismic Design Category (SDC) according to ASCE 7-10
  SDC depends on seismic risk (geographic location), underlying soil, importance
  SDCs are A, B, C, D, E, or F
SDC determines
  Required types of shear walls (prescriptive reinforcement)
  Prescriptive reinforcement for other masonry elements
  Permitted design approaches for LFRS (lateral force-resisting system)
Notes: This slide is a summary of the seismic design provisions in TMS 402.
In Chapter 7, the structure’s Seismic Design Category (SDC) is defined according to ASCE 7. The SDC depends on seismic risk (geographic location), importance, and underlying soil.
The SDC determines the required types of shear walls (prescriptive reinforcement); the prescriptive reinforcement required for other masonry elements; and the permitted design approaches for LFRS (lateral force-resisting system).

## Slide 71: Chapter 7, Seismic Design
Requirements for SDCs are cumulative; requirements in each “higher” category are added to requirements in the previous category:
  SDC A = minimum requirements
  SDC B = A + more
  SDC C = A + B + more
  SDC D = A + B + C + more
  etc…
Notes: This slide is a summary of the seismic design provisions in TMS 402.
Seismic design requirements are keyed to ASCE 7 Seismic Design Categories (from A up to F). Requirements are cumulative; requirements in each “higher” category are added to requirements in the previous category.

## Slide 72: Chapter 7, Seismic Design
Shear walls must meet minimum prescriptive requirements for reinforcement and connections (ordinary reinforced, intermediate reinforced, or special reinforced)
Notes: This slide is a summary of the seismic design provisions in TMS 402.
Seismic design requirements are keyed to ASCE 7 Seismic Design Categories (from A up to F). Requirements are cumulative; requirements in each “higher” category are added to requirements in the previous category.

## Slide 73: Chapter 7, Seismic Design
General analysis
  Element interaction
  Refer to ASCE7-10, Sec. 1.4, General Structural Integrity:
    Load path connections
    Notional lateral forces
    Connection to supports
    Anchorage of walls
Notes: This slide is a summary of the general analysis seismic design provisions in TMS 402.
Basics of seismic design

## Slide 74: Chapter 7, Seismic Design
General analysis
  Drift limits: Use legally adopted building code or ASCE7
  Drift limits assumed satisfied for many wall types
    Special Reinforced Masonry walls are the exception to this rule
Notes: This slide is a summary of the general analysis seismic design provisions in TMS 402.
Basics of seismic design.

## Slide 75: Chapter 7, Seismic Design
Element classification
  Participating
    Part of the seismic force-resisting system
  Non-participating
    Non-participating walls must be isolated from the participating seismic force-resisting system (except as required for gravity support)
Notes: This slide is a summary of the element classification seismic design provisions in TMS 402.
Basics of seismic design.

## Slide 76: Chapter 7, Seismic Design
Seismic Design Category A:
  All types of shear walls permitted:
    Empirical
    Plain
      Ordinary plain: Unreinforced
      Detailed Plain: Has minimum reinforcement
    Ordinary reinforced
    Intermediate reinforced
    Special reinforced
Notes: This slide is a summary of the seismic design provisions in TMS 402 for SDC A.
In Seismic Design Category A, a drift limit of 0.007 and a minimum design connection force are imposed for wall-to-roof and wall-to-floor connections.

## Slide 77: Chapter 7, Seismic Design
Seismic Design Category B:
  Empirical design not permitted, all other types of shear walls permitted:
    Plain
      Ordinary plain
      Detailed plain
    Ordinary reinforced
    Intermediate reinforced
    Special reinforced
Notes: This slide is a summary of the seismic design provisions in TMS 402 for SDC B.
In Seismic Design Category B, the lateral force resisting system cannot be designed empirically.

## Slide 78: Chapter 7, Seismic Design
Seismic Design Category C:
  Empirical and plain not permitted, all other types of shear walls permitted:
    Ordinary reinforced
    Intermediate reinforced
    Special reinforced
  Participating walls shall be reinforced
  Non-participating walls must meet minimum prescriptive requirements for horizontal or vertical reinforcement
  At least 80% of lateral resistance in a given line shall be by shear walls
Notes: This slide is a summary of the seismic design provisions in TMS 402 for SDC C.
In Seismic Design Category C, all walls must be considered shear walls unless isolated. Shear walls must meet minimum prescriptive requirements for reinforcement and connections (ordinary reinforced, intermediate reinforced, or special reinforced) and other walls must meet minimum prescriptive requirements for horizontal or vertical reinforcement.

## Slide 79: Chapter 7, Seismic Design
Seismic Design Category D:
  Only special reinforced type of shear wall permitted
  Shear walls must meet minimum prescriptive requirements for reinforcement and connections (special reinforced)
  Type N mortar and masonry cement mortars are prohibited in the lateral force-resisting system
  “Non-participating” walls must meet minimum prescriptive requirements for horizontal and vertical reinforcement
Notes: This slide is a summary of the seismic design provisions in TMS 402 for SDC D.
In Seismic Design Category D, masonry that is part of the lateral force resisting system must be reinforced so that v + h  0.002, and v and h  0.0007. Type N mortar and masonry cement mortars are prohibited in the lateral force resisting system. Shear walls must meet minimum prescriptive requirements for reinforcement and connections (special reinforced) and other walls must meet minimum prescriptive requirements for horizontal and vertical reinforcement.

## Slide 80: Chapter 7, Seismic Design
Seismic Design Category D:
Extra caution against brittle shear failure for Special Reinforced Masonry Shear Walls (7.3.2.6.1.1):
  Design shear strength shall exceed the shear corresponding to the development of 1.25 times the nominal flexural strength, but
  nominal shear strength need not exceed 2.5 times required shear strength
Notes: This slide is a summary of the seismic design provisions in TMS 402 for SDC D.
Basics of seismic design.

## Slide 81: Minimum Reinforcement for Special Reinforced Shear Walls
roof
diaphragm
roof connectors
@ 48 in. max oc
#4 bar (min) within
16 in. of top of parapet
Top of Parapet
#4 bar (min) @ diaphragms continuous through control joint
#4 bar (min) within 8 in. of all control joints
control joint
Min. #4 bars @ 4 ft oc max. or W1.7 @ 16 in oc
Min. #4 bars @ 4 ft oc max.
#4 bar (min) within 16 in. of corners & ends of walls
24 in. or 40 db past opening
#4 bars around openings
r total both ways = 0.002
Notes: This slide illustrates the minimum reinforcement requirements for special reinforced masonry shear walls.

## Slide 82: Chapter 7, Seismic Design
Seismic Design Categories E and F:
  Additional reinforcement requirements for non-participating stack-bond masonry
Notes: This slide is a summary of the seismic design provisions in TMS 402 for SDC E and F.
In Seismic Design Categories E and F, additional requirements are imposed for stack-bond masonry because it is inherently weaker in flexure across continuous head joints.

## Slide 83: Minimum Reinforcement, SW Types
SW Type | Minimum Reinforcement | Permitted in SDC
Empirically Designed | none | A
Ordinary Plain | none | A, B
Detailed Plain | Vertical reinforcement = #4 at corners, within 16 in. of openings, within 8 in. of movement joints, maximum spacing 10 ft; horizontal reinforcement W1.7 @ 16 in. or #4 in bond beams @ 10 ft | A, B
Ordinary Reinforced | same as above | A, B, C
Intermediate Reinforced | same as above, but vertical reinforcement @ 4 ft | A, B, C
Special Reinforced | same as above, but horizontal reinforcement @ 4 ft, and  ≥ 0.002 (sum of horiz + vert) | A,B,C,D, E, F
Notes: This slide summarizes the requirements for different shear wall types and the Seismic Design Categories in which each type is permitted to be used.

## Slide 84: Organization of TMS 402 Code Chapter 9, Strength Design
Bearing strength
Compressive strength
Modulus of rupture
Strength of reinforcement
Unreinforced masonry
Reinforced masonry
Fundamental basis
Design strength
f factors
Deformation requirements
Anchor bolts
Notes: This slide lists the content in Chapter 9 of TMS 402, Strength Design
Now let’s move to Chapter 9 of TMS 402 dealing with strength design. It is this chapter that first addresses the fundamental basis for strength design.

## Slide 85: Fundamental Basis for Strength Design
Factored design actions must not exceed nominal capacities, reduced by f factors
Load factors come from ASCE7
Quotient of load factor divided by f factor is analogous to safety factor of allowable-stress design, and should be comparable to that safety factor.
Notes: This slide lists fundamental basics for strength design.
Factored design actions must not exceed nominal capacities, reduced by f factors. The quotient of load factor divided by f factor is analogous to safety factor of allowable stress design and should be comparable to that safety factor.

## Slide 86: Code 9.1.3, Design Strength for Strength Design
Design strength (f x nominal strength) must equal or exceed required strength
Notes: This slide discusses the requirement for design strength in strength design.
The design strength must exceed required strength.
To give additional protection against brittle shear failure, the design shear strength for special reinforced masonry shear walls must exceed the shear corresponding to the development of 1.25 times the nominal flexural strength (capacity design). The nominal shear strength need not, however, exceed 2.5 times the required shear strength.

## Slide 87: Code 9.1.4, Strength-reduction Factors (f) for Strength Design
Action | Reinforced Masonry | Unreinforced Masonry
combinations of flexure and axial load | 0.90 | 0.60
shear | 0.80 | 0.80
bearing | 0.60 | 0.60
Notes: The table of this slide summarizes the capacity reduction factors used by TMS 402. For reinforced masonry, they are quite similar to those of ACI 318.

## Slide 88: Code 9.1.4, Strength-Reduction Factors (f) for Strength Design for Anchor Bolts
Capacity of Anchor Bolts as Governed by | Strength-Reduction Factor
steel yield and fracture | 0.90
masonry breakout, crushing, or pryout | 0.50
pullout | 0.65
Notes: This slide summarizes capacity reduction factors for the design of anchor bolts.

## Slide 89: Code 9.1.5, Deformation Requirements
Note drift limits from ASCE 7-10 Table 12.12.1
Deflections of unreinforced masonry (URM) based on uncracked sections
Deflections of reinforced masonry (RM) shall consider the effects of cracking
Notes: This slide lists deformation requirements for shear walls.
TMS 402 imposes the drift limits of ASCE 7-10. It requires that deflections of unreinforced masonry be based on uncracked sections and that deflections of reinforced masonry be based on cracked sections.

## Slide 90: Code 9.1.6, Anchor Bolts
Tensile capacity controlled by:
  Tensile breakout
  Yield of anchor in tension
  Tensile pullout (bent-bar anchor bolts only)
Shear capacity controlled by:
  Shear breakout
  Masonry crushing
  Anchor pry-out
  Yield of anchor in shear
For combined tension and shear, use linear interaction
Notes: This slide lists limit states for anchor bolts.
Tensile capacity is governed by tensile breakout, by yield of the anchor in tension, and by tensile pullout (for bent-bar anchor bolts only).
Shear capacity is governed by shear breakout and by yield of the anchor in shear.
Combined tension and shear are conservatively handled using a linear interaction relationship.

## Slide 91: Code 9.1.9.1.1, Compressive Strength of Masonry
For concrete masonry, 1500 psi ≤ fm ≤ 4000 psi
For clay masonry, 1500 psi ≤ fm ≤ 6000 psi
Notes: This slide lists ranges of masonry compressive strength that the strength design provisions apply to.
Compressive strength of masonry. Remember that with the adoption of TMS 402-13, the default strength of new concrete masonry will be 2000 psi using Type S mortar.

## Slide 92: Code 9.1.9.2, Modulus of Rupture
In-plane and out-of-plane bending
  Table 9.1.9.2
  Lower values for masonry cement and air-entrained portland cement-lime mortar
  Higher values for grouted masonry
  For grouted stack-bond masonry, fr = 335 psi parallel to bed joints for continuous horizontal grout section (i.e., fully grouted wall)
Notes: This slide lists information on modulus of rupture of walls.
TMS 402 specifies identical values of the modulus of rupture for in-plane and out-of-plane bending (Table 9.1.9.2). Modulus of rupture values are lower for masonry cement and air-entrained portland cement-lime mortar and are higher for grouted masonry. For grouted stack-bond masonry, fr = 335 psi parallel to bed joints.

## Slide 93: Code 9.1.9.3, Strength of Reinforcement
fy  60 ksi
Actual yield strength shall not exceed 1.3 times the specified value
Notes: This slide discusses the strength of reinforcement.
The specified yield strength of reinforcement is not to be taken in excess of 60 ksi.
The actual yield strength is not to exceed 1.3 times the specified value (to avoid excesses of actual flexural capacity, which can lead to excessive shear demand).

## Slide 94: Code 9.3, Reinforced Masonry
Masonry in flexural tension is cracked
Reinforcing steel is needed to resist tension
Similar to strength design of reinforced concrete
Compressive strength of reinforcement shall be ignored unless the reinforcement is tied in compliance with Code 5.3.1.4
Notes: This slide lists assumptions made for reinforced masonry for TMS 402.
Masonry in flexural tension is considered to be cracked. Flexural tension is to be resisted entirely by reinforcing steel. Design is similar to strength design of reinforced concrete.
The compressive strength of reinforcement is to be ignored unless the reinforcement is tied in compliance with Code 5.3.1.4.

## Slide 95: Code 9.3, Reinforced Masonry
9.3.2 Design assumptions
9.3.3 Reinforcement requirements and details, including maximum steel area
9.3.4 Design of piers, beams and columns:
  Nominal axial and flexural strength
  Nominal shear strength
9.3.5 Design of walls for out-of-plane loads
9.3.6 Design of walls for in-plane loads
Notes: This slide lists the sections within the TMS 402 reinforced masonry provisions.
Section 9.3 of TMS 402 deals in detail with the assumptions underlying strength design of reinforced masonry:
Section 9.3.3 addresses reinforcement requirements and details, including maximum steel percentage.
Section 9.3.4 addresses design of piers, beams and columns, including nominal axial and flexural strength and nominal shear strength
Section 9.3.5 addresses design of walls for out-of-plane loads.
Section 9.3.6 addresses design of walls for in-plane loads.
Let’s look at each of these in more detail.

## Slide 96: Code 9.3.2, Design Assumptions
Continuity between reinforcement and grout
Equilibrium
mu = 0.0035 for clay masonry, 0.0025 for concrete masonry
Plane sections remain plane
Elasto-plastic stress-strain curve for reinforcement
Tensile strength of masonry is neglected
Equivalent rectangular compressive stress block in masonry, with a height of 0.80 fm and a depth of a = 0.80 c
Notes: This section lists design assumptions for reinforced masonry per TMS 402.
The basic assumptions of flexural design in reinforced masonry are quite similar to those of reinforced concrete.
Continuity between reinforcement and grout is assumed. Equilibrium must be satisfied. The maximum usable strain is to be taken as mu = 0.0035 for clay masonry and 0.0025 for concrete masonry.
Plane sections are assumed to remain plane. An elastoplastic stress-strain curve is used for for reinforcement; and the tensile strength of masonry is to be neglected.
The compressive stress block is idealized as an equivalent rectangle with a height of 0.80 fm and a depth of 0.80 c.

## Slide 97: Code 9.3.2 Flexural Assumptions
Locate neutral axis based on extreme-fiber strains
Calculate compressive force, C
C = P + T
M =  Fi yi (sum moments about centroid of compressive stress block)
mu = 0.0035 clay
0.0025 concrete
s  y
fy
Reinforcement
P
0.80 fm
M
a = 0.8c
c
a
C
T
Notes: The figure shows the stain distribution and equivalent rectangular stress block for the flexural design of reinforced masonry.
This slide summarizes how those flexural assumptions are applied. As will be discussed subsequently, sections are required to be tension-controlled so the strain gradient varies across the depth of the cross-section from the maximum useful strain in the masonry to a steel strain at least equal to yield. Reinforcement is considered to be elastoplastic. The equivalent rectangular stress block is taken as shown.
The axial force in the cross-section is computed as the difference between the compressive and the tensile forces, and the moment is computed as the summation of each of those forces times its respective distance from the plastic centroid (usually the centerline) of the cross-section.
For concrete and masonry design, the plastic centroid is defined as the line of action of the resultant force in the cross-section corresponding to a uniform compressive strain equal to the maximum useful strain in the concrete or masonry.

## Slide 98: Code 9.3.3, Reinforcement Requirements and Details
Bar diameter  1 / 8 nominal wall thickness
Standard hooks and development length:
  Development length based on pullout and splitting
In walls, shear reinforcement shall be bent around extreme longitudinal bars
Splices:
  Lap splices based on required development length
  Welded and mechanical splices must develop 1.25 fy
Notes: This slide lists reinforcement requirements and details.
Section 9.3.3 of TMS 402 addresses reinforcement requirements and details.
The diameter of reinforcement in eighths of an inch must not exceed 1/8 the nominal wall thickness. For example, in a nominal 8-in. wall, reinforcement must not be larger in diameter than #8 (nominal diameter 8/8 inch). This is intended to prevent failure by the masonry by splitting along the bar.
Standard hooks are defined. Development length is based on pullout and on splitting (bar-to-cover and bar-to-bar). In walls, shear reinforcement must be bent around extreme longitudinal bars (intended to increase the effectiveness of the hooks).
Required splice length is based on required development length; welded and mechanical splices must develop 1.25 fy .

## Slide 99: Code 9.3.3.5, Maximum Reinforcement (Flexural Ductility Check)
a = 1.5 Ordinary
3 Intermediate
4 Special
mu = 0.0035 clay
0.0025 concrete
C
T
s = y
fy
Reinforcement
0.80 fm
Does not apply if Mu/Vud <1.0 and R ≤1.5
Locate neutral axis based on extreme-fiber strains
Calculate compressive force, C (may include compressive reinforcement)
Tensile reinforcement + axial load = C
Notes: The figure shows the stain distribution and equivalent rectangular stress block for the flexural design of reinforced masonry.
This slide discusses the maximum reinforcement allowed and shows stress and strain distributions over a wall section subject to axial load and flexure.
This slide illustrates the principle behind the maximum reinforcement limitations of Section 9.3.3.5 of TMS 402. Assumed is a critical strain gradient, whose maximum value on the compression side of the element is the maximum useful strain in masonry and whose maximum value on the tension side of the element is a multiple of the specified yield strain in that reinforcement. That multiple depends on the expected flexural ductility demand on the element. In contrast to the calculation of flexural capacity, the contribution of compressive reinforcement can be considered.
That critical gradient defines the location of the neutral axis and the dimensions of the compressive stress block. That, in turn, gives the maximum compressive capacity of that block. The combination of tensile steel area (acting at a stress limited by fy) and axial compression must not exceed that compressive capacity. The intent of this provision is to prevent compressive crushing of that block and, therefore, ensure tension-controlled behavior.

## Slide 100: Code 9.3.4, Design of Beams, Piers, and Columns
Slenderness is addressed by multiplying axial capacity by slenderness-dependent modification factors
Notes: This slide discusses slenderness of piers and columns.
TMS 402 does not use moment magnifiers for piers or columns. Slenderness is addressed by multiplying axial capacity by slenderness-dependent modification factors. Since axial loads are usually quite low compared to axial capacity in concentric compression, slenderness effects are usually not significant.

## Slide 101: Code 9.3.4, Nominal Shear Strength Basis for requirements
With
horizontal
reinforcement
Truss analogy:
  Objectives:
  Avoid crushing of diagonal strut
  Preclude critical (brittle) shear- related failures
Notes: Figure shows truss analogy for developing shear strength in wall.

## Slide 102: Code 9.3.4, Nominal Shear Strength
Vn = (Vnm + Vns)gg
Vn shall not exceed:
  Mu / Vu dv  0.25 Vn  6 An  fm
  Mu / Vu dv  1.0 Vn  4 An  fm
  Linear interpolation between these extremes
  Objective is to avoid crushing of diagonal strut
  Objective is to preclude critical (brittle) shear-related failures
gg = 1.0 for fully grouted walls
= 0.75 for partially grouted walls
Notes: This slide shows the equation and limits for nominal shear strength.
Section 9.3.4 of TMS 402 addresses nominal shear strength of reinforced masonry in a way that is quite similar to design of reinforced concrete. Nominal shear resistance is taken as the summation of resistance from masonry, plus resistance from shear reinforcement, multiplied by a gg factor to account for lower tested strength in partially grouted walls. To prevent diagonal crushing of masonry, upper limits are imposed on Vn (and thereby on Vs).

## Slide 103: Code 9.3.4, Nominal Shear Strength
Empirical – from research
(9-25)
(9-24)
Vm and Vs are given by:
Notes: This slide gives the equations for shear strength of the masonry and of the reinforcing steel.
Nominal shear resistance due to masonry depends on the aspect ratio of the element, and varies from 2.25 to 4 times the product of the square root of f’m, and the cross-sectional area of the element.
Nominal shear resistance due to shear reinforcement is computed similarly to reinforced concrete as the product of the number of layers of shear reinforcement crossing a 45-degree crack, the cross-sectional area of each layer of reinforcement, and the specified tensile yield strength of the reinforcement. TMS 402 uses an efficiency factor to account for the fact that shear reinforcement does not yield uniformly over the height of a wall element.

## Slide 104: Code 9.3.4.2, Requirements for Beams
Pu  0.05 An fm
Mn  1.3 Mcr (To prevent brittle failures in lightly- reinforced beams)
Lateral bracing spaced at most 32 times beam width (5.2.1.2)
Nominal depth not less than 8 in.
Additional requirements for deep beams (5.2.2)
Notes: This slide lists requirements for beams.
Section 9.3.4 2 of TMS 402 addresses requirements for beams, defined as elements whose design axial load is low. To prevent brittle fracture of tensile reinforcement following flexural cracking, nominal capacity is required to be at least equal to 1.3 times the computed cracking capacity. To prevent lateral-torsional buckling, lateral bracing is required to be spaced at most 32 times the beam width. To ensure reasonable flexural capacity, the total depth (nominal dimension) cannot be less than 8 in. Deep beam provisions have been added to account for nonlinear stress variations over the height of the section when aspect rations are small.

## Slide 105: Code 9.3.4.3, Requirements for Piers
Vertically spanning portion of wall next to opening
Pu  0.3 An fm
Nominal thickness 16 in. max. *
Nominal plan length between 3 and 6 times the nominal thickness *
Lateral support spacing requirements*
Pier designation removed in TMS 402-16
* Judgment-based dimensions - intended to distinguish piers from walls and to prevent local buckling
Notes: This slide lists requirements for piers.
In the context of TMS 402 and TMS 602, a “pier” is a vertical spanning portion of a wall adjacent to an opening resisting axial compression and meeting certain geometric criteria.
For piers, design axial load cannot exceed 0.3 An fm. The nominal thickness must be between 6 and 16 in. The nominal plan length must be between 3 and 6 times the nominal thickness. The clear height must not be more than 5 times the nominal plan length.
The pier designation has been removed from TMS 402 starting with the 2016 edition. Vertical elements should be designed as walls, columns, or pilasters once the 2016 standard is adopted.

## Slide 106: Requirements for Columns
Isolated elements (wall segments are not columns)
No separate requirements for ASD vs. Strength Design, all provisions in Section 5.3
g  0.0025 (1.14.1)
g  0.04 (1.14.1, and also meet Code 3.3.3.5
Lateral ties in accordance with Code 2.1.6.5
Solid-grouted
Least cross-section dimension  8 in.
Notes: This slide lists requirements for columns.
In the context of TMS 402 and TMS 602, a “column” is an isolated structural element resisting axial compression, and meeting certain geometric criteria. Wall segments are normally not columns. There are no separate requirements for a column if it is designed using ASD or strength design, so all the provisions are common to all columns and are found in Chapter 5, Section 5.3.
Columns must have a ratio of total longitudinal reinforcement to gross cross-sectional area between 0.0025 and 0.04. They must meet maximum flexural reinforcement requirements of Section 9.3.3.5 of TMS 402. Longitudinal reinforcement must be supported laterally (tied). Their least cross-sectional dimension must be at least 8 in.

## Slide 107: Code 9.3.5, Design of Walls for Out-of-Plane Loads
pure flexure
Pn
Mn
pure compression
balance point
Capacity under combinations of flexure and axial load is based on the assumptions of Code 9.3.2
Interaction diagram
Note Pmax >> Pbalance
Notes: The figure shows a basic interaction diagram for masonry.
This slide discusses the design of walls for out of plane loads, and shows a basic interaction diagram for masonry.

## Slide 108: Code 9.3.5, Design of Walls for Out-of-Plane Loads
Maximum reinforcement by Code 9.3.3.5
Procedures for computing out-of-plane moments and deflections considering secondary effects (P – D) or using a moment magnifier
Note 9.3.5.4.2 – M and D equations are based on simple supports top & bottom. If other support conditions, use appropriate calculations. Don’t treat code as a cook-book!
Notes: This slide lists requirements for design of walls for out of plane loads.
Maximum reinforcement requirements are given by Section 3.3.3.5 of TMS 402. Slenderness effects are addressed (for walls loaded out of plane only) by computing a magnified moment based on computed out-of-plane deflections, or with a magnifier factor based on Euler buckling strength.

## Slide 109: Code 9.3.6, Design of Walls for In-plane Loads
pure flexure
Pn
Mn
pure compression
balance point
Pn max. per
ductility
requirement
Excluded portion
non-ductile
Capacity under combinations of flexure and axial load is based on the assumptions of Code 9.3.2
Interaction diagram:
Notes: This figure shows a basic interaction diagram for masonry. The maximum axial load on the interaction diagram is limited by ductility requirements to be below the balance point.
Flexural design of walls for in-plane loads is again handled using a strength interaction diagram. Because such walls have multiple layers of reinforcement over their depth, hand computations are tedious, and hand approximations (see design example at the end of this module) or computer spreadsheet calculations are preferable.

## Slide 110: Code 9.3.6, Design of Walls for In-plane Loads
Maximum reinforcement by Code 9.3.3.5
Vertical reinforcement not less than one-third the horizontal reinforcement
Nominal shear strength by Code 9.3.4.1.2
Notes: This slide lists requirements for the design of walls for in plane loads.
Code Section 9.3.6 addresses design of walls for in-plane loads. Maximum longitudinal (flexural) reinforcement is specified by Section 9.3.3.5. Nominal shear strength is calculated by Section 9.3.4.1.2. Vertical reinforcement must be at least one-third the horizontal reinforcement. Usually this will not govern since a certain amount of vertical reinforcement is needed to resist out-of-plane loads (see the example at the end of this module).

## Slide 111: NEHRP Recommended Provisions Masonry Design
Simplified Design for Wall-type Structures
Notes: This slide is the introduction slide for simplified design for wall-type structures.
Most practicing engineers are very familiar with the behavior of frame-type structures. Many, however, may never have formally studied the behavior of wall-type structures. For that reason, it is appropriate to review that behavior. The following series of slides presents the basic starting point for design of wall-type structures and their components.

## Slide 112: Essential Function of Walls in Resisting Lateral Forces
Vertical strips of walls perpendicular to lateral forces resist combinations of axial load and out-of-plane moments, and transfer their reactions to horizontal diaphragms
Bond beams transfer reactions from walls to horizontal diaphragms and act as diaphragm chords
Walls parallel to lateral forces act as shear walls
Notes: This slide shows a graphic of a building with horizontal load applied at the roof and distributed to the parallel walls. The perpendicular wall is highlighted for design of out of plane forces.
This slide shows how wall-type structures resist lateral loads.
Vertically spanning strips in the walls oriented perpendicular to the direction of lateral load resist combinations of axial load (from self-weight and roof bearing) and moments from out-of-plane wind.
Reactions from those strips are transferred to horizontal diaphragms that must resist in-plane shears and moments. The load transfer to diaphragms and the in-plane resistance are accomplished with the help of the bond beams that act as diaphragm chords.
The diaphragms, in turn, transfer their reactions to walls oriented parallel to the direction of lateral load, which then act as shear walls.

## Slide 113: Effect of Openings for Lateral Load Perpendicular to the Wall
Width C
Effective width of strip C
Width B
Effective width of strip B
Width A
Effective width of strip A
Strip A
Strip B
Strip C
Notes: This slide shows a graphic of a wall elevation and the effect of openings for lateral load perpendicular to the wall.
When walls oriented perpendicular to the direction of lateral load have door or window openings, these interrupt the path of vertical force transmission and change the design concept to a combination of horizontally spanning and vertically spanning strips.
The openings’ vertical strips resist the loads that act directly on them and also reactions from the horizontal strips that they support. Strip B, for example, resists loads acting on its own width and also loads from the right half of the horizontal strips at the door and from the left half of the horizontal strips at the window. Strip B therefore resists loads tributary to an effective width extending from the center of the opening to the left, to the center of the opening to the right.

## Slide 114: Effect of Openings
Openings increase most original design actions on each strip by a factor equal to the ratio of the effective width of the strip divided by the actual width
Notes: This slide discusses the effect of openings.
Openings in effect increase the original design actions on each strip by a factor equal to the ratio of the effective width of the strip divided by the actual width. This is precise for wind loads. It is usually conservative for seismic loads because the masses associated with doors and windows are often less than those associated with walls.
Basically, because the openings don’t change the loads on the wall, the wall’s required vertical reinforcement remains the same, and the designer must simply move that steel horizontally so that it does not coincide with the openings.

## Slide 115: Design of Vertical Strips in Perpendicular Walls
M = P e
M = P e / 2
Mwind, eq
~
Moments and axial forces due to combinations of gravity and lateral load
Notes: This slide shows a graphic of a building with horizontal load applied to the roof. Moment diagrams are shown for moment due to eccentricity and for wind or seismic loading.
Vertically spanning strips in walls perpendicular to the direction of lateral load are subjected to axial load and possibly to eccentric gravity load from the roof.
If the strips are assumed to be simply supported at the level of the slab, the moment diagram due to eccentric gravity load varies linearly from its maximum value at the roof, to zero at the slab. These moments must be combined with moments from out-of-plane wind and earthquake forces.
This example shows the effect on the moment diagram due to a parapet and also shows that wind can act in either direction.

## Slide 116: Design of Vertical Strips in Out-of-Plane Walls
f Pn
fMn
Mu, Pu .
Moment-axial force interaction diagram (with the help of a spreadsheet)
Notes: This slide shows a graphic of a building with horizontal load applied and an interaction diagram for masonry with point Mu, Pu within the interaction curve.
Design of the vertical strips consists simply of comparing the combination of factored design moment and axial load, with the design capacity expressed in terms of a moment-axial force interaction diagram, including the effects of phi-factors.
In such walls, axial loads are usually quite low, and the out-of-plane flexural capacity of the strips is essentially proportional to their flexural reinforcement.
Moment-axial force interaction diagrams can be computed by hand or by spreadsheet. Such walls usually have only a single layer of reinforcement at their midplane.
Because such a single layer usually cannot be supported laterally, it is not considered effective in resisting compressive stress. It is permitted to be included in computing maximum tensile reinforcement.

## Slide 117: Design of Shear Walls
P
V
h
Moments, axial forces, and shears due to combinations of gravity and lateral loads
Notes: This slide shows a graphic of a building with horizontal load applied at the roof, and an elevation of a wall of height h with axial and shear load applied to the top of wall.
Parallel walls must be designed to resist shears from the diaphragms plus moments and axial forces.

## Slide 118: Design of Shear Walls
f Pn
fMn
Mu, Pu .
Moment-axial force interaction diagram (with the help of a spreadsheet)
Notes: This slide shows a graphic of a building with horizontal load applied and an interaction diagram for masonry with point Mu, Pu within the interaction curve.
Flexural design of shear walls is expressed in terms of the relationship between combinations of factored moment and axial force and a moment-axial force interaction diagram.
The easiest way to generate such a diagram is by use of a spreadsheet in which the position of the neutral axis is moved from one side of the cross-section to the other; forces in masonry and reinforcement are computed; and the resulting axial force and moment are calculated.

## Slide 119: Design of Shear Walls
()
Shearing resistance
Per TMS 402:
Notes: This slide shows a graphic of a building with horizontal load applied and the equations for masonry shear strength.
The shear design of shear walls is quite similar to that of reinforced concrete shear walls. Nominal resistance is taken as the summation of resistance from masonry plus the resistance from shear reinforcement. A factor gg has been included to account for the lower strength values seen experimentally for partially grouted walls. Nominal resistance due to masonry is considered to vary with the aspect ratio of the element. Capacity design is required for shear walls -- they must either be designed for a design strength at least equal to 1.25 times the shear associated with development of the nominal flexural strength or for a nominal strength at least equal to 2.5 times the required shear strength.
Because the nondimensional aspect ratio need not be taken greater than 1.0, nominal resistance due to masonry varies from 2.25 to 4.0 times the product of the area and the square root of the specified compressive strength of the masonry.

## Slide 120: Distribution of Shears to Shear Walls
Classical approach
  Determine whether the diaphragm is “rigid” or “flexible”
  Carry out an appropriate analysis for shears
Notes: This slide shows a graphic of a building with horizontal load applied and a discussion of the distribution of shears to shear walls.
In designing low-rise masonry buildings for lateral load, it is also necessary to compute the distribution of lateral loads to shear walls.
The classic approach is to first determine whether the diaphragm is “rigid” or “flexible” compared to the lateral force resisting system and then to carry out the appropriate analysis for wall shears. In the next few slides, the appropriate analysis for each case is briefly explained.
At the end, however, the designer is encouraged to reduce design effort by simplifying the analysis for each case and finally by bounding the shears from each case.

## Slide 121: Classical Analysis of Structures with Rigid Diaphragms
Locate center of rigidity
Treat the lateral load as the superposition of a load acting through the center of rigidity and a torsional moment about that center of rigidity
Notes: This slide shows a graphic of a building with horizontal load applied and a discussion of the distribution of shears to shear walls.
In a structure with a rigid diaphragm, the classic approach is first to locate the “center of rigidity,” or shear center of the plan. The shear center is the point through which lateral forces must be applied so that the building will not twist in plan.
The lateral load is then decomposed into a load acting through the center of rigidity and a torsional moment about the center of rigidity.
The lateral load produces direct shears on shear walls oriented parallel to the direction of the lateral load; the torsional moment produces torsional shears on all shear walls. For each wall, direct shears and torsional shears are added to get the design shear. This process is tedious.

## Slide 122: Simplified Analysis of Structures with Rigid Diaphragms
40 ft
8 ft
40 ft
8 ft
8 ft
8 ft
8 ft
V
Consider only the shearing stiffness, which is proportional to plan length
Neglect plan torsion
  Reasonable assumption for:
  Walls well-distributed and same thickness
  Low-rise buildings
  Short, long walls
  Not valid for:
  Bldgs with large openings in walls
  Tall, narrow walls
Notes: This slide shows a plan view of a building with load applied. The building has solid wall on three elevations and two openings between wall segments on the fourth elevation. The slide also has a discussion of the distribution of shears to shear walls for a rigid diaphragm building.
This process can be simplified considerably by neglecting plan torsion. This assumption is generally valid if the building has several walls oriented in each plan direction and well-distributed about the plan perimeter. It is not valid for garage-type buildings with one side almost completely open.
For low-rise buildings, it also is possible to neglect flexural deformations because they are quite small. Considering shearing deformations only and assuming uniform wall thickness and story height, the shearing stiffness of different walls is simply proportional to their plan lengths.

## Slide 123: Simplified Analysis of Structures with Rigid Diaphragms
40 ft
8 ft
40 ft
8 ft
8 ft
8 ft
8 ft
V
Notes: This slide shows a plan view of a building with load applied. The building has solid wall on three elevations and two openings between wall segments on the fourth elevation. The slide also has a simplified distribution of shears to shear walls for a rigid diaphragm building.
Consider the building plan shown above in which the wall on the left has a plan length of 40 ft and the wall on the right is composed of three segments with a plan length of 8 ft each.
The left and right walls together have a total stiffness proportional to their total plan length of 64 ft. The wall on the left represents 40/64 (or 5/8) of that stiffness and, therefore, resists 5/8 the applied shear. The wall on the right resists the remaining 3/8 of the applied shear.

## Slide 124: Classical Analysis of Structures with Flexible Diaphragms
Distribute shears according to tributary areas of the diaphragm independent of the relative stiffnesses of the shear walls
Notes: This slide shows a graphic of a building with horizontal load applied at the roof. The slide also discusses distribution of shear for flexible diaphragm buildings.
For buildings with flexible diaphragms, the diaphragm is idealized as a simply supported beam acting in the horizontal plane and resting on the shear walls. Because the shear walls are very stiff compared to the diaphragm, the shears on the shear walls depend on the tributary areas of the diaphragm that each shear wall supports.

## Slide 125: Classical Analysis of Structures with Flexible Diaphragms
40 ft
8 ft
40 ft
8 ft
8 ft
8 ft
8 ft
half
half
V
Notes: This slide shows a plan view of a building with load applied. The building has solid wall on three elevations and two openings between wall segments on the fourth elevation. The slide also has a simplified distribution of shears to shear walls for a flexible diaphragm building.
For the same building studied above but with a flexible diaphragm, the left and right shear walls each resist 1/2 the total lateral load.

## Slide 126: Simplified Diaphragm Analysis
5 / 8 V
1 / 2 V
3 / 8 V
1 / 2 V
40 ft
8 ft
40 ft
8 ft
8 ft
8 ft
8 ft
V
Design for the worse of the two cases:
Notes: This slide shows a plan view of a building with load applied. The shear forces from the rigid and flexible diaphragm analyses are enveloped.
Further, it is possible to avoid the need to classify the diaphragm as “rigid” or “flexible.” Simply design each wall for the more critical of the simplified rigid-diaphragm case and the flexible-diaphragm case.
For this example, the left-hand wall had a shear of 5/8 V for the rigid-diaphragm case and a shear of 1/2 V for the flexible-diaphragm case. It could therefore be designed for the more severe of the two design shears or 5/8 V.
The right-hand wall would be similarly designed for the worse of 3/8 V (rigid) and 1/2 V (flexible) or 1/2 V.
Even though these two design shears sum to more than V, the design is conservative and valid. It might be too conservative for a few cases in which event the diaphragm stiffness would have to be evaluated.

## Slide 127: Diaphragm Design
w
L / 2
M = w L2 / 8
V = w L / 2
Diaphragm shears are resisted by total depth or by cover (for plank diaphragms). Diaphragm moments are resisted by diaphragm chords in bond beams.
Notes: This slide discusses diaphragm design and shows a plan view of a diaphragm with a distributed load on one face and shear and moment on the perpendicular faces.
If the diaphragm is continuous, diaphragm shears are resisted by the total depth of the diaphragm. If the diaphragm is discontinuous, diaphragms are resisted by cover only. Flexural resistance comes from forces in diaphragm chords separated by the internal lever arm (distance between chords)

## Slide 128: Details
Wall-diaphragm connections
Design of lintels for out-of-plane loads between wall-diaphragm connections
Connections between bond beam and walls
Connections between walls and foundation
Notes: This slide lists detailing considerations for load transfer.
After designing the out-of-plane strips, the in-plane shear walls and the lintels, additional details would have to be addressed: wall-diaphragm connections, design of lintels for out-of-plane loads between wall-diaphragm connections, connections between bond beam and walls, and connections between walls and foundations.

## Slide 129: Compute Factored Design Moments and Shears
MOMENTS
SHEARS
M / V
Factored design moments and shears for in-plane loading depend on actions transferred to shear walls by horizontal diaphragms at each floor level.
Factored design moments and shears for out-of-plane loading depend on wind or earthquake forces acting between floor levels
Notes: The top figure shows the shear and moment distribution for in-plane loading. The bottom figure show the moment distribution for out-of-plane loading.
The first step is computation of factored design shears and moments.
Factored design moments and shears for in-plane loading depend on actions transferred to shear walls by horizontal diaphragms at each floor level.
Factored design moments and shears for out-of-plane loading depend on wind or earthquake forces acting between floor levels.

## Slide 130: Design Flexural Reinforcement as Governed by Out-of-plane Loading
Practical wall thickness is governed by available unit dimensions:
  8- by 8- by 16-in. nominal dimensions is most common
  Specified thickness = 7-5/8 in.
  One curtain of bars, placed in center of grouted cells
Practical wall thickness = 7-5/8 in.
Can have nominal 6” through 12”
Proportion flexural reinforcement to resist out-of- plane wind or earthquake forces
Notes: The next step is to design the flexural reinforcement as governed by out-of-plane loading, which usually will govern over the reinforcement necessary to resist in-plane loading.
The practical wall thickness is governed by available unit dimensions. Using concrete masonry units, nominal dimensions of 8 by 8 by 16 in. are most common. This implies a specified thickness of 7-5/8 in., and a single curtain of reinforcement, placed in the center of grouted cells.
The specified wall thickness is 7-5/8 in.
Proportion flexural reinforcement to resist out-of- plane wind or earthquake forces. Because axial loads are small, the necessary reinforcement can be estimated by dividing the maximum factored design moment from out-of-plane loads by the product of the specified steel yield strength and the internal lever arm.

## Slide 131: Design Flexural Reinforcement as Governed by In-plane Loading
Axial Capacity
Flexural Capacity
Construct moment – axial force interaction diagram
  Initial estimate (more later)
  Computer programs
  Spreadsheets
  Tables
Notes: A simplified axial load-moment interaction diagram for masonry is shown.
The next step is to design flexural reinforcement as governed by in-plane loading. A moment-axial force interaction diagram can be computed by hand or by spreadsheet. As an initial estimate for hand calculations, the approach of Cardenas and Magura can also be used, and is discussed in a few more slides.

## Slide 132: Strict Limits on Maximum Flexural Reinforcement
Axial Capacity
Flexural Capacity
Design prohibited
Design permitted
Objective -- Keep compressive stress block from crushing (brittle failure):
  Walls must be below balance point.
  Maximum steel percentage decreases as axial load increases, so that design above balance point is impossible.
Notes: This graph shows a simplified axial load-moment interaction diagram with the area below the balance point as “Design permitted” and the area above the balance point as “Design prohibited”.
As noted previously, TMS 402 places strict limits on maximum flexural reinforcement. To keep the compressive stress block from crushing, the maximum steel percentage decreases as axial load increases so that design above the balance point is impossible.

## Slide 133: Revise Design as Necessary
If flexural reinforcement required for out-of-plane moments is less than or equal to that required for in-plane moments, no adjustment is necessary. Use the larger amount.
If flexural reinforcement required for out-of-plane moments exceeds that required for in-plane moments, consider making the wall thicker so that in-plane flexural capacity does not have to be increased. Excess in-plane reinforcement increases shear demand.
Notes: This slide lists considerations for revising the design if necessary.
After determining the reinforcement required to resist out-of-plane loads, and the reinforcement required to resist in-plane loads, the greater of the two requirements governs. If out-of-plane requirements considerably exceed in-plane requirements, consider making the wall thicker. In-plane over-capacities in flexure can lead to an unacceptable increase in shear demand if capacity design is used (see subsequent example).

## Slide 134: Check Shear Capacity (1)
shears and moments
corresponding to
probable flexural capacity
shears and moments from factored design loads
WALL
MOMENTS
WALL
SHEARS
M / V
shears and moments corresponding to nominal flexural capacity
Elastic structures or those with considerable shear overstrength:
  Compute factored design shears based on factored design actions.
Inelastic structures:
  Compute design shears based on flexural capacity
Notes: A graphic of wall shears and moments is shown with shears and moments from factored design loads, corresponding to nominal flexural capacity, and corresponding to probably flexural capacity.
In checking shear capacity, the first step is to estimate the design shear.
If the structure is essentially elastic, factored design shears should be computed based on factored design actions.
If the structure is expected to have significant inelastic flexural deformation, then capacity design should be used. Design shears should be computed based on flexural capacity.
In the above figure, the gray diagrams represent shears and moments from factored design loads. The black diagrams represent shears and moments corresponding to nominal flexural capacity. They are the gray diagrams,divided by the capacity reduction factor for flexure. The red diagrams represent the shears and moments corresponding to the probable flexural capacity. They are the black diagrams, multiplied by the ratio of the probable yield strength of the flexural reinforcement divided by the specified yield strength and also multiplied by the ratio of the probable area of reinforcement divided by the required reinforcement.

## Slide 135: Check Shear Capacity (2)
45 o
 Av fy
V
Vn = (Vnm + Vns)gg
Vnm depends on (Mu / Vudv) ratio
Vns = (0.5) Av fy (note efficiency factor when combining Vnm and Vns)
gg = 1.0 for fully grouted walls
Notes: This slide shows a free body diagram of force in the rebar due to horizontal shear is shown.
As discussed previously, shear resistance is calculated similarly to that of reinforced concrete.

## Slide 136: Shear Resistance from Masonry, Vnm (1)
(9-24)
Vnm depends on (Mu / Vudv) ratio and axial force
(Mu / Vudv) need not be taken greater than 1.0
Notes: As discussed previously, Vm depends on aspect ratio.

## Slide 137: Total Shear Resistance, Vn (1)
Vn / h Lw  fm’
10
8
6
4
2
0
0.5
1.5
1.0
Mu / Vu dv
4.0
0.25
6.0
Vn = resistance from masonry (Vnm) plus resistance from reinforcement (Vns)
Upper limit on Vn depends on (Mu / Vu dv) ratio
Notes: A plot with Mu/Vudv on the x-axis and Vn/(hLw x sqrt(f’m)) on the y-axis is shown.
As discussed previously, total shear resistance is limited to prevent diagonal crushing of masonry.

## Slide 138: Check Detailing
Cover
Placement of flexural and shear reinforcement
Boundary elements not required:
  Ductility demand is low
  Maximum flexural reinforcement is closely controlled to delay the onset of toe crushing
Notes: Finally, the designer must check detailing, including cover and placement of flexural and shear reinforcement. Boundary elements are not required because ductility demand is usually low and maximum flexural reinforcement is closely controlled.

## Slide 139: Detailing (1)
Cover:
  Automatically satisfied by putting reinforcement in grouted cells
Placement of flexural and shear reinforcement:
  Minimum flexural reinforcement and spacing dictated by Seismic Design Category
  Flexural reinforcement placed in single curtain. Typical reinforcement for SDC D would be at least #4 bars @ 48 in.
  Place horizontal reinforcement in single curtain. Typical reinforcement for SDC D would be at least #4 bars @ 48 in.
  Add more flexural reinforcement if required, usually uniformly distributed.
Notes: This slide discusses detailing considerations for reinforcement.
Detailing requirements usually are not difficult to satisfy.
Cover requirements are satisfied automatically by putting reinforcement in grouted cells.
Flexural and shear reinforcement must comply with the minimum flexural reinforcement and spacing dictated by the Seismic Design Category.
Flexural reinforcement is normally placed in single curtain.
Typical reinforcement would be at least #4 bars @ 48 in.
Horizontal reinforcement is also placed in the same single curtain.
Typical reinforcement would be at least #4 bars @ 48 in.
Additional reinforcement (usually uniformly distributed) can be added if required to resist in-plane flexure.

## Slide 140: In-Plane Flexural Strength of Lineal Walls (1)
For ductile behavior, consider portion of curve below balance point
Axial Capacity
Flexural Capacity
Moment-axial force interaction diagram for low axial load
Notes: This slide shows a simplified axial load-moment interaction diagram for masonry with the zone below the balance point highlighted for design.
Now let’s look briefly at Cardenas and Magura’s approximation for flexural strength.

## Slide 141: Design Example (1)
Refer to NEHRP Design
Examples (FEMA P-751)
Ch. 13, Masonry
Shear Wall:
Next slide
Notes: The figure shows the exterior end wall elevation of the 5-bay, 1-story example structure. The story height is 28’-0” with a 2’-0” parapet above, for a total building height of 30’-0”. The overall elevation is 100’-0” long. A continuous stem wall and footing are shown below grade. There are 5 door openings spaced evenly across the elevation; the openings are 12’-0” wide and 12’-0” tall. The two end piers are 4’-0” wide and the four interior piers are 8’-0” wide. The wall is labeled 12” masonry.
Slide shows elevation of wall for example problem in P-751.

## Slide 142: Design Example (1)
Refer to NEHRP
Ch. 13, Masonry
Shear Wall
Notes: The figure shows a free body diagram of a single 8’ wide x 12’ tall pier. At the top of the pier the forces are Ptop = 45.1 kips, Vtop = 41.0 kips, and Mtop = 523 ft-kip for axial, shear, and moment respectively. At the bottom of the pier the forces are Rbot = 55.0 kips, Vbot = 43.6 kips, and Mbot = 0 for axial, shear, and moment respectively.
Slide shows a pier of the wall and forces acting on pier.

## Slide 143: Design Example (1)
Trial design: (6) cells w/ (2) #6
Refer to NEHRP
Ch. 13, Masonry
Notes: The figure shows a section through the length of a single pier with the grouted cells filled in. Overall length of the pier is 8’-0” = 96”. Distance ‘d’ from the extreme compression fiber to the outermost steel is 92”. Axial load is distributed uniformly across the length of the wall with the resultant P = (Pf + Pw) acting at the center of the wall length.
Slide shows section of wall with grouted cells and reinforcement.

## Slide 144: Design Example (1)
Refer to NEHRP
Ch. 13, Masonry
Note: a = 4
for Special
Reinforced
Masonry Shear
Wall
Ductility Check
Notes: The figure shows a section through the length of a single pier with the grouted cells filled in as in the previous slide. Overall length of the pier is 8’-0” = 96”. Distance ‘d’ from the extreme compression fiber to the outermost steel is 92”. Axial load is distributed uniformly across the length of the wall with the resultant P = (Pf + Pw) acting at the center of the wall length. A strain diagram is shown below the section with the extreme compressive strain em = 0.0025, and the tensile strain at the steel at the end of the wall 4ey = 0.0083, and a linear strain variation between these two points. The neutral axis (dimension ‘c’) is located 21.3” from the extreme compression face. The strain at the steel along the length of the wall is shown on the strain diagram. The compression strains in the steel in the first two cells are 0.0020 and 0.0011 acting at 17.3” and 9.3” from the neutral axis respectively. The tensile strains in the steel are, in order, 0.0017, 0.0045, 0.0073 and 0.0083 as previously mentioned. The respective distances of the tension steel to the neutral axis are 14.7”, 38.7”, 62.7”, and 70.7”.
Slide shows strain profile on wall section.

## Slide 145: Design Example (1)
Refer to NEHRP Ch. 13, Masonry
Ductility Check (cont.)
Notes: The figure shows two stress diagrams. The first stress diagram shows the masonry compressive stress with a magnitude of 0.8f’m and a length ‘a’ of 17.0”. The resultant force Cm is located 12.8” from the neutral axis. The second stress diagram shows the steel tensile and compressive stresses. The steel stresses are shown for each steel location. Steel stresses in tension and compression are capped at the yield stress of fy = 60 ksi. Stresses Cs1, Cs2, and Ts3 are shown in the linear elastic stress range, while Ts2 and T­s1 are shown at the yield stress.
Slide shows stress profile on wall section.

## Slide 146: Design Example (1)
Refer to NEHRP Ch. 13, Masonry
Ductility Check (continued)
SC > ST + P
Cm + Cs1 + Cs2 > Ts1 + Ts2 + Ts3 + Ts4 + P
315.5 + 53.6 + 28.1 > 52.8 + 52.8 + 52.8 + 43.4 + 45.1
397 kips > 247 kips OK
OK because comp capacity > tension capacity
Notes: Slide shows ductility check calculations.

## Slide 147: Design Example (1)
P = 0 Case
Refer to NEHRP Ch. 13, Masonry
Notes: The figure shows a section through the length of a single pier with the grouted cells filled in as in previous slides. Overall length of the pier is 8’-0” = 96”. Distance from the center of the pier to the outermost steel is 44”. Two stress and strain profiles are shown below the section.
Stress and strain profiles are shown for the P = 0 case. The strain diagram is shown superimposed on the stress diagram with the extreme compressive strain em = 0.0025, and a linear strain variation discontinued below the tensile yield strain of the steel ey = Fy/E = 0.00207. The neutral axis (dimension ‘c’) is located 14.2” from the extreme compression face. The masonry compressive stress is shown with a magnitude of 0.8f’m and a length ‘a’ of 11.3”, with the resultant force Cm acting at 42.35” from the center of the pier. All the steel in tension is shown at yield. Ts4 and Ts3 are 12” on either side of the pier centerline. Ts2 is 36” from the centerline, and Ts1 was previously defined at 44” from the centerline.
Slide shows analysis of section with zero axial load.

## Slide 148: Design Example (1)
Balanced Case
Refer to NEHRP Ch. 13, Masonry
Notes: The figure shows a section through the length of a single pier with the grouted cells filled in as in previous slides. Overall length of the pier is 8’-0” = 96”. Distance from the center of the pier to the outermost steel is 44”.
Stress and strain profiles are shown for the balanced case. The strain diagram is shown superimposed on the stress diagram with the extreme compressive strain em = 0.0025, and a linear strain variation to a maximum tensile strain equal to the tensile yield strain of the steel ey = Fy/E = 0.00207. The neutral axis (dimension ‘c’) is 50.3”, which is 2.3” past the centroid of the pier. The masonry compressive stress is shown in three components, each with a magnitude of 0.8f’m with a total dimension ‘a’ of 40.3”. The first component is for the first two grouted cells over a length of 16” with the resultant force Cm1. The second component is over a length of 16” for the next two cells which are ungrouted with the resultant force Cm2. The third component is for the next grouted cell over a length of 8.3” with the resultant force Cm3. The steel in the first grouted cell is shown at yield stress with resultant Cs1. The steel in the second grouted cell is in the linear elastic range with a resultant Cs2. The steel in the next grouted cell is marked by * and not labeled further. The tension steel in the grouted cell at the end of the pier is at yield with a resultant Ts1. The tension steel in the second grouted cell is in the linear elastic range with a resultant Ts2. The steel in the next grouted cell is marked by * and not labeled further.
Slide shows strain profile under balanced conditions.

## Slide 149: Design Example (1)
Pn = SC - ST = 534 kips
fPn = (0.9)(534) = 481 kips
S Mcl = 0:
Mn = = 23,540 in.-kips
fMn = (0.9)(23,540) = 1,765 ft-kips
Refer to NEHRP Ch. 13, Masonry
Notes: Slide provides calculations for wall axial strength and corresponding flexural strength.

## Slide 150: Design Example (1)
fPn – fMn Diagram
Refer to NEHRP Ch. 13, Masonry
Next Slide
Notes: Axial Force –Bending Moment interaction diagram for wall section.

## Slide 151: Design Example (1)
Refer to NEHRP Ch. 13, Masonry
ɸMn
Notes: The figure shows the low-axial load portion of a simplified axial load – moment interaction diagram. The x-axis is fMn with units of ft-kips, and the y-axis is fPn with units of kips. The curve is formed from coordinates (fMn = 988, fPn = 0) and the balance point (fMn = 1765, fPn = 481). fPn max for ductility = 223 kips is shown as a dashed horizontal line. The curve continues above the balance point with decreasing moment capacity with increasing axial load but the curve is cut off. Demands are shown at a moment Mu = 523 ft-kips with axial loads Pu,min = 41 kips and Pu,max = 67 kips. Both points are within the bounds of the interaction curve. A horizontal line is drawn from Pu,max to the curve, where fMn = 1096 ft-kips.
Diagram determining if wall has adequate strength.

## Slide 152: Web sites for more information
BSSC = www.bssconline.org
TMS = www.masonrysociety.org
ACI = www.concrete.org
ASCE / SEI = www.seinstitute.org
MSJC = www.masonrystandards.org
NCMA = www.ncma.org
BIA = www.bia.org
Notes: Further information on the topics presented here is given in these web sites.

## Slide 153: Acknowledgements
This presentation was adapted from material prepared by Prof. Richard E. Klingner, University of Texas at Austin and by Dr. James Harris, J.R. Harris & Co.
Some of the material originally prepared by Prof. Klingner was for a US Army short course.
Some of the material originally prepared by Prof. Klingner was for The Masonry Society and is used with their permission.
The material originally prepared by Dr. Harris was for FEMA, The Building Seismic Safety Council, and the American Society of Civil Engineers.
Notes: This slide shows acknowledgements for the presentation.

## Slide 154: Questions?
Notes: Slide is a questions slide with a graphic of a CGI person sitting on a large question mark.
Slide prompts participants for questions

## Slide 155: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.