## Slide 1: Design for Nonstructural Components Design Examples Robert Bachman, S.E., John Gillengerten, S.E., and Susan Dowty, S.E.
Disclaimer
18
Notes: An image of the cover of the data disk containing the 2015 NEHRP Recommended Seismic Provisions.
Title slide, consisting of an image of the cover of the data disk containing the 2015 NEHRP Recommended Seismic Provisions, and the names of the authors of the 2015 Design Provisions Examples.
This unit includes three design example problems for earthquake resistant design of nonstructural components. The images come from a variety of FEMA publications, especially FEMA E-74, Reducing the Risks of Nonstructural Earthquake Damage – A Practical Guide.

## Slide 2: Design Examples
Egress Stairs
  Force Calculation
  Drift Demands
HVAC Fan Unit Support
  Force Calculation
  Anchor Design Forces
Elevated Vessel Seismic Design
  Force Calculation
  Support Frame Connection to Floor Slab
Notes: This slide shows the three design examples. Each example contains the lateral force calculations, and another area of interest in the design.

## Slide 3: General Notes
All references to chapters, sections, and equations are to ASCE/SEI 7-16
The examples focus on determination of the seismic force and displacement demands
Detailed design of the components, supports, and attachments are not covered, and would performed in accordance with the appropriate materials standards
Notes: This slide contains some general notes applicable to all the examples. All references to chapters, sections, and equations are to ASCE/SEI 7-16, and the focus is on determination of forces and displacements. Detailed design of the components, supports and attachments are not shown, but would be performed in accordance with the appropriate standards.

## Slide 4: Egress Stairs
Notes: The slide introduces the first design example, Egress stairs. The image shows a stairway damaged by story drift in the 1994 Northridge earthquake.
This example focuses on quantifying the prescribed seismic forces and displacements. The design of the stairs themselves and their connections for dead, live, and seismic loads is not covered.

## Slide 5: Egress Stairs
Egress stairs are an essential part of the system used to evacuate building occupants following an earthquake
In the 2016 edition of the ASCE/SEI 7, a new section was added to Chapter 13 with specific requirements intended to limit damage and improve functionality of egress stairs following an earthquake
The new requirements do not apply to egress stair systems and ramps that are integral with the building structure
Notes: The slide provides background information on the importance of egress stairs. It discusses changes to egress stair requirements incorporated in ASCE/SEI 7-16, and that stairs that are integral with the building structure are not covered by the nonstructural provisions.

## Slide 6: Example Description
Egress stairs of prefabricated steel construction are installed in a five-story reinforced concrete moment frame building
The example focuses on the flight of stairs running between the 3rd and 4th Levels of the building
  The treads and landings are fabricated from 1/8 inch thick steel checkered plate
  The stringers are fabricated from ¼ inch thick steel plate, and other members and supports are fabricated from steel channels, angles, and tube.
The effective dead load is estimated at 20 psf, and the design live load is 100 psf.
Notes: This slide provides a description of the egress stairs covered in the example. The stairs are installed in a 5-story building and the focus of the example is on the flight of stairs between the third and fourth floors. The dead and live loads are given.

## Slide 7: Elevation of Egress Stair
Notes: The figure shows a vertical section of a 3-bay, 5-story structure.
The floors of the structure are identified as Levels 1 through 5. The story height is 14’-0”, for a total building height of 70’-0”. In the center bay, the egress stairs are shown, running from Level 1 through Level 5. At each level, the egress stairs consist of a flight of stairs running from left to right, a landing mid height in the story, and a flight of stairs running right to left to the level above.

## Slide 8: Plan of Egress Stair
Notes: The illustration shows a plan of the egress stairs.
The flight of stairs from the lower level to the landing is shown at the bottom left of the figure. Each flight of stairs is 10’-1” long and 3’-6” wide. The lower flight of stairs rise from the lower level to the left to the landing to the right. The upper flight stairs, run from the landing on the right to the upper level on the left. The landing on the right of the figure is 3’-6” wide and 7’-4” long, and supported by 4 steel posts, near the corners of the landing. The stair treads and landings are of 1/8” steel checker plate.

## Slide 9: Isometric View
Notes: The illustration shows an isometric view of the egress stairs from Level 3 to Level 4.
The lower flight of stairs rises left to right from Level 3 to the landing; the upper flight rises right to left from the landing to Level 4. A right-hand Cartesian coordinate system is shown with the x-axis parallel to the flight of stairs, the y-axis perpendicular to the flight of stairs, and the z axis vertical. The landing is shown in the middle of the 14’-0” story height, and the landings are supported from the floor below by HSS3x3 posts. Five connection points between the stairs and the structure are identified, 3 points at Level 3, and 2 points at Level 4. At Level 3, connections A3 and B3 are at the base of the flight of stairs, and provide translational restraints in the X, Y, and Z directions. Connection C3 is at the base of the HS3x3 supporting the landing nearest to the stair stringer. At Level 4, connections A4 and B4 support the top of the flight of stairs running from the landing to Level 4, and provide vertical support (Z-direction) only. These connections permit the structure to move freely relative to the flight of stairs in the X- and Y-directions.

## Slide 10: Design Parameters
ap = 1.0 Egress stairways not part of the seismic force-resisting system (Table 13.5-1)
ap = 2.5 Egress stairs and ramp fasteners and attachments (Table 13.5-1)
SDS = 1.00 (for the selected location and site class) (given)
Seismic Design Category = D (Table 11.6-1)
Rp = 2.5 Egress stairways not part of the seismic force-resisting system (Table 13.5-1)
Rp = 2.5 Egress stairs and ramp fasteners and attachments (Table 13.5-1)
Ip = 1.5 (Sec. 13.1.3)
Ω0 = 2.0 for fasteners of the connecting system (Table 13.5-1)
Notes: The slide summarizes the values for the variables used in the seismic design of egress stairs.

## Slide 11: Design Parameters
Flight: Wp = (20 lb/ft2)(10.08 ft)(3.5 ft) = 706 lb (Single flight from landing to floor)
Landing: Wp = (20 lb/ft3)(7.33 ft)(3.5 ft) = 513 lb
(at Level 3)
(at Level 4)
The redundancy factor, ρ, for nonstructural components is taken as 1.0 in load combinations (Section 13.3.1)
Notes: This slide shows the calculations for the weights of the landing and a flight of stairs. It also shows the calculations for the ration of component attachment height to the height in the building, and the redundancy factor.

## Slide 12: Performance Criteria
Seismic attachments must be bolted, welded, or otherwise positively fastened without considering the frictional resistance produced by the effects of gravity (Sec. 13.4).
The net relative displacement is assumed to occur in any horizontal direction, and must be accommodated through slotted or sliding connections, or metal supports designed with rotation capacity to accommodate seismic relative displacements (Sec. 13.5.10).
Sliding connections (slotted or oversize holes), sliding bearing supports with restraints that engage after the displacement DpI, is exceeded (e.g. keeper assemblies or end stops), and connections that permit movement by deformation of metal attachments must accommodate DpI, but not less than 0.5 in. without loss of vertical support or inducing displacement-related compression forces in the stair (Sec. 13.5.10).
Notes: This slide lists some of the performance criteria for exit stairs, relating to seismic attachments and accommodation of story drift.

## Slide 13: Performance Criteria
Sliding bearing supports without keeper assemblies or end stops must be designed to accommodate a displacement 1.5DpI, but not less than 1.0 in. without loss of vertical support. Break-away restraints are permitted if their failure does not lead to loss of vertical support (Sec. 13.5.10).
If sliding or ductile connections are not provided to accommodate seismic relative displacements, the stiffness and strength of the stair or ramp structure shall be included in the building structural model of Section 12.7.3 and the stair shall be designed with Ω0 corresponding to the seismic force-resisting system but not less than 2½ (Standard Sec. 13.5.10).
Notes: A508 notes

## Slide 14: Accommodating Story Drift
Fixed Connections
Sliding Connections
There are many different approaches for dealing with seismic displacement demand on egress stairs
In this example, for lateral displacements (X- and Y-direction) the stair assembly is fixed at Level 3 of the structure by connections A3 and B3
Connections A4 and B4 on Level 4 are detailed to accommodate story drift by sliding in the X- and Y-directions
Notes: The graphic shows an isometric view of the egress stairs from Level 3 to Level 4.
This slide illustrates the method chosen in the example for accommodating story drift. The graphic on the right of the slide shows an isometric view of the egress stairs from Level 3 to Level 4. The lower flight of stairs rises left to right from Level 3 to the landing; the upper flight rises right to left from the landing to Level 4. A right-hand Cartesian coordinate system is shown with the x-axis parallel to the flight of stairs, the y-axis perpendicular to the flight of stairs, and the z axis vertical. The landing is shown in the middle of the 14’-0” story height, and the landings are supported from the floor below by HSS3x3 posts. At level 3, fixed connections are indicated. At level four, sliding connections that accommodate story drift are indicated.

## Slide 15: Simplifying Assumptions
For simplicity in the connection calculations in this example, the mass of the stairs is lumped at the landing and at the center of gravity of each flight of stairs
Although the mass of the stairs is distributed between Levels 3 and 4, the lateral force is calculated assuming it is concentrated at Level 3, since the connections at Level 4 are free to slide in the X- and Y- directions
Lateral stiffness of the HSS3x3 posts is considered negligible
Notes: This slide lists some of the assumptions made to simplify the analysis of the stairs. The masses of the flights of stairs and the landings are assumed to be lumped at their centers of gravity. The connections at level three assumed to resist all the horizontal lateral forces from the flights and landing, since the connections at level 4 are free to slide. The lateral stiffness of the HSS3x3 posts is ignored.

## Slide 16: Induced Torsion
Fp (stairs)
Fp (stairs)
Fp (landing)
The seismic forces are distributed relative to the components mass distribution
The connection configuration induces twisting about the Z axis, due to the eccentricity between the center of mass of the stairs and the center of resistance of the connections
This eccentricity must be accounted for in the design
Notes: The graphic on the right of the slide shows an isometric view of the egress stairs from Level 3 to Level 4.
This slide illustrates the design implications of torsion induced by the geometry of the stairs and connections. The graphic on the right of the slide shows an isometric view of the egress stairs from Level 3 to Level 4. The lower flight of stairs rises left to right from Level 3 to the landing; the upper flight rises right to left from the landing to Level 4. A right-hand Cartesian coordinate system is shown with the x-axis parallel to the flight of stairs, the y-axis perpendicular to the flight of stairs, and the z axis vertical. The horizontal seismic forces for the landings and the stair risers are indicated by red arrows. At level 3, the reactions at the fixed connections are indicated by green arrows. At level four, the vertical reactions in direction z are indicated by green arrows, while sliding connections that accommodate story drift result in no reactions along the x and y axes.

## Slide 17: Design Force Equations
  Equation 13.3-3
  Equation 13.3-2
Fp (max) = 1.6 SDS Ip Wp
Fp (min) = 0.3 SDS Ip Wp
Equation 13.3-1
Notes: This slide presents Equation 13.3-1, the basic equation for seismic forces on nonstructural components. Equation 13.3-1 is intentionally conservative to cover the wide range of building structural systems, heights, etc. Fp forces are typically larger than those used for the design of the building. The minimum and maximum forces are given in Equations 13.3-2 and 13.3-3, respectively.

## Slide 18: Design Force Equations
  Eq.12.4-4a
Eq. 12.4-3
Seismic Load Effects
Eh = ρQE
Ev = 0.2SDSD
Load Combinations (Strength Design, Sec.2.3.6)
1.2D + Ev + Eh + L + 0.2S (Basic Load Combination 6)
0.9D - Ev + Eh (Basic Load Combination 7
Where:
QE load due to horizontal application of Fp (Sec. 12.4.2.1)
ρ = 1.0 because egress stairs are nonstructural components
D = dead load effect (due to vertical load application)
L= 0.5 times the Live Load (Sec. 12.4.2.3, Item 1)
Notes: This slide shows the formulas used for calculating seismic load effects and combining seismic loads with other loads.

## Slide 19: Force Demands – Flight of Stairs
D = Wp = 706 lb (vertical gravity effect)
L = (10.08)(3.5)(100 psf) = 3,528 lb (Live load vertical gravity effect)
Fpmax = 1.6(1.0)(1.5)(706 lb) = 1,694 lb
Fpmin = 0.3(1.0)(1.5)(706 lb) = 318 lb
Eq. 13.3-3 (the minimum force) governs, and Fp = 318 lb
Eh = ρQE = (1.0)( 318 lb) = 318 lb (horizontal earthquake effect)
Ev = 0.2SDSD = (0.2)(1.0)(706 lb) = 141 lb (vertical earthquake effect)
Notes: In this slide, the calculations for vertical and horizontal seismic forces for a flight of stairs are shown. The minimum horizontal force governs the design.

## Slide 20: Force Demands – Landing
D = Wp = 513 lb (vertical gravity effect)
L = (7.33)(3.5)(100 psf) = 2,566 lb (Live load vertical gravity effect)
Fpmax = 1.6(1.0)(1.5)(513 lb) = 1,231 lb
Fpmin = 0.3(1.0)(1.5)(513 lb) = 231 lb
Eq. 13.3-3 (the minimum force) governs, and Fp = 318 lb
Eh = ρQE = (1.0)( 231 lb) = 231 lb (horizontal earthquake effect)
Ev = 0.2SDSD = (0.2)(1.0)(513 lb) = 103 lb (vertical earthquake effect)
Notes: In this slide, the calculations for vertical and horizontal seismic forces for the landing are shown. The minimum horizontal force governs the design.

## Slide 21: Stair Design
The force demands are substituted into the Basic Load Combinations for Strength Design from Section 2.3.6 to determine the design member forces, in conjunction with seismic and gravity loads
The stairs members are designed to carry the dead, live, and seismic loads, and the connections can be detailed and designed according to the appropriate standards
Notes: This slide discusses the procedures for applying the calculated seismic force demands to the design of the stairs, in accordance with the appropriate material standards.

## Slide 22: Fasteners and Attachments
The value of ap for egress stair and ramp fasteners and attachments is increased
Intent is to prevent premature failure in those elements, which could cause loss of vertical support
The change in ap only effects the force calculated using Standard Eq. 13.3-1. For a flight of stairs:
This value of Fp will govern, as it is greater than minimum force and less than the maximum force
A similar calculation would be done for the landing
Notes: The seismic loads for fasteners and attachments are higher than those for the stairs themselves, in order to avoid premature failures that could lead to loss of vertical support. This slide describes the calculations for a flight of stairs.

## Slide 23: Seismic Displacements
Assume that results of an elastic analysis of the building structure is not available for use in the design of the egress stairs
In such cases, the prescribed seismic displacements are calculated based on allowable story drift requirements:
  hsx = story height = 14’-0”
  hx = height of upper support attachment, Level 4 = 42’-0”
  hy = height of lower support attachment, Level 3 = 28’-0”
ΔaA = 0.020hsx Table 12.12-1
Dp = = = 3.36 in. Eq. 13.3-8
DpI = DpIe= 3.36 in (1.5) = 5.14 in. Eq. 13.3-6
Notes: This slide describes the calculations used to determine the design seismic displacements. In this example, it is assumed that structural displacements determined by analysis are not available. Calculations determining the seismic displacements based on allowable story drift are shown.

## Slide 24: Displacement Design Considerations
The connections of the egress stairs to the structure at Level 4 are sliding connections with slotted or oversize holes
Sliding bearing supports must be provided with restraints that engage after the displacement DpI, is exceeded (e.g. keeper assemblies or end stops)
The connections must be designed to accommodate DpI, without loss of vertical support or inducement of displacement-related compression forces in the stair
The displacement can act in any direction, so the connection must be able to accommodate a total range of movement of two times DpI, or 10.28 inches in all directions
If a keeper assemblies or end stops are not provided, the connection must be designed accommodate 1.5 DpIe, or 7.56 inches, or a total range of movememt of 15.12 inches.
Notes: This slide discusses some of the design consideration when using sliding connections to accommodate lateral displacements. The impact of keeper assemblies and end stops on the design displacement capacities are discussed.

## Slide 25: HVAC Fan Unit
Notes: The slide introduces the second design example, support design for a HVAC fan unit. The image shows a group of rooftop HVAC units the displaced or toppled in the 1994 Northridge earthquake.
This example focuses on quantifying the prescribed seismic forces and determination of the forces in attachments to the structure.

## Slide 26: HVAC Fan Unit Support Design Example
The component located at roof level of a five-story office building, near a an active fault in Los Angeles, California. Risk Category II.
Notes: This slide lists shows a plan and two elevations of a HVAC fan unit, which will be used as an example to illustrate the application of the nonstructural seismic design requirements.
In this example, the HVAC fan unit is 4-feet high, 5-feet wide, 8-feet long and weighs 3000 lbs. The unit is anchored to a concrete roof slab and attached with 4 anchors, one at each corner of the unit.

## Slide 27: Seismic Design Parameters and Coefficients
SDS = 1.487 (for the selected location and site class)
Seismic Design Category = D (Table 11.6-1)
Wp = 3,000 lb (given)
ap = 2.5 for both direct attachment (Table 13.6-1)
and spring isolated
Rp = 6.0 for HVAC fans, directly attached (Table 13.6-1)
(not vibration isolated)
Rp = 2.0 for spring isolated components (Table 13.6-1)
with restraints
  Ω0 = 2.5 for anchors in concrete or masonry unless controlled by a ductile yielding element
Ip = 1.0 (Sec. 13.1.3)
z/h = 1.0 (for roof-mounted equipment)
Notes: This slide provides design parameters and coefficients from Chapters 11 and 13 of ASCE/SEI 7.including the ground shaking intensity, and the design coefficients from Table 13.6-1. The component importance factor is 1.0.

## Slide 28: Free Body Diagram for Force Analysis
Notes: This slide shows a free body diagram for seismic force analysis, including dead loads, and the horizontal and vertical seismic forces. The horizontal and vertical reactions at the supports are also shown.

## Slide 29: Determine Seismic Forces
Fp = = 2,231 lb (Eq.13.3-1)
Fpmax = 1.6 x 1.487 x 1.0 x 3,000 = 7,138 lb (Eq. 13.3-2)
Fpmin = 0.3 x 1.487 x 1.0 x 3,000 = 1,338 lb (Eq. 13.3-3)
Since Fp is greater the Fpmin and less than Fpmax, the value determined from
Equation 13.3-1 applies.
Eh = ρQE (Eq. 12.4-3)
Ev = 0.2SDSD (Eq. 12.4-4)
where:
QE (due to horizontal application of Fp) = 2,231 lb (Sec. 12.4.2-1)
ρ = 1.0 (HVAC units are nonstructural components) (Sec. 13.3.1)
D = dead load effect (due to vertical load application)
Notes: The slide provides calculations and notes for computing component forces. The design force Fp is calculated using Equation 13.3-1, and the upper and lower limits on the lateral forces are also checked.

## Slide 30: Determine Reactions
Substituting, one obtains:
Eh = ρQE = (1.0)(2,231 lb) = 2,231 lb (horizontal earthquake effect)
Ev = 0.2SDSD = (0.2)(1.487)(3,000 lb) = 892 lb (vertical earthquake effect)
(1.2 + 0.2SDS) D + ρQE + L + 0.2S (Basic Load Combination 5)
(0.9 - 0.2SDS) D + ρQE + 1.6H (Basic Load Combination 7)
U = (1.2 + 0.2SDS) D + ρQE
Vu = = 558 lb/bolt
Tu = (no tension)
Notes: The terms Eh and Ev are substituted into the basic load combinations for strength design of Section 12.4.2 to determine the design member and connection forces to be used in conjunction with seismic loads.
Based on the free-body diagram, the seismic load effects can be used to determine bolt shear, Vu, and tension, Tu (where a negative value indicates tension).

## Slide 31: Determine Anchor Loads
U = (0.9 - 0.2SDS) D + ρQE
Vu = = 558 lb/bolt
Tu = (no tension)
Notes: In the final step, the shear and tension loads on the anchors are calculated. The signs of SDS and FP have been selected to result in the largest value of anchor tension Tu.

## Slide 32: Elevated Vessel Seismic Design
Notes: The image shows a tank supported on legs with chevron
The slide introduces the third design example, support design for a HVAC fan unit. bracing. The example focuses on the determination of force demands on the different components of the support system

## Slide 33: Elevated Vessel Seismic Design
This example illustrates seismic design for a small platform-supported vessel in the upper floor of a structure
The example focuses on the determination of force demands on the different components of the support system
The sizing of the various elements (beams, columns, braces, connections, anchor bolts, etc.) are not covered in detail
Notes: The figure shows an elevation of the elevated vessel.
This slide introduces the example illustrating the seismic design for a small platform supported vessel. The example focuses on determination of force demands. The figure to the right shows an elevation of the elevated vessel. The vessel itself is cylindrical with a 6’-0” diameter and hemispherical ends. It is supported on 4 legs which are attached to a supporting frame. The supporting frame is attached to the concrete floor slab. The supporting frame is 6’-0” square in plan and 5’-0” tall, constructed of HSS2x2x1/4 legs and HSS6x2x1/4 beams with vertical X-bracing on all 4 sides. The vessel is supported on 4 legs that extend from the vessel shell to rest on the HSS6x2 beams. For analysis, the “supporting frame” extends from the floor slab to the top of the beams. The “vessel” includes all items above that level. The center of gravity of the vessel is 5’6” above the top of the supporting frame, and in plan it is located in the center of the vessel.

## Slide 34: Seismic Design Requirements
Seismic design requirements for vessels depend on the system importance factor (Ip), the mass of the vessel relative to that of the supporting structure and the installation geometry
Special analytical requirements trigger when the weight of the nonstructural component exceeds 25 percent of the effective seismic weight of the structure
This condition is not present in the example but if it was the component would be classified as a nonbuilding structure and Section 15.3.2 (nonbuilding structures) would apply
Given that the structure is assigned to Seismic Risk Category II, components are assigned Ip = 1.0, unless they must function for life-safety protection or contain hazardous materials
Neither of these conditions apply, so Ip = 1.0
Notes: In this slide, the general seismic design requirements, with a focus on condition that trigger special analytical requirements

## Slide 35: Building Section
Notes: The figure shows a vertical section through the building structure supporting the elevated vessel.
The structure is 40’-0” tall. The Levels 0 and 1 have story heights of 12’-0”. The second floor to roof story height is 18’-0”. The elevated vessel is supported at Level 2 of the structure.

## Slide 36: Level 2 Plan
Notes: The figure shows a plan of the second level of the building structure supporting the elevated vessel.
A Cartesian coordinate system is shown with the X-axis horizontal on the page and the Y axis vertical. The building structure is square in plan, with dimensions of 30’-0” by 30’-0”. Steel wide-flange columns are located at each corner of the building and there are perimeter beams. A 6-inch thick reinforced concrete slab is supported by the perimeter beams and a beam running in the X-direction across the middle of floor plate. The elevated vessel is centered in the upper half of the floor in the figure, supported on 4 columns 6’-0” apart, The distance from the center beam to the first pair of legs is 4’-6”. The distance from the perimeter beams running in the Y-direction to the vessel legs is 12’-0”.

## Slide 37: Vessel and Supporting Frame
Notes: The figure shows an elevation of the elevated vessel.
The vessel itself is cylindrical with a 6’-0” diameter and hemispherical ends. It is supported on 4 legs which are attached to a supporting frame. The supporting frame is attached to the concrete floor slab. The supporting frame is 6’-0” square in plan and 5’-0” tall, constructed of HSS2x2x1/4 legs and HSS6x2x1/4 beams with vertical X-bracing on all 4 sides. The vessel is supported on 4 legs that extend from the vessel shell to rest on the HSS6x2 beams. For analysis, the “supporting frame” extends from the floor slab to the top of the beams. The “vessel” includes all items above that level. The center of gravity of the vessel is 5’6” above the top of the supporting frame, and in plan it is located in the center of the vessel.

## Slide 38: Design Parameters and Coefficients
ap = 1.0 for vessels not supported on skirts and not subject to Chapter 15 (Table 13.6-1)
Rp = 2.5 for vessels not supported on skirts and not subject to Chapter 15 (Table 13.6-1)
Ω0 = 2.0 overstrength factor for nonductile anchorage to concrete (Table 13.6-1)
SDS=1.2 selected location and site class (given)
Seismic Design Category = D (Table 11.6-1)
Notes: The slide summarizes the values for the variables used in the seismic design of the elevated vessel.

## Slide 39: Design Parameters and Coefficients
h = 46 feet (roof height) (given)
z = 28 feet (system supported at the Level 2) (given)
Ip = 1.0 Sec. 13.1.3
D = Dead Load = Wp = 5,000 lb (vessel and legs) (given)
= 1,000 lb (allowance, supporting frame) (given)
Notes: This slide shows the calculations for the weights of the vessel and supporting frame. It also shows the calculations for the ratio of component attachment height to the height in the building, and the importance factor.

## Slide 40: Seismic Design Forces
Eq. 13.3-1
Eq. 13.3-2
Eq. 13.3-3
Eq. 12.4-4a
Notes: In this slide, the calculations are shown for vertical and horizontal seismic forces the vessel and supporting frame, expressed as a percentage of the component weight. The basic horizontal force from Eq. 13.3-1 governs the design.

## Slide 41: Seismic Design Forces
Vessel
= 2,129 lb
= 1,200 lb
Supporting Frame
= 426 lb
= 240 lb
Notes: Using the seismic forces determined in the previous slide, the values of the horizontal and vertical components of the seismic force are calculated.

## Slide 42: Performance Criteria
Component seismic attachments must be bolted, welded, or otherwise positively fastened without considering the frictional resistance produced by the effects of gravity (Sec. 13.4)
Local elements of the structure, including connections, must be designed and constructed for the component forces where they control the design (Sec. 13.4)
Anchors to concrete shall be designed so that either the support or component that the anchor is connecting to the structure undergoes ductile yielding at a load level corresponding to anchor forces not greater than their design strength, or the anchors shall be designed to resist the load combinations considering Ω0 in accordance with Section 2.3.6.
Notes: This slide lists some specific requirements for attachments, supports, and anchors to concrete.

## Slide 43: Design Force Equations
  Eq.12.4-4a
Eq. 12.4-3
Seismic Load Effects
Eh = ρQE
Ev = 0.2SDSD
Load Combinations (Strength Design, Sec.12.4.2.3)
1.2D + Ev + Eh + L + 0.2S (Basic Load Combination 6)
0.9D - Ev + Eh (Basic Load Combination 7
Where:
QE load due to horizontal application of Fp (Sec. 12.4.2.1)
ρ = 1.0 because egress stairs are nonstructural components
D = dead load effect (due to vertical load application)
Notes: A508 notes: This slide shows the formulas that will be used for calculating seismic load effects and combining seismic loads with other loads.

## Slide 44: Vessel Supports
Supports and attachments for the vessel must meet the requirements listed in Table 13.2-1
Seismic design of the vessel itself is not required, since Ip = 1.0
While the vessel itself need not be checked for seismic loading, the component supports listed in Section 13.6.4 must be designed to resist the prescribed seismic forces
  The legs supporting the vessel
  Connection between the legs and the vessel shell
  Base plates and the welds attaching them to the legs
  Bolts connecting the base plates to the supporting frame
Notes: This slides list some design considerations for designing the vessel support, including a list of components in the load path that need to be checked.

## Slide 45: Loads imposed by the Vessel on the Supporting Frame
Eh
Ev
Notes: The figure shows an elevation of the elevated vessel and supporting frame.
The vessel and frame are as described in previous slides. The horizontal and vertical seismic forces are applied to the center of mass of the tank and are indicated by the red arrows. The horizontal and vertical reactions applied to the supporting frame are shown with green arrows.

## Slide 46: Forces in Vessel Supports
The lateral force, Fp, must be applied independently in at least two orthogonal directions
For vertically cantilevered systems, the lateral force also must be assumed to act in any horizontal direction
In this example, layout of the vessel legs is symmetric and there are two horizontal directions of interest, separated by 45 degrees
Notes: The figure is a plan view of the supporting frame, with the location of the vessel legs indicated by the green circles.
This slide illustrated the critical lateral force directions that must be checked. Because the layout of the vessel legs and supporting frame are symmetric, there are two horizontal directions of interest separated by 45 degrees. The figure on right is a plan view of the supporting frame, with the location of the vessel legs indicated by the green circles. The direction of lateral forces for the two load cases are indicated by the red arrows. Load Case 1 with horizontal force in the x direction will cause overturning about the y-y axis. Load Case 2 with horizontal force in the y’ direction will cause overturning about the x’-x’ axis.

## Slide 47: Case 1 - overturning about the y-y axis
The height of the vessel’s center-of-gravity above the bottom of the leg base plates is 5.5 feet. The moments about the bottom of these base plates are :
= 11,710 ft-lb
Assuming the vessel acts as a rigid body, in Case 1 the overturning moments is resisted by the two legs along the x-x axis and the maximum tension and compression loads in the legs is:
where the distance between legs A and C, d, is 6.0 feet.
= 1,952 lb
The vertical load per leg due to gravity is Wp/4 = 5,000/4 = 1,250 lb
The shear per leg due to Fp is V= Fp/4 = 2,129/4 = 532 lb
Notes: This slide describes the calculations for Load Case 1, overturning about the y-y axis. The overturning is resisted by two legs at opposite ends of the vessel, one in tension and one in compression. Shear is resisted by all four legs.

## Slide 48: Case 2 - moments about the x'-x' axis
In Case 2 the overturning moments are resisted by all four legs, two in compression and two in tension
The loads in the legs due to gravity are the same as in Case 1, as is the shear in the legs due to Fp
Under seismic load, the vessel is assumed to rotate about the x'-x’ axis
where the distance between legs A and C, 0.707d , is 4.24 feet
= 1,380 lb
Notes: This slide describes the calculations for Load Case 2, overturning about the x’-x’ axis. The overturning is resisted by all four legs, two in tension and two in compression. Shear is resisted by all four legs.

## Slide 49: Loads in the Vessel Legs
The axial loads in the vessel legs due to seismic overturning about the y-y axis (Case 1) are substantially larger than those obtained for overturning about the x'-x' axis (Case 2)
Therefore, by inspection Case 1 governs the design of the legs.
The design compression loads on the vessel legs is governed by Load Combination 5:
U = [1.2 + 0.2(1.2)](1,250 lb) + 1.0( 1,952 lb) = 3,752 lb = CU
The design tension load on the vessel legs is governed by Load Combination 7 (a negative sign denotes tension):
U = [0.9 – 0.2(1.2)](1,250 lb) - 1.0(1,952 lb) = -1,127 lb = TU
The design shear in each leg is U = 1.0(532 lb) = 532 lb = VU.
Notes: This slide describes the calculation of the design axial forces in the vessel legs.

## Slide 50: Supporting Frame
The design of the supporting frame can be performed separately from that of the vessel
The reactions from the vessel are applied to the frame and combined with the seismic loads resulting from the supporting frame itself.
Notes: The drawing is an elevation of the supporting frame.
The slide summarizes the approach for design the support frame, which can be performed separately from the design of the vessel legs. The reactions from the vessel legs must be combined with the seismic loads due to the mass of the supporting frame itself. To the right is an elevation of the supporting frame. The supporting frame is 6’-0” square in plan and 5’-0” tall, constructed of HSS legs and beams with vertical X-bracing on all 4 sides.

## Slide 51: Connection to the Floor Slab
Fp-vessel
Fp-frame
Ev-vessel
Ev-frame
Notes: The figure to the left shows an elevation of the elevated vessel and supporting frame. The figure on right is a plan view of the supporting frame, with the location of the support frame legs indicated by the green squares.
The figure to the left shows an elevation of the elevated vessel and supporting frame. The vessel and frame are as described in previous slides. The horizontal and vertical seismic forces are indicated by the red arrows and are applied to the centers of mass of the tank and the supporting frame. The figure on right is a plan view of the supporting frame, with the location of the support frame legs indicated by the green squares. The direction of lateral forces for Load case 2, the governing load case, is indicated by the red arrow.

## Slide 52: Connection to the Floor Slab
The case where the vessel rotates about the x'-x' axis governs the design of the connections to the slab
The overturning moment is:
=24,485 ft-lb
Assuming the vessel acts as a rigid body, the overturning moment is resisted by the two legs along the y'-y' axis
The vessel is assumed to rotate about the legs on the x'-x' axis
T = C =M/d = 24,485/(6.0)1/2 = 2,886 lb
The vertical load in each leg due to gravity is Wp/4 = (5,000+1,000)/4 = 1,500 lb
Notes: This slide describes the calculations for Load Case 2, overturning about the x’-x’ axis which will govern the design of the support frame legs. The overturning is resisted by two legs at opposite ends of the supporting frame, one in tension and one in compression. Shear is resisted by all four legs.

## Slide 53: Anchors to Concrete
There are special considerations for the design of the anchor bolts to the concrete slab that are unique to nonstructural components
Anchors in concrete and masonry must be proportioned so that either:
  The component or support that the anchor is connecting to the structure undergoes ductile yielding at a load level corresponding to anchor forces not greater than their design strength, or
  The anchors shall be designed to resist the load combinations considering Ω0 in accordance with Section 2.3.6.
Notes: This slide summarizes some of the design considerations for anchorage to concrete. Anchors must be designed using the overstrength factor Ω0 unless a ductile yielding mechanism is present.

## Slide 54: Anchor Tension
  In this example, it is assumed that the anchor design strength is less than the yielding strength of the vessel or supporting frame, and so Ω0 must be applied to the anchor loads.
By inspection, the load combination that results in net tension on the anchors will govern. Applying the load combinations of Section 2.3.6, Load Combination 7, the vertical design tension force is:
U = 0.9D - Ev + Emh
Emh = Ω0QE (Eq. 12.4-7)
U = 0.9(1,500 lb)-0.2(1.2)(1,500 lb)-2.0(2,886 lb) = -4,782 lb = TU
This is represents a 152 percent increase in the design tension compared to the case where Ω0 is not applied
Notes: This slide describes the calculation of concrete anchor tension demands, assuming that that the anchor design strength is less than the yielding strength of the vessel or supporting frame, and so Ω0 must be applied to the anchor loads.

## Slide 55: Questions?
Notes: Slide prompting participants to ask questions.

## Slide 56: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.