## Slide 1: Design for Nonstructural Components Robert Bachman, S.E., John Gillengerten, S.E., and Susan Dowty, S.E.
Disclaimer
18
Notes: An image of the cover of the data disk containing the 2015 NEHRP Recommended Seismic Provisions.
Title slide, consisting of an image of the cover of the data disk containing the 2015 NEHRP Recommended Seismic Provisions, and the names of the authors of the 2015 Design Provisions Examples.
This unit is only a brief introduction to the subject of earthquake resistant design of nonstructural components. The images come from a variety of FEMA publications, especially FEMA E-74, Reducing the Risks of Nonstructural Earthquake Damage – A Practical Guide.

## Slide 2: Nonstructural Components
Nonstructural components include equipment, distribution systems such as piping, ducts, and electrical raceways, and architectural components
These items make up the majority of the replacement value of most buildings.
Notes: An image of a suspended acoustical ceiling system missing some of its’ tiles.
The consists of text on the left and an image of a suspended acoustical ceiling system missing some of its’ tiles. The slide describes what constitutes nonstructural components and that the they make up most of the replacement values of a building.
Architectural, mechanical and electrical components are commonly referred to as “nonstructural components.”

## Slide 3: Approach to Nonstructural Components
Building codes have long history of seismic requirements for nonstructural components
Nonstructural components are grouped in broad categories for seismic design based on:
  Function
  Behavior under seismic loading
Requirements vary with the ground motion intensity
Components serving essential functions are subject to more stringent requirements
Notes: An image of a suspended mechanical unit that fell to the floor in an earthquake.
The slide, consists text on the left and an image of a suspended mechanical unit that fell to the floor in an earthquake. The slide describes the way nonstructural components classified and factors that influence the seismic requirements.
The earliest code requirements for nonstructural components are found in an Appendix of the 1927 Uniform Building Code. The requirements have evolved over time to reflect changes in the nonstructural systems found in buildings and advances in earthquake engineering.

## Slide 4: Nonstructural Design Requirements
2015 NEHRP Recommended Provisions:
Part 1, Provisions
ASCE/SEI 7-10 including Supplement 1, Minimum Design Loads for Buildings and Other Structures including Supplement 1, Chapters 11-23 adopted by reference
In ASCE/SEI 7-10
Chapter 13 – Seismic Design Requirements for Nonstructural Components
Section 12.11.2 Anchorage of Concrete and Masonry Structural Walls
Significant revisions in ASCE/SEI 7-16 will be noted
Notes: The slide identifies the reference sources for nonstructural requirements in the 2015 NEHRP Provisions.
ASCE 7-10 including Supplement 1 are incorporated in the 2015 NEHRP Recommended Provisions by reference.
Chapter 13 of ASCE/SEI 7-10 also references other Chapters of ASCE 7 for its provisions. For example, it references Chapter 11 for ground motions. Of special interest is the reference to Section 12.11.2 Anchorage of Concrete and Masonry Structural Walls. It references Section 12.11.2 for the application connection requirements of nonstructural concrete and masonry walls for buildings with flexible diaphragms.
The reason Section 12.11.2 is listed is because code users are often confused about what design forces should be applied to structural walls out-of-plane and this is the section that Ch. 13 refers the user to for concrete and masonry walls.
All equation numbers in this presentation are from ASCE/SEI 7-10 including Supplement 1, unless otherwise noted

## Slide 5: ASCE/SEI 7-10 Chapter 13 Organization
ASCE/SEI 7-10 Section | Title
13.1 | General
13.2 | General Design Requirements
13.3 | Seismic Demands on Nonstructural Components
13.4 | Nonstructural Component Anchorage
13.5 | Architectural Component
13.6 | Mechanical and Electrical Components
Notes: A table containing a partial list of ap and Rp values for architectural nonstructural component values from ASCE/SEI 7-10 Table 13.5-1 is presented.

## Slide 6: ASCE/SEI 7-10 Chapter 13 Organization
Section 13.1: Information on the applicability of the nonstructural design provisions
Section 13.2: General information on determination of:
  Importance of the component or system,
  Methods for establishing the adequacy of the component for seismic forces,
  Certification requirements for items identified as critical to life safety or function
Notes: This slide provides additional detail on the contents of Sections 13.1 and 13.2 of ASCE/SEI 7-10.

## Slide 7: ASCE/SEI 7-10 Chapter 13 Organization
Section 13.3: Procedures for determining the acceleration and displacement demands on nonstructural components
Section 13.4: Design considerations for attachment of nonstructural components to the structure
Sections 13.5 and 13.6: Detailed design considerations for architectural components, and mechanical and electrical components, respectively
Notes: This slide provides additional detail on the contents of Sections 13.3 through 13.6 of ASCE/SEI 7-10.

## Slide 8: Nonstructural Importance Factor - Ip
ASCE/SEI 7-10 Nonstructural Components are assigned a Component Importance Factor, Ip
The values of Ip is either 1.0 or 1.5
In ASCE/SEI 7-10, the value of Ip is based on
1. Requirement of the component to function after a DBE or
2. Occupancy Category of the structure or facility
In ASCE/SEI 7-10, nonstructural components/systems which are assigned an Ip = 1.5 are called Designated Seismic Systems.
Notes: This slide provides a discussion of the component importance factor, Ip. Nonessential components are assigned an importance factor equal to 1.0. Components with an importance factor of 1.5 must meet more stringent requirements.
For Ip = 1.0, the following behaviors are anticipated:
Minor earthquake ground motions – minimal damage; not likely to affect functionality.
Moderate earthquake ground motions – some damage that may affect functionality
Design earthquake ground motions – major damage but significant falling hazards are avoided; likely loss of functionality
Components with Ip = 1.5, they are expected to remain in place, sustain limited damage, and, when necessary, function following design earthquake level motions.

## Slide 9: Limits of Applicability
ASCE/SEI 7-10 Nonstructural provisions apply throughout the United States
Some components are exempt from the requirements of Chapter 13:
  All components in structures assigned to SDC A
  MEP components in structures assigned to SDC B
  Architectural components in structures assigned to SDC B if Ip = 1.0 (except certain parapets)
  MEP components in structures assigned to SDC C if Ip = 1.0
  Furniture and light or temporary items
  Small piping and ductwork in structures assigned to SDC D-F
Notes: This slide discuss limits on the application of the nonstructural seismic design requirements. Some nonstructural components are exempt from the requirements, depending on the seismic hazard level, component type, and size.
Chapter 13 does not apply to SDC A due to its very low level of seismic hazard; see ASCE/SEI 7-10 Section 11.7 and Section C11.7.
The exceptions applicable to other seismic design categories are based on SDC and Importance Factor.
With the exception of parapets supported by bearing walls or shear walls, all components in SDC B are exempt due to the low level of seismic risk. Parapets are not exempt because experience has shown these items can fail and pose a significant falling hazard even at low shaking levels.
Mechanical and electrical components in Seismic Design Category C with an importance factor (Ip) equal to 1.0 are exempt because they are subject to low levels of seismic hazard, they do not contain hazardous substances, and their function is not required to maintain life safety following an earthquake. Note that fire sprinkler piping is not exempt because it has an importance factor of 1.5
Small components with Ip in SDC D, E, and F also are exempt since they do not contain hazardous substances and are not large enough to pose a life-safety hazard if they fall, slide, or topple. Failures of unbraced distribution systems at or near the point of connection to nonstructural components have been observed in past earthquakes. For this reason, flexible connections such as expansion loops, braided hose, or expansion joints are required to allow for the larger relative displacements associated with unbraced components. Note that the stiffness of flexible connections may be sensitive to internal pressure and length of the connection.

## Slide 10: Nonstructural Demands
Seismic forces for design are computed considering variation of acceleration with relative height within the structure, and reduction in design force based upon estimated ductility of the component or its attachment
Procedures for evaluating nonstructural components subject to imposed deformations, such as story drift are provided
The seismic force demands tend to control the design for vibration-isolated or heavy components
Deformations control the design of elements that are continuous through multiple levels of a structure or across expansion joints between adjacent structures, such as cladding or piping
Notes: In this slide, the seismic demands on nonstructural components are summarized. Nonstructural components may be either acceleration or drift controlled, depending on the nature of the component. The seismic force calculations consider location of the component in the structure, as well as the estimated component ductility..
There are two types of demands on nonstructural components: forces and relative displacements between points of attachment. The forces are associated with the acceleration response of the structure at the points of attachment. Nonstructural demands are based on design earthquake level motions and MCE motions are not considered.

## Slide 11: Nonstructural Force Demands
Several different methods are available for calculating the force demands on nonstructural components
Several new methods for determining force demands were added in the ASCE/SEI 7-16
Equivalent Static Forces – Fp Equations
  Fp Equation 13.3-1 is independent of building structural properties
  Fp Equation 13.3-4 is dependent on building structural properties.
Both Fp equations are subject to the maximum and minimum values of Fp provided in Equations 13.3-2 and 13.3-3.
Notes: This slide provides a general overview of the equations used to determine forces on nonstructural components.
There are several different formulas for determining the acceleration demands on nonstructural components: forces and relative displacements between points of attachment. The forces are associated with the acceleration response of the structure at the points of attachment. Nonstructural demands are based on design earthquake level motions and MCE motions are not considered.
Equation 13.3-1 is intentionally conservative to cover the wide range of building structural systems, heights, etc.

## Slide 12: Nonstructural Force Demand
  Equation 13.3-3
  Equation 13.3-2
Fp (max) = 1.6 SDS Ip Wp
Fp (min) = 0.3 SDS Ip Wp
Equation 13.3-1
Notes: This slide presents Equation 13.3-1, the basic equation for seismic forces on nonstructural components. Equation 13.3-1 is intentionally conservative to cover the wide range of building structural systems, heights, etc. Fp forces are typically larger than those used for the design of the building. The minimum and maximum forces are given in Equations 13.3-2 and 13.3-3, respectively.

## Slide 13: Nonstructural Component Factors
ASCE/SEI 7-10 has ap and Rp factors assigned in tables that are used in Fp equation.
ap values range from 1.0 to 2.5 and values of ap can be taken as less than 2.5 based on dynamic analysis.
Rp values range from 1.0 to 12.0.
Importance factor Ip values are 1.0 or 1.5.
Wp is the component operating weight.
z is the height in structure of point of attachment of component with respect to the base.
h = average roof height of structure with respect to the base
Notes: The variables in the seismic force equations are discussed in the slide.
ap values represent the dynamic amplification of component response as a function of the fundamental periods of the structure and component. ap values are based on component behavior that is assumed to be either rigid or flexible. Where the fundamental period of the component is less than 0.06 seconds, dynamic amplification is not expected and the component is considered rigid and ap is equal to 1.
Rp values represent the energy absorption capability of a component and its attachments and is dependent on both overstrength and deformability.

## Slide 14: ap and Rp values for Selected Architectural Components
Architectural Component | ap | Rp
Cantilever Parapets | 2.5 | 2.5
Exterior Nonstructural Walls and Elements (e.g. precast cladding) | 1 | 2.5
Partitions | 1 | 2.5
Ceilings | 1 | 2.5
Penthouses (not an extension) | 2.5 | 3.5
Signs and Billboards | 2.5 | 2.5
Access Floors (special) | 1 | 2.5
Storage Cabinets | 1 | 2.5
Notes: A table containing a partial list of ap and Rp values for architectural nonstructural component values from ASCE/SEI 7-10 Table 13.5-1 is presented.

## Slide 15: Component Amplification Factor ap
Notes: A graph showing an alternate means of determining the component amplification factor is presented.
The tabulation of assumed ap values is not meant to preclude more precise determination of the component amplification factor where the fundamental periods of both structure and component are available. The NCEER formulation shown in Figure C13.3-1 may be used to compute ap as a function of Tp/T. This works if the building structure does not have significant higher modes of vibration.

## Slide 16: Explanation of 0.4SDS(1 + 2 z/h)
0.4SDS
1.2SDS
AA= 0.4SDS (1+2zA/h)
AB = 0.4SDS (1+2zB/h)
A
B
zA
zB
h
Floor Acceleration Distribution
Notes: This graphic illustrates the distribution of seismic accelerations over the height of a building, using an elevation of a 5-story building.
Equation 13.3-1 represents a trapezoidal distribution of floor accelerations within a structure, varying linearly from the acceleration at the ground (taken as 0.4SDS) to the acceleration at the roof (taken as 1.2SDS). The ground acceleration (0.4SDS) is intended to be the same acceleration used as design input for the structure itself, including site effects. The roof acceleration is established as three times the input ground acceleration based on examination of recorded in-structure acceleration data for short and moderate height structures in response to large California earthquakes. The minimum and maximum acceleration limits of Equations 13.3-2 and 13.3-3 are shown. Two nonstructural components are shown. Component “A” is attached at the second floor at a height of ZA. Component “B”, while at the 4th floor level, is suspended from the floor above. The shaking intensity it will experience is associated with the 5th floor, at a height of ZB.

## Slide 17: Explanation of z/h
h
z/h = 0
z/h = 2/5
z/h = 3/5
z/h = 4/5
z/h = 1
or design both connections for z/h = 3/5
z
Notes: This graphic provides other examples of how the location of the point of attachment of nonstructural component to the building influences the value of the factor z/h in the Equation 13.3-1, using an elevation of a 5-story building. In this example, floors are equally spaced with a story height of h/5.

## Slide 18: Alternative to Fp Equation 13.3-1
ai = acceleration at level i from modal analysis per Section 12.9 with R = 1.0
Ax = torsional amplification factor per Eq. 12.8-14
Linear dynamic or nonlinear response history analysis may be used
Upper and lower limits of Fp per Eqs. 13.3-2 and 13.3-3 apply to dynamic analysis
Equation 13.3-4
Notes: This slide discusses Equation 13.3-4, which permits an alternate determination of the component design forced based on the dynamic properties of the structure.
To use the equation, a modal analysis of the structure must be performed satisfying modal analysis procedures described in Chapter 12 of ASCE/SEI 7-10 including scaling of results assuming R = 1. Significant nonstructural items can be included in the modal analysis model. If the nonstructural item is included the value of ap can also be determined in the analysis. However ap cannot be taken as less than 1.0. Use of this equation can sometimes lead to significantly lower Fp values than Equation 13.3-1 especially in the middle and upper levels of moment frame building with 3 or more stories but requires much more computational effort , which often is impractical.
Where seismic response history analysis is used with at least seven ground motions, ai is taken as the average of the maximum accelerations. When less than seven ground motions are used, the maximum acceleration value for each floor is the maximum value obtained from the ground motions analyzed.

## Slide 19: New Alternatives in ASCE/SEI 7-16
The use of floor response spectra for determination of the seismic design force is now explicitly permitted (ASCE/SEI 7-16 Sec. 13.3.1.4.1).
The floor response spectrum is calculated for each ground motion record analyzed.
The floor acceleration, ai, is the maximum acceleration value from the floor response spectra for the component period, and the value of ap shall be taken as 1.0.
Notes: The use of floor response spectra for determination of the seismic design force is now explicitly permitted (ASCE/SEI 7-16 Sec. 13.3.1.4.1). Application of this approach requires that a floor response spectrum be calculated for the design earthquake at each level of the structure, based on a seismic response history analysis performed in accordance with ASCE/SEI 7-10 Section 12.9 or in accordance with the procedures in ASCE/SEI 7-10 Chapters 16, 17 or 18.

## Slide 20: New Alternatives in ASCE/SEI 7-16
Aix = floor acceleration for mode x at Level i
pix = modal participation factor for mode x at Level i
Sai = spectral acceleration for mode x
Alternate floor response spectra method based on a modal analysis is available (ASCE/SEI 7-16 Sec. 13.3.1.4.2).
The periods/mode shapes of the structure must be calculated for at least the first three modes in each orthogonal direction
The component dynamic amplification factor, DAF, determined by the ratio of the component period, Tp, to the building modal period, Tx
Notes: The graph shows the dynamic amplification factor is determined by the ratio of the component period, Tp, to the building modal period, Tx.
This slide discusses the use of floor response spectra for determination of the seismic design force, which is now explicitly permitted (ASCE/SEI 7-10 Sec. 13.3.1.4.1). The graph used for determining the dynamic amplification factor, DAF, is shown, Application of this approach requires that a floor response spectrum be calculated for the design earthquake at each level of the structure, based on a seismic response history analysis performed in accordance with ASCE/SEI 7-10 Section 12.9 or in accordance with the procedures in ASCE/SEI 7-10 Chapters 16, 17 or 18.

## Slide 21: Relative Displacement Demand for Design Earthquake Motions
Relative Displacements for Displacement-Sensitive Components (ASCE/SEI 7-10 Section 13.3.2)
  Anticipated Relative Displacements at Design Earthquake Level (Dp)
  Explicit equations and options for use of building drifts
Required for anchorage of nonstructural components (ASCE/SEI 7-10 Section 13.4.1)
Required for architectural components themselves which pose a life safety hazard including exterior wall elements and glazing. (ASCE/SEI 7-10 Section 13.5.2)
Required for mechanical and electrical components themselves where Ip is greater than 1.0. (ASCE/SEI 7-10 Section 13.6.3)
Notes: This slide provides an overview of the displacement requirements for nonstructural components. The displacement demands can be based on building specific or generic building information. Glazing acceptance criteria is set forth in ASCE/SEI 7-10 Section 13.9. Except for glazing, no specific displacement acceptance criteria is provided.

## Slide 22: Load Combinations
In ASCE/SEI 7-10 Section 12.4,strength and allowable stress design load combinations are provided
Eh is defined as Fp for nonstructural components and Ev is defined as 0.2 SDSD
The redundancy factor, ρ, is specified as 1.0 for nonstructural components. (ASCE/SEI 7-10 Section 13.3.1)
Ωo is specified in Tables 13.5-1 and 13.6-1
The load combinations with Ωo and are used for calculating demands on attachments to concrete and masonry
Allowable stress design methods are addressed in ASCE/SEI 7-10 Section 13.1.7.
Notes: This slide discusses how seismic loads on nonstructural components are combined with other loads using load combinations. The seismic design force on the component, Fp, is required to be combined with other loads as set forth in ASCE/SEI 7-10 Section 12.4. To use Section 12.4, there are certain items that need to be defined and these include Eh, Ev,  and Ωo.

## Slide 23: Attachment of Nonstructural Components
Design seismic forces in the connected parts, Fp, are prescribed in ASCE/SEI 7-10 Section 13.4
  Rp limited to 6 for design of attachments to the structure
  Design capacity for anchors in concrete is determined in accordance with ACI 318
  Design capacity for anchors in masonry is determined in accordance with ACI 530
Notes: This slide discusses the requirements in Section 13.4 for attachment of nonstructural components to the structure. The goal of this section is to ensure that attachments such as anchor bolts exhibit ductile behavior or provide a specified degree of excess strength. The requirements for anchorage to concrete and masonry were revised in the 2010 and 2016 editions of the ASCE 7

## Slide 24: Attachment of Nonstructural Components to Concrete or Masonry
For anchors in concrete and masonry, at least one of the following conditions must be satisfied:
  The component or a support in the load path leading to the structure undergoes ductile yielding at a load level less than the design strength of the corresponding anchor, or
  The anchors are designed to resist the load combinations considering Ω0
Notes: In this slide, the special requirements for attachment of components to concrete an masonry are summarized. Attachments must be designed to behave in a ductile manner or be designed for amplified forces.

## Slide 25: Architectural Components (Table 13.5-1)
  Nonstructural walls & partitions
  Parapets & chimneys
  Exterior nonstructural wall elements & connections
  Veneer
  Penthouses
  Ceilings
  Cabinets
  Access floors
  Signs
  Billboards
  Appendages
  Glazing
Notes: This slide contains a partial list of architectural components included in ASCE/SEI 7 Table 13.5-, and an image of a large interior workspace.
The requirements are intended to apply only to permanently attached components – not to furnishings, temporary items, or mobile units. Furnishings such as tables, chairs, and desks may shift but generally pose minimal hazards provided they do not obstruct emergency egress routes. Storage cabinets, tall bookshelves, and other items of significant mass are not exempt and must be anchored or braced in accordance with ASCE/SEI 7.

## Slide 26: Mechanical Components (Table 13.6-1)
OSHPD/FDD
Boilers and furnaces
HVAC
Piping systems
Engines
Turbines
Fans
Furnaces
Chillers
Elevators
Escalators
Notes: This slide contains a partial list of the mechanical components and systems found in ASCE/SEI 7 Table 13.6-1, and an image of a pump that was torn from an inertia pad in the 1994 Northridge earthquake.
For both mechanical and electrical components the focus is on the supports and anchorage of the component unless Ip = 1.5, in which case the component itself must be checked.

## Slide 27: Electrical Components (Table 13.6-1)
Conduits
Bus ducts
Cable trays
Lighting fixtures
Motors
Generators
Communication eqmt
Inverters
Transformers
Motor control centers
Switch gear
Notes: This slide contains a partial list of the electrical components and systems found in ASCE/SEI 7 Table 13.6-1, and an image of a worker installing wiring above a suspended ceiling grid.

## Slide 28: Design and Detailing Requirements of Architectural Components
ASCE/SEI 7-10 Section 13.5
Specific demands for exterior nonstructural wall elements and connections (13.5.3)
Suspending Ceilings – CISCA, ASTM C635 and ASTM C636 (13.5.6)
Access Floors (13.5.7)
Tall Partitions – independent bracing (13.5.8)
Glazing – Drift capacity AAMA 501.6 (13.5.9)
Notes: This slide lists some of the sections in ASCE/SEI 7 Section 13.5 that contain specific design requirements for architectural components..
The requirements of Section 13.5 are intended to reduce property damage and life-safety hazards posed by architectural components due to loss of stability or integrity. Architectural components may pose a direct falling hazard to building occupants or to people outside the building (as in the case of parapets, exterior cladding, and glazing). Failure or displacement of interior components (such as partitions and ceiling systems in exits and stairwells) may block egress.

## Slide 29: Design and Detail Requirements for Mechanical and Electrical Equipment
ASCE/SEI 7-10 Section 13.6:
Sprinkler systems – NFPA 13
Escalators and Elevators – ASME A17.1
Vessels – ASME BPVC
Piping – ASME B31
Lighting fixtures – Prescriptive detail requirements
Many specific prescriptive details for mechanical and
electrical Equipment
Notes: This slide lists some of the sections in ASCE/SEI 7 Section 13.6 that contain specific design requirements for mechanical and electrical components..
Many of these components have requirements found in the applicable referenced standard.

## Slide 30: Special Certification Requirements for Certain Designated Seismic Systems (Ip=1.5)
In ASCE/SEI 7-10 Section 13.2.2 - Seismic qualification required in SDC C through F for :
  Active mechanical and electrical equipment that are required to function following a DBE
  Components containing hazardous contents
Qualification to demonstrate functionality after being subject to a DBE to be determined by one of the following:
  Shake table testing – ICC-ES AC-156
  Experience Data
  Analysis (extremely difficult for active equipment)
Certification required by supplier indicating compliance
Notes: This slide lists some of the requirements for Designated Seismic Systems which may be subject to special certification. While the goal of design for most nonstructural components is to prevent detachment or toppling that would pose a hazard to life safety, designated seismic systems (with Ip = 1.5) are intended to meet higher performance goals. In some cases, failure of mechanical or electrical equipment itself poses a significant hazard. This section addresses the design and certification of designated seismic system components and their supports and attachments. Examples of designated seismic systems include fire protection piping, uninterruptible power supplies for hospitals, and certain vessels or piping that contain highly toxic or explosive substances.

## Slide 31: HVAC Fan Unit Support Design Example
The component located at roof level of a five-story office building, near a an active fault in Los Angeles, California. Risk Category II.
Notes: This slide lists shows a plan and two elevations of a HVAC fan unit, which will be used as an example to illustrate the application of the nonstructural seismic design requirements.
In this example, the HVAC fan unit is 4-feet high, 5-feet wide, 8-feet long and weighs 3000 lbs. The unit is anchored to a concrete roof slab and attached with 4 anchors, one at each corner of the unit.

## Slide 32: Seismic Design Parameters and Coefficients
SDS = 1.487 (for the selected location and site class)
Seismic Design Category = D (Table 11.6-1)
Wp = 3,000 lb (given)
ap = 2.5 for both direct attachment (Table 13.6-1)
and spring isolated
Rp = 6.0 for HVAC fans, directly attached (Table 13.6-1)
(not vibration isolated)
Rp = 2.0 for spring isolated components (Table 13.6-1)
with restraints
  Ω0 = 2.5 for anchors in concrete or masonry unless controlled by a ductile yielding element
Ip = 1.0 (Sec. 13.1.3)
z/h = 1.0 (for roof-mounted equipment)
Notes: This slide provides design parameters and coefficients from Chapters 11 and 13 of ASCE/SEI 7.including the ground shaking intensity, and the design coefficients from Table 13.6-1. The component importance factor is 1.0.

## Slide 33: Free Body Diagram for Force Analysis
Notes: This slide shows a free body diagram for seismic force analysis, including dead loads, and the horizontal and vertical seismic forces. The horizontal and vertical reactions at the supports are also shown.

## Slide 34: Determine Seismic Forces
Fp = = 2,231 lb (Eq.13.3-1)
Fpmax = 1.6 x 1.487 x 1.0 x 3,000 = 7,138 lb (Eq. 13.3-2)
Fpmin = 0.3 x 1.487 x 1.0 x 3,000 = 1,338 lb (Eq. 13.3-3)
Since Fp is greater the Fpmin and less than Fpmax, the value determined from
Equation 13.3-1 applies.
Eh = ρQE (Eq. 12.4-3)
Ev = 0.2SDSD (Eq. 12.4-4)
where:
QE (due to horizontal application of Fp) = 2,231 lb (Sec. 12.4.2-1)
ρ = 1.0 (HVAC units are nonstructural components) (Sec. 13.3.1)
D = dead load effect (due to vertical load application)
Notes: The slide provides calculations and notes for computing component forces. The design force Fp is calculated using Equation 13.3-1, and the upper and lower limits on the lateral forces are also checked.

## Slide 35: Determine Reactions
Substituting, one obtains:
Eh = ρQE = (1.0)(2,231 lb) = 2,231 lb (horizontal earthquake effect)
Ev = 0.2SDSD = (0.2)(1.487)(3,000 lb) = 892 lb (vertical earthquake effect)
(1.2 + 0.2SDS) D + ρQE + L + 0.2S (Basic Load Combination 5)
(0.9 - 0.2SDS) D + ρQE + 1.6H (Basic Load Combination 7)
U = (1.2 + 0.2SDS) D + ρQE
Vu = = 558 lb/bolt
Tu = (no tension)
Notes: The terms Eh and Ev are substituted into the basic load combinations for strength design of Section 12.4.2 to determine the design member and connection forces to be used in conjunction with seismic loads.
Based on the free-body diagram, the seismic load effects can be used to determine bolt shear, Vu, and tension, Tu (where a negative value indicates tension).

## Slide 36: Determine Anchor Loads
U = (0.9 - 0.2SDS) D + ρQE
Vu = = 558 lb/bolt
Tu = (no tension)
Notes: In the final step, the shear and tension loads on the anchors are calculated. The signs of SDS and FP have been selected to result in the largest value of anchor tension Tu.

## Slide 37: Questions?
Notes: Slide prompting participants to ask questions.

## Slide 38: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.