## Slide 1: Nonbuilding Structure Design Example Problems By J. G. (Greg) Soules, P.E., S.E., SECB Originally developed by Harold O. Sprague, Jr., P.E.
17
Disclaimer
Notes: Introduction slide.
This unit is only a brief introduction to the subject of earthquake resistant design of nonbuilding structures.

## Slide 2: Nonbuilding Structures Design Examples
Example 17.1 - Nonbuilding Structures versus Nonstructural Components
  Example 17.1.1 - Nonbuilding Structure
  Example 17.1.2 - Nonstructural Component
Nonbuilding Structures Similar to Buildings
  Example 17.2 - Pipe Rack, SDC D
  Example 17.3 - Steel Storage Rack, SDC C
  Example 17.4 - Electric Generating Power Plant, SDC D
  Example 17.5 - Pier/Wharf Design, SDC D
Notes: Slide 2 is the table of contents for the presentation. SDC stands for Seismic Design Category

## Slide 3: Nonbuilding Structures Design Examples
Nonbuilding Structures Not Similar to Buildings
  Example 17.6 - Tanks and Vessels, SDC D
    Example 17.6.1 - Flat-Bottom Water Storage Tank
    Example 17.6.2 - Flat-Bottom Gasoline Tank
  Example 17.7 - Vertical Vessel, SDC D
Notes: Slide 3 is the table of contents for the presentation.

## Slide 4: Nonbuilding Structures vs. Nonstructural Components
  Many industrial structures are classified as either nonbuilding structures or nonstructural components.
  The intent of ASCE 7-16 is to provide a clear and consistent design methodology regardless of whether the structure is a nonbuilding structure or a nonstructural component.
  Central to the methodology is how to determine which classification is appropriate.
Notes: Slide 4 is a discussion of the differences between nonbuilding structures and nonstructural components.

## Slide 5: Nonbuilding Structures vs. Nonstructural Components
  Table 17-1 provides a simple method to determine the appropriate classification.
Table 17-1 Applicability of the Chapters of the Standard |  | 
Supporting Structure | Supported Item | 
 | Nonstructural Component | Nonbuilding Structure
Building | Chapter 12 for supporting structure; Chapter 13 for supported item | Chapter 12 for supporting structure; Chapter 15 for supported item
Nonbuilding | Chapter 15 for supporting structure; Chapter 13 for supported item | Chapter 15 for both supporting structure and supported item
Notes:   Slide 5 shows Table 17-1, which provides a simple method to determine if the structure in question is a nonbuilding structure or a nonstructural component.
  Additional discussion on determining if the structure is a nonstructural component or a nonbuilding structure can be found in Bachman, Robert and Dowty, Susan, “Nonstructural Component or Nonbuilding Structure?”, Building Safety Journal, International Code Council, April-May 2008.

## Slide 6: Nonbuilding Structures vs. Nonstructural Components
Example 17.1.1
  Combustion turbine building.
  Building supports four filter units connected in a fashion that couples their dynamic response.
Example 17.1.2
  Combustion turbine building.
  Building supports four filter units that are independent structures.
Figure 17-1 Combustion turbine building
(1.0 ft = 0.3048 m)
Notes: Slide 6 introduces Example Problem 17.1 – Nonbuilding Structures vs. Nonstructural Components. The slide shows Figure 17-1, a combustion turbine building, on the right. The illustration shows an isometric view of a single story rectangular steel braced frame nonbuilding structure. The longitudinal direction of the nonbuilding structure is made up of four equal 30-foot long bays with the center two bays braced with chevron bracing. The transverse direction of the nonbuilding structure is made up of three bays with a total length of 80 feet with the center bay braced with chevron bracing. The height of the nonbuilding structure is shown as 25 feet. The roof of the nonbuilding structure is shown supporting 4block shaped inlet filters. One inlet filter is shown centered on each longitudinal bay. All 4 inlet filters are shown centered on the middle bay in the transverse direction.
The following two examples illustrate the difference between nonbuilding structures that are treated as nonstructural components, using ASCE 7-16 Chapter 13, and those which are designed in accordance with ASCE 7-16 Chapter 15. In many instances, the weight of the supported nonbuilding structure is relatively small compared to the weight of the supporting structure (less than 25% of the combined weight) such that the supported nonbuilding structure will have a relatively small effect on the overall nonlinear earthquake response of the primary structure during design level ground motions. It is permitted to treat such structures as nonstructural components and use the requirements of ASCE 7-16 Chapter 13 for their design. Where the weight of the supported structure is relatively large (greater than or equal to 25% of the combined weight) compared to the weight of the supporting structure, the overall response can be affected significantly. In such cases it is intended that seismic design loads and detailing requirements be determined following the procedures of ASCE 7-16 Chapter 15. Where there are multiple large nonbuilding structures, such as vessels supported on a primary nonbuilding structure and the weight of an individual supported nonbuilding structure does not exceed the 25 percent limit but the combined weight of the supported nonbuilding structures does, it is recommended that the combined analysis and design approach of ASCE 7-16 Chapter 15 be used.

## Slide 7: Nonbuilding Structures vs. Nonstructural Components
Example 17.1.1
  Four inlet filters = WIF = 4 x 34 kips = 136 kips
  Support structure = WSS = 288 kips
  WCombined = 136 kips + 288 kips = 424 kips
  Therefore, ASCE 7-16 Section 15.3.2 is applicable and the requirements of Chapter 15 are to be followed.
Notes: Slide 7 shows Example 17.1.1 – inlet filters dynamically coupled.
Because the weight of the inlet filters is 25 percent or more of the combined weight of the nonbuilding structure and the supporting structure (ASCE 7-16 Section 15.3.2), the inlet filters are classified as “nonbuilding structures” and the seismic design forces must be determined from analysis of the combined seismic-resistant structural systems. This would require modeling the filters, the structural components of the filters, and the structural components of the combustion turbine supporting structure to determine accurately the seismic forces on the structural elements as opposed to modeling the filters as lumped masses.

## Slide 8: Nonbuilding Structures vs. Nonstructural Components
Example 17.1.2
  One (effective) inlet filters = WIF = 34 kips
  Support structure = WSS = 288 kips
  WCombined = (4 x 34 kips) + 288 kips = 424 kips
  Therefore, ASCE 7-16 Section 15.3.1 is applicable and the requirements of Chapter 13 are to be followed.
Notes: Slide 8 shows Example 17.1.2 – inlet filters not dynamically coupled.
Because the weight of an inlet filter is less than 25 percent of the combined weight of the nonbuilding structures and the supporting structure (ASCE 7-16 Section 15.3.1), the inlet filters are classified as “nonstructural components” and the seismic design forces must be determined in accordance with ASC 7-16 Chapter 13. In this example, the filters could be modeled as lumped masses. The filters and the filter supports could then be designed as nonstructural components.

## Slide 9: Nonbuilding Structures Similar to Buildings
Example 17.2 Pipe Rack
Figure 17-2 Pipe rack (1.0 ft = 0.3048 m)
Notes: The figure shows the plan, elevation and section views of a pipe rack.
Slide 9 shows Example 17.2 – Pipe Rack. Three figures are shown. The top figure is a plan view of the pipe rack. The width of the pipe rack is 20 feet. The left side of the pipe rack is made up of six equal 20-foot long bays. The center bay is 20 feet long and contains x-bracing in the horizontal plane. The right side of the pipe rack is made up of five equal 20-foot long bays. Four runs of piping are shown parallel to the longitudinal direction. An expansion loop is shown on the right side of the pipe rack indicating a break in the continuity of the pipe rack. The second figure is an elevation view of the pipe rack in the longitudinal direction. X-bracing in the vertical plane is shown in the same bay as the x-bracing shown in the plan view. Two tiers of piping are shown. The height from grade to the bottom of the upper run of piping is shown as 15 feet. The distance from the bottom of the upper run of piping to the top of the frame is shown as 3 feet. The third figure is an elevation view of the pipe rack in the transverse direction. The transverse direction of the pipe rack is shown as a single bay moment frame with two tiers of piping with four pipes on each tier. The height from grade to the bottom of the lower run of piping is shown as 10 feet. The distance from the bottom of the lower run of piping to the top of the frame is shown as 8 feet.
A two-tier, 12-bay pipe rack in a petrochemical facility has concentrically braced frames in the longitudinal direction and ordinary moment frames in the transverse direction. The pipe rack supports four runs of 12-in.-diameter pipe carrying naphtha on the top tier and four runs of 8-in.-diameter pipe carrying water for fire suppression on the bottom tier. The minimum seismic dead load for piping is 35 psf on each tier to allow for future piping loads. The seismic dead load for the steel support structure is 10 psf on each tier.

## Slide 10: Nonbuilding Structures Similar to Buildings
This example illustrates the calculation of design base shears and maximum inelastic displacements for a pipe rack using the equivalent lateral force (ELF) procedure.
For this example, the design ground motion parameters are as follows:
  SDS = 0.40
  SD1 = 0.18
Notes: Slide 10 is a continuation of Example 17.2 – Pipe Rack.

## Slide 11: Nonbuilding Structures Similar to Buildings
Risk Category and Importance Factor
  The upper piping carries naphtha.
  Material safety datasheet (MSDS) for naphtha indicates that naphtha has a medium lethal concentration [LC(50)] of 5.2 mg per liter.
  Standard Section C1.5.3 defines a toxic material as a chemical with a LC(50) between 2 mg per liter and 20 mg per liter.
  Naphtha is therefore a toxic material and is assigned to Risk Category III per ASCE 7-16 Table 1.5-1.
Notes: Slide 11 is a continuation of Example 17.2 – Pipe Rack.

## Slide 12: Nonbuilding Structures Similar to Buildings
Risk Category and Importance Factor
  The lower piping is required for fire suppression and is assigned to Risk Category IV per ASCE 7-16 Table 1.5-1.
  Therefore, pipe rack is assigned to Risk Category IV based on the more severe category.
  From ASCE 7-16 Table 1.5-2, Ie = 1.5
Seismic Design Category
  Per ASCE 7-16 Section 11.6 based on Risk Category IV, SDS = 0.40, and SD1 = 0.18, the Seismic Design Category (SDC) is D.
Notes: Slide 12 is a continuation of Example 17.2 – Pipe Rack.
ASCE 7-16 Section 15.4.1.1 directs the user to use the largest value of Ie based on the applicable reference document listed in ASCE 7-16 Chapter 23, the largest value selected from ASCE 7-16 Table 1.5-2, or as specified elsewhere in Standard Chapter 15. It is important to be aware of the requirements of ASCE 7-16 Section 15.4.1.1. While the importance factor for most structures will be determined based on ASCE 7-16 Table 1.5-2, there are reference documents that define importance factors greater than those found in ASCE 7-16 Table 1.5-2.

## Slide 13: Nonbuilding Structures Similar to Buildings
Transverse Direction – R Factor Options
  In ASCE 7-16 Table 12.2-1, ordinary steel moment frames are not permitted in Seismic Design Category D. There are several options for ordinary steel moment frames found in ASCE 7-16 Table 15.4-1 as follows:
  ASCE 7-16 Table 15.4-1, Ordinary moment frames of steel, R = 3.5. According to note c in ASCE 7-16 Table 15.4-1, this system is allowed for pipe racks up to 35’ without limitations on the connection type. Option requires the use of the AISC Seismic Provisions.
Notes: Slide 13 is a continuation of Example 17.2 – Pipe Rack.
According to ASCE 7-16 Section 15.4-1, either ASCE 7-16 Table 12.2-1 or ASCE 7-16 Table 15.4-1 may be used to determine the seismic parameters, although mixing and matching of values and requirements from the tables is not allowed. In ASCE 7-16 Chapter 15, selected nonbuilding structures similar to buildings are provided an option where both lower R values and less restrictive height limits are specified. This option permits selected types of nonbuilding structures which have performed well in past earthquakes to be constructed with fewer restrictions in Seismic Design Categories D, E and F provided seismic detailing is used and design force levels are considerably higher. The R value-height limit trade-off recognizes that the size of some nonbuilding structures is determined by factors other than traditional loadings and result in structures that are much stronger than required for seismic loadings (Soules, 2006). Therefore, the structure’s ductility demand is generally much lower than a corresponding building. The R value-height trade-off also attempts to obtain the same structural performance at the increased heights. The user will find that the option of reduced R value with less restricted height will prove to be the economical choice in most situations due to the relative cost of materials and construction labor. It must be emphasized that the R value-height limit trade-off of ASCE 7-16 Table 15.4-1 applies only to nonbuilding structures similar to buildings and cannot be applied to building structures.

## Slide 14: Nonbuilding Structures Similar to Buildings
Transverse Direction – R Factor Options
  ASCE 7-16 Table 15.4-1, Ordinary moment frames of steel with permitted height increase, R = 2.5. This option is intended for pipe racks greater than 65’ high and limited to 100’ and is not applicable for this example.
  ASCE 7-16 Table 15.4-1, Ordinary moment frames of steel with unlimited height, R=1. Option does not require the use of the AISC Seismic Provisions.
  For this example, option with R = 3.5 is chosen.
Notes: Slide 14 is a continuation of Example 17.2 – Pipe Rack.
Ordinary steel moment frames are retained for use in nonbuilding structures such as pipe racks because they allow greater flexibility for accommodating process piping and are easier to design and construct than special steel moment frames.

## Slide 15: Nonbuilding Structures Similar to Buildings
Transverse Direction – Seismic Response Coefficient
  Using ASCE 7-16 Equation 12.8-2:
  From analysis, T = 0.42 second. Using ASCE 7-16 Equation 12.8-3 for T ≤ TL, Cs does not need to exceed:
Notes: Slide 15 is a continuation of Example 17.2 – Pipe Rack.
For nonbuilding structures, the fundamental period is generally approximated for the first iteration and must be verified with final calculations. ASCE 7-16 Section 15.4.4 makes clear that the approximate period equations of ASCE 7-16 Section 12.8.2 do not apply to nonbuilding structures.

## Slide 16: Nonbuilding Structures Similar to Buildings
Transverse Direction – Seismic Response Coefficient
  Using ASCE 7-16 Equation 12.8-5, Cs must not be less than: Cs = 0.044IeSDS ≥ 0.01 = 0.044(1.5)(0.4) = 0.0264
  ASCE 7-16 Equation 12.8-2 controls; Cs = 0.171.
Notes: Slide 16 is a continuation of Example 17.2 – Pipe Rack.
Always remember to check the minimum base shear value.

## Slide 17: Nonbuilding Structures Similar to Buildings
Transverse Direction – Seismic Weight
  The seismic weight resisted by the moment frame in the transverse direction is shown below based on two levels of piping, a 20 ft bent spacing, a bent width (perpendicular with the piping) of 20 ft, piping dead weight of 35 psf and structure dead weight of 10 psf: W = 2(20 ft)(20 ft)(35 psf + 10 psf) = 36 kips
Notes: Slide 17 is a continuation of Example 17.2 – Pipe Rack.
The piping dead weight includes the weight of the fluid in the pipe. In ASCE 7-16 Chapter 3, this topic is discussed under Section 3.1.3 “Weight of Fixed Service Equipment”.

## Slide 18: Nonbuilding Structures Similar to Buildings
Transverse Direction – Base Shear & Drift
  Using ASCE 7-16 Equation 12.8-1 the base shear V is: V = CsW = 0.171(36 kips) = 6.2 kips
  Drift of the pipe rack in the transverse direction was calculated by elastic analysis using the design forces calculated above. The calculated lateral drift, δxe = 0.328 inch. Using ASCE 7-16 Equation 12.8-15:
Notes: Slide 18 is a continuation of Example 17.2 – Pipe Rack.
The lateral drift must be checked with regard to acceptable limits. The acceptable limits for nonbuilding structures are not found in codes. Rather, the limits are what is acceptable for the performance of the piping. In general, piping can safely accommodate the amount of lateral drift calculated in this example. P-delta effects must also be considered and checked as required in ASCE 7-16 Section 15.4.5.

## Slide 19: Nonbuilding Structures Similar to Buildings
Transverse Direction – Redundancy Factor
  The seismic force-resisting system is an ordinary moment resisting frame with only two columns in a single frame. The frames repeat in an identical pattern.
  Loss of moment resistance at the beam-to-column connections at both ends results in a loss of more than 33% in story strength. Therefore, ASCE 7-16 Section 12.3.4.2 Condition a is not met.
Notes: Slide 19 is a continuation of Example 17.2 – Pipe Rack.
Some nonbuilding structures are designed with parameters from ASCE 7-16 Table 12.2-1 or 15.4-1 if they are termed “nonbuilding structures similar to buildings”. For such structures (assigned to Seismic Design Category D, E, or F) the redundancy factor applies. Pipe racks, being fairly simple moment frames or braced frames, are in the category similar to buildings. Because this structure is assigned to Seismic Design Category D, ASCE 7-16 Section 12.3.4.2 applies.

## Slide 20: Nonbuilding Structures Similar to Buildings
Transverse Direction – Redundancy Factor
  The moment frame as described above consists only of a single bay. Therefore, ASCE 7-16 Section 12.3.4.2 Condition b is not met.
  The value of r in the transverse direction is therefore 1.3.
Notes: Slide 20 is a continuation of Example 17.2 – Pipe Rack.

## Slide 21: Nonbuilding Structures Similar to Buildings
Longitudinal Direction – R Factor Options
  In ASCE 7-16 Table 12.2-1, ordinary steel concentrically braced frames are not permitted for Seismic Design Category D (with some exceptions). Several options for ordinary steel concentrically braced frames are found in ASCE 7-16 Table 15.4-1 as follows:
  ASCE 7-16 Table 15.4-1, ordinary steel concentrically braced frame, R = 3.25. According to Note b in ASCE 7-16 Table 15.4-1, this system is allowed for pipe racks up to 65 feet high. Option requires the use of the AISC Seismic Provisions.
Notes: Slide 21 is a continuation of Example 17.2 – Pipe Rack.

## Slide 22: Nonbuilding Structures Similar to Buildings
Longitudinal Direction – R Factor Options
  ASCE 7-16 Table 15.4-1, ordinary steel concentrically braced frames with permitted height increase, R = 2.5. This option is intended for pipe racks with height greater than 65 feet and limited to 160 feet. This option is not applicable for this example.
  ASCE 7-16 Table 15.4-1, ordinary steel concentrically braced frames with unlimited height, R = 1.5. Option does not require the use of the AISC Seismic Provisions.
  For this example, option with R = 3.25 is chosen.
Notes: Slide 22 is a continuation of Example 17.2 – Pipe Rack.

## Slide 23: Nonbuilding Structures Similar to Buildings
Longitudinal Direction – Seismic Response Coefficient
  Using ASCE 7-16 Equation 12.8-2:
  From analysis, T = 0.24 second. Using ASCE 7-16 Equation 12.8-3 for T ≤ TL, Cs does not need to exceed:
Notes: Slide 23 is a continuation of Example 17.2 – Pipe Rack.
For nonbuilding structures, the fundamental period is generally approximated for the first iteration and must be verified with final calculations. ASCE 7-16 Section 15.4.4 makes clear that the approximate period equations of ASCE 7-16 Section 12.8.2 do not apply to nonbuilding structures.

## Slide 24: Nonbuilding Structures Similar to Buildings
Longitudinal Direction – Seismic Response Coefficient
  Using Standard Equation 12.8-5, Cs must not be less than: Cs = 0.044IeSDS ≥ 0.01 = 0.044(1.5)(0.4) = 0.0264
  ASCE 7-16 Equation 12.8-2 controls; Cs = 0.185.
Notes: Slide 24 is a continuation of Example 17.2 – Pipe Rack.
Always remember to check the minimum base shear value.

## Slide 25: Nonbuilding Structures Similar to Buildings
Longitudinal Direction – Seismic Weight
  The seismic weight resisted by the braced frame in the longitudinal direction is shown below based on two levels of piping, a 240 ft span, a bent width (perpendicular with the piping) of 20 ft, piping dead weight of 35 psf and structure dead weight of 10 psf: W = 2(240 ft)(20 ft)(35 psf + 10 psf) = 432 kips
Notes: Slide 25 is a continuation of Example 17.2 – Pipe Rack.
The piping dead weight includes the weight of the fluid in the pipe. In ASCE 7-16 Chapter 3, this topic is discussed under Section 3.1.3 “Weight of Fixed Service Equipment”. In this example problem, only one panel of bracing is present in the longitudinal direction.

## Slide 26: Nonbuilding Structures Similar to Buildings
Longitudinal Direction – Base Shear
  Using ASCE 7-16 Equation 12.8-1 the base shear V is: V = CsW = 0.185(432 kips) = 79.9 kips
Notes: Slide 26 is a continuation of Example 17.2 – Pipe Rack.

## Slide 27: Nonbuilding Structures Similar to Buildings
Longitudinal Direction – Redundancy Factor
  The seismic force-resisting system is an ordinary braced frame with only one set of bracing provided on each side.
  Removal of one brace would result in a reduction of greater than 33% in story strength. Therefore, ASCE 7-16 Section 12.3.4.2 Condition a is not met.
  Condition b is not met because two bays of seismic force-resisting perimeter framing are not provided in each orthogonal direction.
  The value of r in the longitudinal direction is therefore 1.3.
Notes: Slide 27 is a continuation of Example 17.2 – Pipe Rack.
Some nonbuilding structures are designed with parameters from ASCE 7-16 Table 12.2-1 or 15.4-1 if they are termed “nonbuilding structures similar to buildings”. For such structures (assigned to Seismic Design Category D, E, or F) the redundancy factor applies. Pipe racks, being fairly simple moment frames or braced frames, are in the category similar to buildings. Because this structure is assigned to Seismic Design Category D, ASCE 7-16 Section 12.3.4.2 applies.
If two bays of bracing were provided on each side of the pipe rack in the longitudinal direction, the pipe rack would meet Condition (a) and qualify for a redundancy factor, , of 1.0 in that direction.

## Slide 28: Nonbuilding Structures Similar to Buildings
Orthogonal Loads
  For SDC D, ASCE 7-16 Section12.5.4 requires that the braced sections of the pipe rack be evaluated using the orthogonal combination rule of ASCE 7-16 Section 12.5.3a.
  Two cases must be checked
    100% transverse seismic force plus 30% longitudinal seismic force.
    100% longitudinal seismic force plus 30% transverse seismic force.
Notes: Slide 28 is a continuation of Example 17.2 – Pipe Rack.
Because the pipe rack in this example falls in SDC D, ASCE 7-16 Section 12.5.4 requires that the braced sections of the pipe rack be evaluated using the orthogonal combination rule of ASCE 7-16 Section 12.5.3a. Two cases must be checked - 100% transverse seismic force plus 30% longitudinal seismic force and 100% longitudinal seismic force plus 30% transverse seismic force. The vertical seismic force represented by 0.2SDSD is only applied once in each load case. Do not include the vertical seismic force in with both horizontal seismic load combinations. In this pipe rack example, due to the bracing configuration, the foundation and column anchorage would be the only components impacted by the orthogonal load combinations.

## Slide 29: Nonbuilding Structures Similar to Buildings
Example 17.3 Steel Storage Rack
Figure 17-3 Steel storage rack (1.0 ft = 0.3048 m)
Notes: The figure shows an isometric view of a four-tier, five-bay steel storage rack.
Slide 29 shows Example 17.3 – Steel Storage Rack. The illustration shows an isometric view of a four-tier, five-bay steel storage rack. The longitudinal direction of the steel storage rack is made up of five equal 5-foot long bays with the center bay braced with x-bracing on the back side of the steel storage rack only. The transverse direction of the steel storage rack is made up six, four-tier high, 3-foot wide braced frames with x-bracing in each tier. Each tier is 3-foot high.
The general public has direct access to the aisles and merchandise is stored on the upper racks. The rack is supported on a slab on grade. The design operating load for the rack contents is 125 psf on each tier. The weight of the steel support structure is assumed to be 5 psf on each tier.

## Slide 30: Nonbuilding Structures Similar to Buildings
This example uses the ELF procedure to calculate the seismic base shear in the east-west direction for a steel storage rack.
For this example, the design ground motion parameters are as follows:
  SDS = 0.40
  SD1 = 0.18
Notes: Slide 30 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 31: Nonbuilding Structures Similar to Buildings
Risk Category and Importance Factor
  Use ASCE 7-16 Section 1.5.1. The storage rack is in a retail facility.
  Therefore, the storage rack is assigned to Risk Category II.
  According to the exception listed in ASCE 7-16 Section 15.5.3.3.1, Ie = Ip = 1.5 because the rack is in an area open to the general public.
Notes: Slide 31 is a continuation of Example 17.3 – Steel Storage Rack.
In Chapter 17 of FEMA 1051, the requirement for Ie = Ip = 1.5 is shown in Section 15.5.3.5. Supplement 1 to ASCE 7-16 added a second type of storage rack, Steel Cantilever Storage Rack to Section 15.5.3. This addition resulted in the renumbering and combination of some previous sections. The requirement for Ie = Ip = 1.5 is now shown in Section 15.5.3.3.1.

## Slide 32: Nonbuilding Structures Similar to Buildings
Seismic Design Category
  Per ASCE 7-16 Section 11.6 based on Risk Category II, SDS = 0.40, and SD1 = 0.18, the Seismic Design Category (SDC) is C.
Design Coefficients
  According to ASCE 7-16 Table 15.4-1, the R value for this steel storage rack is 4.
Notes: Slide 32 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 33: Nonbuilding Structures Similar to Buildings
Seismic Response Coefficient
  Using RMI Section 2.6.3, from analysis, T = 0.24 seconds.
  For this particular example, the short period spectral value controls the design.
  As shown in the calculations that follow, in the RMI method the importance factor appears in the equation for V rather than in the equation for Cs.
Notes: Slide 33 is a continuation of Example 17.3 – Steel Storage Rack.
ASCE 7-16 Section 15.5.3.1 allows designers some latitude in selecting the seismic design methodology. Designers may use the Rack Manufacturer’s Institute specification (MH16.1-2012) to design steel storage racks as modified by Sections 15.5.3.1.1 and 15.5.3.1.2. In other words, racks designed using the RMI method of Section 15.5.3.1 are deemed to comply as long as the anchorage of the rack complies with Sections 15.5.3..11 and 15.5.3..12. RMI reproduces the seismic ground motion maps from ASCE 7-10. The intent of the ASCE 7-16 is to always use the ground motions defined in ASCE 7-16 Section 11.4 and not the ground motions defined in a reference standard, such as RMI. ASCE 7-16 Section 15.5.3 has been revised to make this point clear. As an alternate, designers may use the requirements of ASCE 7-16 Section 15.5.3.3. The RMI approach will be used in this example.
Please note that FEMA 1051 was created before Supplement 1 to ASCE 7-16 was published. In Chapter 17 of FEMA 1051, some of the references to steel storage rack requirements are no longer correct. Supplement 1 to ASCE 7-16 added a second type of storage rack, Steel Cantilever Storage Rack to Section 15.5.3. This addition resulted in the renumbering and combination of some previous sections.

## Slide 34: Nonbuilding Structures Similar to Buildings
Seismic Response Coefficient
  The seismic response coefficient from RMI is:
  But need not be greater than:
  Nor less than:
Notes: Slide 34 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 35: Nonbuilding Structures Similar to Buildings
Seismic Response Coefficient
  The governing value of Cs = 0.10. From RMI Section 2.6.2, the seismic base shear, V, is calculated as follows:
  RMI requires that two loading conditions be evaluated:
    Condition 1 – Each rack loaded.
    Condition 2 – Only top rack loaded.
Notes: Slide 35 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 36: Nonbuilding Structures Similar to Buildings
Condition 1 – Each Rack Loaded
  Seismic Weight. In accordance with RMI Section 2.6.9, Item 1:
  Design Forces and Moments. Using RMI Section 2.6.2, the design base shear for Condition 1 is calculated as follows: V = CsIpWs = 0.15(42.6 kips) = 6.39 kips
Ws = 4(5)(8 ft)(3 ft)[0.67(125 psf)+5 psf] = 42.6 kips
Notes: Slide 36 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 37: Nonbuilding Structures Similar to Buildings
Seismic forces must be distributed vertically in accordance with RMI Section 2.6.7 as shown in Table 17.3-1.
Resisting moment at base is: MOT, resisting = Ws (1.5 ft) = 42.6(1.5 ft) = 63.9 ft-kips
Table 17.3-1 Seismic Forces, Shears and Overturning Moment |  |  |  |  |  |  | 
Level X | Wx (kips) | hx (ft) | (k = 1) |  | Fx (kips) | Vx (kips) | Mx (ft-kips)
5 | 10.65 | 12 | 127.80 | 0.40 | 2.56 |  | 
 |  |  |  |  |  | 2.56 | 7.68
4 | 10.65 | 9 | 95.85 | 0.30 | 1.92 |  | 
 |  |  |  |  |  | 4.48 | 21.1
3 | 10.65 | 6 | 63.90 | 0.20 | 1.28 |  | 
 |  |  |  |  |  | 5.76 | 38.4
2 | 10.65 | 3 | 31.95 | 0.10 | 0.63 |  | 
 |  |  |  |  |  | 6.39 | 57.6
Σ | 42.6 |  | 319.5 |  |  |  | 
1.0 ft = 0.3048 m, 1.0 kip = 4.45 kN, 1.0 ft-kip = 1.36 kN-m. |  |  |  |  |  |  | 
Notes: Slide 37 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 38: Nonbuilding Structures Similar to Buildings
Condition 2 – Only Top Rack Loaded
  Seismic Weight. In accordance with RMI Section 2.6.9, Item 2:
  Base Shear. Using RMI Section 2.6.2, the design base shear for Condition 2 is calculated as follows: V = CsIpWs = 0.15(17.4 kips) = 2.61 kips
Ws = 1(5)(8 ft)(3 ft)(125 psf) + 4(5)(8 ft)(3 ft)(5 psf) = 17.4 kips
Notes: Slide 38 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 39: Nonbuilding Structures Similar to Buildings
Condition 2 – Only Top Rack Loaded
  Overturning moment at the base. Although the forces could be distributed as shown above for Condition 1, a simpler, conservative approach for Condition 2 is to assume that a seismic force equal to the entire base shear is applied at the top level. MOT = Vb (12 ft) = 2.61 kip (12 ft) = 31.3 ft-kips
  Resisting moment at the base. MOT, resisting = Ws (1.5 ft) = 17.4(1.5 ft) = 26.1 ft-kips
Notes: Slide 39 is a continuation of Example 17.3 – Steel Storage Rack.

## Slide 40: Nonbuilding Structures Similar to Buildings
Controlling Conditions
  Condition 1 controls shear demands at all but the top level. Although the overturning moment is larger under Condition 1, the resisting moment is larger than the overturning moment.
  Under Condition 2 the resistance to overturning is less than the applied overturning moment.
  Therefore, the rack anchors must be designed to resist the uplift induced by the base shear for Condition 2.
Notes: Slide 40 is a continuation of Example 17.3 – Steel Storage Rack.
While RMI is generally viewed as deeming to comply with the ASCE 7-16, ASCE 7-16 Sections 15.5.3.1.1 and 15.5.3.1.2 were added to address deficiencies in RMI with regards to anchorage. Standard Section 15.5.3.1.1 was added to modify RMI Section 7.1.2 to require that the rack’s anchorage to concrete or masonry be based on using design forces determined using load combinations with overstrength provided in ASCE 7-16 Section 12.4.3.2 and to require that the anchorage of the rack to concrete comply with ASCE 7-16 Section 15.4.9. ASCE 7-16 Section 15.5.3.1.2 was added to modify RMI Section 7.1.4 to require that shim stacks be interlocked or welded together in order to transfer shear forces to the foundation and that bending in the anchors associated with the shims or grout be taken into account in the design of the anchors.

## Slide 41: Nonbuilding Structures Similar to Buildings
Torsion
  It should be noted that the distribution of east-west seismic shear will induce torsion in the rack system because the east-west brace is only on the back of the storage rack.
  The torsion should be resisted by the north-south braces at each end of the bay where the east-west braces are placed.
Notes: Slide 41 is a continuation of Example 17.3 – Steel Storage Rack.
  If the torsion were to be distributed to each end of the storage rack, the engineer would be required to calculate the transfer of torsional forces in diaphragm action in the shelving, which may be impractical. Therefore, north-south braces are provided in each bay.

## Slide 42: Nonbuilding Structures Similar to Buildings
Example 17.4 Electric Generating Power Plant
Figure 17-4 Boiler building (1.0 ft = 0.3048 m)
Notes: The first figure shows an view of a braced steel frame supporting a hanging boiler
Slide 42 shows Example 17.4 – Electric Generating Power Plant. The illustration shows two figures. The first figure shows an isometric view of a braced steel frame supporting a hanging boiler. The frame is 230 feet in the north-south direction, 185 feet in the east-west direction, and 240 feet high. The second figure shows a Section A-A through the boiler. The boiler is shown suspended from plate girders attached to the top of the frame. The boiler is shown with additional lateral supports, known as buck stays, along the sides of the boiler.

## Slide 43: Nonbuilding Structures Similar to Buildings
This example highlights some of the differences between the design of nonbuilding structures and the design of building structures.
The boiler building in this example illustrates a solution using the ELF procedure.
Due to mass irregularities, the boiler building would probably also require a modal analysis.
Notes: Slide 43 is a continuation of Example 17.4 – Electric Generating Power Plant.
Large boilers in coal-fired electric power plants generally are suspended from the supporting steel near the roof level. Additional lateral supports (called buck stays) are provided near the bottom of the boiler. The buck stays resist lateral forces but allow the boiler to move vertically. Lateral seismic forces are resisted at the roof and at the buck stay level. Close coordination with the boiler manufacturer is required in order to determine the proper distribution of seismic forces.

## Slide 44: Nonbuilding Structures Similar to Buildings
In this example, a boiler building for a 950 MW coal-fired electric power generating plant is braced laterally with ordinary concentrically braced frames in both the north-south and east-west directions.
The facility is part of a grid and is not for emergency backup of an Risk Category IV facility.
Notes: Slide 44 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 45: Nonbuilding Structures Similar to Buildings
Structural Properties
  The dead load of the structure, equipment and piping, WDL, is 16,700 kips.
  The weight of the boiler in service, WBoiler, is 31,600 kips.
  The natural period of the structure (determined from analysis) is as follows:
    North-South, TNS = 1.90 seconds
    East-West, TEW = 2.60 seconds
Notes: Slide 45 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 46: Nonbuilding Structures Similar to Buildings
Seismic Parameters
  Risk Category (Section 1.5.1) = III
  Importance Factor, Ie (Table 1.5-2) = 1.25
  Short-period Response, SS = 0.864
  One-second Period Response, S1 = 0.261
  Site Class (Standard Sec. 11.4.2) = D
  Design Spectral Acceleration Response Parameters
    SDS = 0.665
    SD1 = 0.327
  Seismic Design Category (Section. 11.6) = D
Notes: Slide 46 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 47: Nonbuilding Structures Similar to Buildings
Seismic Parameters
  Seismic Force-resisting System (Table 15.4-1)
    Ordinary steel concentrically braced frame with unlimited height
  Response Modification Coefficient, R = 1.5
Notes: Slide 47 is a continuation of Example 17.4 – Electric Generating Power Plant.
According to ASCE 7-16 Section 15.4.1(1), either ASCE 7-16 Table 12.2-1 or ASCE 7-16 Table 15.4-1 may be used to determine the seismic parameters, although mixing and matching of values and requirements from the tables is not allowed. If the structure were classified as a “building,” its height would be limited to 35 feet for a Seismic Design Category D ordinary steel concentrically braced frame, according to ASCE 7-16 Table 12.2-1. A review of ASCE 7-16 Table 12.2-1 shows that three steel high ductility braced frame systems (two eccentrically braced systems and the special concentrically braced system) and two special moment frame systems can be used at a height of 240 feet. In most of these cases, the additional requirements of ASCE 7-16 Section 12.2.5.4 must be met to qualify the system at a height of 240 feet. Boiler buildings normally are constructed using ordinary concentrically braced frames.
Chapter 15 of the ASCE 7-16 presents options to increase height limits for design of some nonbuilding structures similar to buildings where R factors are reduced. For this example, an ordinary steel concentrically braced frame with unlimited height is chosen from ASCE 7-16 Table 15.4-1. By using a significantly reduced R value, the seismic design and detailing requirements of AISC 341 need not be applied.

## Slide 48: Nonbuilding Structures Similar to Buildings
Design in the North-South Direction
  Seismic response coefficient. Using ASCE 7-16 Equation 12.8-2:
  From analysis, T = 1.90 seconds. Using ASCE 7-16 Equation 12.8-3, CS does not need to exceed:
Notes: Slide 48 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 49: Nonbuilding Structures Similar to Buildings
Design in the North-South Direction
  Using ASCE 7-16 Equation 12.8-5, Cs must not be less than:
  Cs = 0.044IeSDS ≥ 0.01 = 0.044(1.25)(0.665) = 0.0366
  ASCE 7-16 Equation 12.8-3 controls; Cs = 0.143.
Notes: Slide 49 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 50: Nonbuilding Structures Similar to Buildings
Design in the North-South Direction
  Seismic weight. Calculate the total seismic weight, W, as follows:. W = WDL + WBoiler = 16,700 kips + 31,600 kips = 48,300 kips
  Base shear. Using ASCE 7-16 Equation 12.8-1: V = CsW = 0.143(48,300 kips) = 6,907 kips
Notes: Slide 50 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 51: Nonbuilding Structures Similar to Buildings
Redundancy Factor
  The structure meets the requirements of Condition b specified in ASCE 7-16 Section 12.3.4.2, because two bays of seismic force-resisting perimeter framing are provided in each orthogonal direction.
  Therefore, the redundancy factor, , is 1.0.
Notes: Slide 51 is a continuation of Example 17.4 – Electric Generating Power Plant.
It is important to note that each story resists more than 35 percent of the base shear because the boiler is hung from the top of the structure. Therefore, each story must comply with the requirements of Condition b. If a story resisted less than 35 percent of the base shear, the requirements of ASCE 7-16 Section 12.3.4.2 would not apply and that story would not be considered in establishing the redundancy factor.

## Slide 52: Nonbuilding Structures Similar to Buildings
Vertical Seismic, Ev
  ASCE 7-16 Section 15.1.4 requires that the design vertical response spectral acceleration, Sav, be taken as the peak value from the response spectrum of ASCE 7-16 Section 11.9 for hanging structures and nonbuilding structures incorporating horizontal cantilevers.
  Using ASCE 7-16 Equation 11.9.2-3, the peak vertical response spectral acceleration at the MCER is:
  SaMv = 0.8CvSMS
Notes: Slide 52 is a continuation of Example 17.4 – Electric Generating Power Plant.
ASCE 7-16 Section 11.9 defines the vertical response spectrum at the MCER level. Only ASCE 7-16 Chapter 15 invokes the provisions of Section 11.9. Specifically, ASCE 7-16 Section 15.1.4 requires the use of the provisions of Section 11.9 for tanks, vessels, hanging structures, and nonbuilding structures incorporating horizontal cantilevers.
Because the boiler building of this example contains a hanging boiler, the provisions of ASCE 7-16 Sections 11.9 and 15.1.4 will be applied to determine the vertical seismic load effect, Ev.

## Slide 53: Nonbuilding Structures Similar to Buildings
Vertical Seismic, Ev
  The coefficient Cv is determined from ASCE 7-16 Table 11.9.2-1 and is based on the value of SS and the site class.
  For this example, the value of Cv is 1.23.
  According to ASCE 7-16 Section 11.9.3, the peak design vertical response spectral acceleration, Sav, is taken as two-thirds of SaMv and is determined as follows: Sav = (2/3)SMS(0.8)(1.23) = 0.665(0.8)(1.23) = 0.654
Notes: Slide 53 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 54: Nonbuilding Structures Similar to Buildings
Design in the East-West Direction
  Seismic response coefficient. Using ASCE 7-16 Equation 12.8-2:
  From analysis, T = 2.60 seconds. Using ASCE 7-16 Equation 12.8-3, Cs does not need to exceed:
Notes: Slide 54 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 55: Nonbuilding Structures Similar to Buildings
Design in the East-West Direction
  Using Standard Equation 12.8-5, Cs must not be less than: Cs = 0.044IeSDS ≥ 0.01 = 0.044(1.25)(0.665) = 0.0366
  ASCE 7-16 Equation 12.8-3 controls; Cs = 0.105.
Notes: Slide 55 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 56: Nonbuilding Structures Similar to Buildings
Design in the East-West Direction
  Seismic weight. Calculate the total seismic weight, W, as follows:
W = WDL + WBoiler = 16,700 kips + 31,600 kips = 48,300 kips
  Base shear. Using ASCE 7-16 Equation 12.8-1:
V = CsW = 0.105(48,300 kips) = 5072 kips
Notes: Slide 56 is a continuation of Example 17.4 – Electric Generating Power Plant.

## Slide 57: Nonbuilding Structures Similar to Buildings
Example 17.5 Pier/Wharf Design
Figure 17-5 Pier plan and elevation (1.0 ft = 0.3048 m)
Notes: The figure shows plan and elevation views of a pier showing two rows of four piles each running in the north-south direction.
Slide 57 shows Example 17.5 – Pier/Wharf Design. The illustration shows two figures. The top figure is a plan view of the pier showing two rows of four piles each running in the north-south direction. The two rows of piles are spaced 15 feet apart in the east-west direction with a 3-foot overhang for the pier slab. Beams run between piles in the east-west direction forming moment frames. In the north-south direction, the left end of the pier is tied to an abutment structure supported on grade. The lower figure is an elevation view of the pier. The figure shows the piles extending 30 feet below the sea floor. The piles extend 30 feet above the see floor, which includes 20 feet below mean sea level and 10 feet above mean sea level. The figure shows the spacing of the piles in the north-south direction to be 10 feet with a 3-foot overhang for the pier slab.

## Slide 58: Nonbuilding Structures Similar to Buildings
This example illustrates the calculation of the seismic base shear in the east-west direction for the pier using the ELF procedure. Piers and wharves are covered in ASCE 7-16 Section 15.5.6.
A cruise ship company is developing a pier in Long Beach, California, to service ocean liners.
The pier will be accessible by the general public.
Notes: Slide 58 is a continuation of Example 17.5 – Pier/Wharf Design.

## Slide 59: Nonbuilding Structures Similar to Buildings
The pier contains a large warehouse owned by the cruise ship company.
In the north-south direction, the pier is tied directly to an abutment structure supported on grade.
In the east-west direction, the pier resists seismic forces using moment frames.
The design live load for warehouse storage is 1,000 psf..
Notes: Slide 59 is a continuation of Example 17.5 – Pier/Wharf Design.

## Slide 60: Nonbuilding Structures Similar to Buildings
Seismic Parameters
  Risk Category (Section 1.5.1) = II
  Importance Factor, Ie (Table 1.5-2) = 1.0
  Site Class (ASCE 7-16 Section 11.4.2) = D
  Design Spectral Acceleration Response Parameters
    SDS = 1.167
    SD1 = 0.60
  Seismic Design Category (Section. 11.6) = D
Notes: Slide 60 is a continuation of Example 17.5 – Pier/Wharf Design.

## Slide 61: Nonbuilding Structures Similar to Buildings
Seismic Parameters
  Seismic Force-resisting System (Table 15.4-1)
    Intermediate concrete moment frame with permitted height increase
  Response Modification Coefficient, R = 3
Notes: Slide 61 is a continuation of Example 17.5 – Pier/Wharf Design.
If the structure was classified as a building, an intermediate reinforced concrete moment frame would not be permitted in Seismic Design Category D.
According to ASCE 7-16 Section 15.4.1(1), either ASCE 7-16 Table 12.2-1 or ASCE 7-16 Table 15.4-1 may be used to determine the seismic parameters, although mixing and matching of values and requirements from the tables is not allowed. If the structure were classified as a “building,” its height would be limited to 35 feet for a Seismic Design Category D ordinary steel concentrically braced frame, according to ASCE 7-16 Table 12.2-1. A review of ASCE 7-16 Table 12.2-1 shows that three steel high ductility braced frame systems (two eccentrically braced systems and the special concentrically braced system) and two special moment frame systems can be used at a height of 240 feet. In most of these cases, the additional requirements of ASCE 7-16 Section 12.2.5.4 must be met to qualify the system at a height of 240 feet. Boiler buildings normally are constructed using ordinary concentrically braced frames.
Chapter 15 of the ASCE 7-16 presents options to increase height limits for design of some nonbuilding structures similar to buildings where R factors are reduced. For this example, an ordinary steel concentrically braced frame with unlimited height is chosen from ASCE 7-16 Table 15.4-1. By using a significantly reduced R value, the seismic design and detailing requirements of AISC 341 need not be applied.

## Slide 62: Nonbuilding Structures Similar to Buildings
Seismic response coefficient. Using ASCE 7-16 Equation 12.8-2:
From analysis, T = 0.596 seconds. Using ASCE 7-16 Equation 12.8-3, Cs does not need to exceed:
Notes: Slide 62 is a continuation of Example 17.5 – Pier/Wharf Design.

## Slide 63: Nonbuilding Structures Similar to Buildings
Using ASCE 7-16 Equation 12.8-5, Cs must not be less than:
  Cs = 0.044IeSDS ≥ 0.01 = 0.044(1.0)(1.167) = 0.0513
ASCE 7-16 Equation 12.8-3 controls; Cs = 0.336.
Notes: Slide 63 is a continuation of Example 17.5 – Pier/Wharf Design.

## Slide 64: Nonbuilding Structures Similar to Buildings
Seismic weight. In accordance with ASCE 7-16 Section 12.7.2, calculate the dead load due to the deck, beams and support piers, as follows: WDeck = 1.0(43 ft)(21 ft)(0.150 kip/ft3) = 135.5 kips WBeam = 4(2 ft)(2 ft)(21 ft)(0.150 kip/ft3) = 50.4 kips WPier = 8[π(1.25 ft)2][(10 ft - 3 ft) + (20 ft)/2](0.150 kip/ft3) = 100.1 kips WDL = WDeck + WBeams + WPiers = 135.5 + 50.4 + 100.1 = 286.0 kips
Notes: Slide 64 is a continuation of Example 17.5 – Pier/Wharf Design.

## Slide 65: Nonbuilding Structures Similar to Buildings
Calculate 25 percent of the storage live load, as follows: W1/4 LL = 0.25(1,000 psf)(43 ft)(21 ft) = 225.8 kips
A “virtual” mass of water equal to a column of water of identical dimensions of the circular pile is to be considered in the effective seismic mass. This additional weight is calculated as follows: WVirtual Mass = 8[π(1.25 ft)2][(20 ft)/2](64 pcf) = 25.1 kips
Therefore, the total seismic weight is: W = WDL + W1/4LL + WVirtual Mass = 286.0 + 225.8 + 25.1 = 536.9 kips
Notes: Slide 65 is a continuation of Example 17.5 – Pier/Wharf Design.
ASCE 7-16 Section 15.5.6.2 requires that all applicable marine loading combinations be considered (such as those for mooring, berthing, wave and current on piers and wharves). For this example, additional seismic loads from water flowing around the piles will be considered. A “virtual” mass (Jacobsen, 1959) of water equal to a column of water of identical dimensions of the circular pile is to be considered in the effective seismic mass.
Additional seismic forces from the water due to wave action may also act on the piles. These additional forces are highly dependent on the acceleration and velocity of the waves and are heavily dependent on the geometry of the body of water. These forces can be calculated using the Morison Equation (Morison, 1950). The determination of these forces is beyond the scope of this example.

## Slide 66: Nonbuilding Structures Similar to Buildings
Base shear. Using Standard Equation 12.8-1:
V = CsW = 0.336(536.9 kips) = 180.4 kips
Redundancy factor. The pier in this example has a sufficient number of moment frames that loss of moment resistance at both ends of a single beam would not result in more than a 33 percent reduction in story strength.
Notes: Slide 66 is a continuation of Example 17.5 – Pier/Wharf Design.
ASCE 7-16 Section 15.5.6.2 requires that all applicable marine loading combinations be considered (such as those for mooring, berthing, wave and current on piers and wharves). For this example, additional seismic loads from water flowing around the piles will be considered. A “virtual” mass (Jacobsen, 1959) of water equal to a column of water of identical dimensions of the circular pile is to be considered in the effective seismic mass.
Additional seismic forces from the water due to wave action may also act on the piles. These additional forces are highly dependent on the acceleration and velocity of the waves and are heavily dependent on the geometry of the body of water. These forces can be calculated using the Morison Equation (Morison, 1950). The determination of these forces is beyond the scope of this example.

## Slide 67: Nonbuilding Structures Similar to Buildings
However, the direct tie to a much stiffer abutment at the north end likely would cause an extreme torsional irregularity for east-west motion, so that Condition (a) would not be met.
Condition (b) is not met because two bays of seismic force-resisting perimeter framing are not provided in each orthogonal direction.
Therefore, the redundancy factor, , is taken to be 1.3.
Notes: Slide 67 is a continuation of Example 17.5 – Pier/Wharf Design.
ASCE 7-16 Section 15.5.6.2 requires that all applicable marine loading combinations be considered (such as those for mooring, berthing, wave and current on piers and wharves). For this example, additional seismic loads from water flowing around the piles will be considered. A “virtual” mass (Jacobsen, 1959) of water equal to a column of water of identical dimensions of the circular pile is to be considered in the effective seismic mass.
Additional seismic forces from the water due to wave action may also act on the piles. These additional forces are highly dependent on the acceleration and velocity of the waves and are heavily dependent on the geometry of the body of water. These forces can be calculated using the Morison Equation (Morison, 1950). The determination of these forces is beyond the scope of this example.

## Slide 68: Nonbuilding Structures Not Similar to Buildings
Example 17.6.1 Flat-Bottom Water Storage Tank
Figure 17-6 Storage tank section (1.0 ft = 0.3048 m)
Notes: The figure shows an elevation view of a fire water storage tank.
Slide 68 shows Example 17.6.1 – Flat-Bottom Water Storage Tank. The illustration shows an elevation view of a fire water storage tank. The diameter of the tank is 20 feet and the height of the tank is 15 feet. The liquid level is shown as 10 feet with a freeboard of 5 feet. A graphical representation of a seismic sloshing is shown with a wave height above the liquid level of ds.
The seismic response of tanks and vessels can be significantly different from that of buildings. For a structure composed of interconnected solid elements, it is not difficult to recognize how ground motions accelerate the structure and cause inertial forces within the structure. Tanks and vessels, where empty, respond in a similar manner.
Where there is liquid in the tank, the response is much more complicated. As earthquake ground motions accelerate the tank shell, the shell applies lateral forces to the liquid. The response of the liquid to those lateral forces may be amplified significantly if the period content of the earthquake ground motion is similar to the natural sloshing period of the liquid.
Earthquake-induced impulsive fluid forces are those calculated assuming that the liquid is a solid mass. Convective fluid forces are those that result from sloshing in the tank. It is important to account for convective forces on columns and appurtenances inside the tank, because they are affected by sloshing in the same way that waves affect a pier in the ocean.
Freeboard considerations are critical. Oftentimes, the roof acts as a structural diaphragm. If a tank does not have sufficient freeboard, the sloshing wave can rip the roof from the wall of the tank. This could result in failure of the wall and loss of the liquid within.
Seismic design for liquid-containing tanks and vessels is complicated. The fluid mass that is effective for impulsive and convective seismic forces is discussed in AWWA D100 and API 650.

## Slide 69: Nonbuilding Structures Not Similar to Buildings
This example illustrates the calculation of the design base shear and the required freeboard using the procedure outlined in AWWA D100 for a steel water storage tank used to store potable water for fire protection within a chemical plant (Figure 17-6).
According to ASCE 7-16 Section 15.7.7.1, the governing reference document for this tank is AWWA D100.
Notes: Slide 69 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.
ASCE 7-16 has added two exceptions to the use of AWWA D100. The exceptions require that the seismic ground motion values be determined according to ASCE 7-16 Section 11.4 and that the seismic freeboard meet the requirements of ASCE 7-16. AWWA D100 is written in terms of allowable stress design (ASD) while the seismic requirements of the Standard are written in terms of strength design. AWWA D100 translates the force equations from the ASCE 7-16 by substituting 1.4R for R. For the purposes of this example, all loads are calculated in terms of strength design. Where appropriate, AWWA D100 equations are referenced for the determination of impulsive and convective (sloshing) masses.

## Slide 70: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Risk Category (Section 1.5.1) = IV
  Importance Factor, Ie (Table 1.5-2) = 1.5
  Long-period Transition Period, TL = 6 sec.
  Site Class (ASCE 7-16 Section 11.4.2) = C
  Design Spectral Acceleration Response Parameters
    SDS = 0.824
    SD1 = 0.376
Notes: Slide 70 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.

## Slide 71: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Seismic Force-resisting System (Table 15.4-2)
    Flat-bottom, ground-supported, mechanically anchored steel tank
  Response Modification Coefficient, R = 3
Notes: Slide 71 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.

## Slide 72: Nonbuilding Structures Not Similar to Buildings
Spectral acceleration. Based on AWWA D100 Section 13.5.1, the impulsive acceleration is set equal to SDS. Sai = SDS = 0.824
Seismic (impulsive) weight. Wtank = 15.4 kips
Wiwater = π(10 ft)2(10 ft)(0.0624 kip/ft3) (Wi/WT) = 196.0 (0.542) kips = 106.2 kips
Notes: Slide 72 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.
AWWA D100 Section 13.5.1 does not require the computation of the natural period for the first mode of vibration. The impulsive acceleration is assumed to be equal to SDS.

## Slide 73: Nonbuilding Structures Not Similar to Buildings
The ratio Wi/WT (= 0.542) was determined from Equation 13-24 (only valid for D/H ≥ 1.333) of AWWA D100 for a diameter-to-liquid height ratio of 2.0 as shown below:
Wi = Wtank + Wiwater = 15.4 + 106.2 = 121.6 kips
Notes: Slide 73 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.

## Slide 74: Nonbuilding Structures Not Similar to Buildings
Base Shear. According to ASCE 7-16 Equation 15.7-5:
Notes: Slide 74 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.

## Slide 75: Nonbuilding Structures Not Similar to Buildings
Convective Response
Natural period for the first mode of sloshing. Using ASCE 7-16 Equation 15.7-12:
Notes: Slide 75 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.

## Slide 76: Nonbuilding Structures Not Similar to Buildings
Spectral acceleration. Using ASCE 7-16 Equation 15.7-10 with Tc < TL = 6 seconds:
Seismic (convective) weight. Wc = Wwater (Wc/WT) = 196 (0.437) = 85.7 kips
Notes: Slide 76 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.

## Slide 77: Nonbuilding Structures Not Similar to Buildings
The ratio Wc/WT (= 0.437) was determined from Equation 13-26 (valid for all D/H) of AWWA D100 for a diameter-to-liquid height ratio of 2.0 as shown below:
Base shear. According to ASCE 7-16 Equation 15.7-6:
Notes: Slide 77 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.
Item b of Standard Section 15.7.2 indicates that impulsive and convective components may, in general, be combined using the SRSS method. ASCE 7-16 Equation 15.7-4 requires that the direct sum be used for ground-supported storage tanks for liquids. Note b under ASCE 7-16 Section 15.7.6.1 allows the use of the SRSS method in lieu of using ASCE 7-16 Equation 15.7-4.

## Slide 78: Nonbuilding Structures Not Similar to Buildings
Minimum Freeboard δs = 0.42DiIeSac = 0.42(20 ft)(1.0)(0.212) = 1.78 ft
Notes: Slide 78 is a continuation of Example 17.6.1 – Flat-Bottom Water Storage Tank.
Because the tank is assigned to Risk Category IV, the full value of the theoretical wave height must be provided for freeboard. For the case of Risk Category IV tanks, the wave height is calculated based on the convective acceleration using the actual value of TL and an importance factor of 1.0. ASCE 7-16 Table 15.7-3 indicates that a minimum freeboard equal to δs is required for this tank. Using ASCE 7-16 Equation 15.7-13 and Note (c) (sets Ie = 1.0 for Risk Category IV for wave height determination) from ASCE 7-16 Section 15.7.6.1, the seismic freeboard is determined.
The 5 feet of freeboard provided is adequate. Please note that AWWA D100 has not been updated to reflect Standard Equation 15.7-13. Under the AWWA D100 rules, the required freeboard is determined as follows:
δs = 0.5DiIeSac = 0.5(20 ft)(1.0)(0.212) = 2.12 ft
ASCE 7-16 Table 15.7-3, Section 15.7.6.1, and Section 15.7.6.1.2 have been reorganized for increased clarity. No technical changes have occurred relative to the discussions above. Note (c) referenced above has become subsection (b) and placed in Section 15.7.6.1.2.

## Slide 79: Nonbuilding Structures Not Similar to Buildings
Example 17.6.2 Flat-Bottom Gasoline Tank
Figure 17-7 Storage tank section (1.0 ft = 0.3048 m)
Notes: The figure shows an elevation view of a steel gasoline storage tank.
Slide 79 shows Example 17.6.2 – Flat-Bottom Gasoline Tank. The illustration shows an elevation view of a steel gasoline storage tank. The diameter of the tank is 120 feet and the height of the tank is 40 feet. The high liquid level is shown as 33 feet and the low liquid level is shown as 3 feet. The tank is shown with a cone roof supported by a 20 inch diameter Schedule 10 pipe center column and (54) W14x26 rafters. The cone roof is sloped up to the center of the tank by 3’-9 5/16. The tank is equipped with an aluminum internal floating roof with a high rest position of 6 feet and a low rest position of 3 feet. The steel bottom of the tank is ¼-inch thick and sloped up to the center of the tank by 6 inches. The tank shell is shown with five shell rings. Ring 1 is 0.401 inches thick and rings 2 through 5 are 5/16 inches thick.
The seismic response of tanks and vessels can be significantly different from that of buildings. For a structure composed of interconnected solid elements, it is not difficult to recognize how ground motions accelerate the structure and cause inertial forces within the structure. Tanks and vessels, where empty, respond in a similar manner.
Where there is liquid in the tank, the response is much more complicated. As earthquake ground motions accelerate the tank shell, the shell applies lateral forces to the liquid. The response of the liquid to those lateral forces may be amplified significantly if the period content of the earthquake ground motion is similar to the natural sloshing period of the liquid.
Earthquake-induced impulsive fluid forces are those calculated assuming that the liquid is a solid mass. Convective fluid forces are those that result from sloshing in the tank. It is important to account for convective forces on columns and appurtenances inside the tank, because they are affected by sloshing in the same way that waves affect a pier in the ocean.
Freeboard considerations are critical. Oftentimes, the roof acts as a structural diaphragm. If a tank does not have sufficient freeboard, the sloshing wave can rip the roof from the wall of the tank. This could result in failure of the wall and loss of the liquid within.
Seismic design for liquid-containing tanks and vessels is complicated. The fluid mass that is effective for impulsive and convective seismic forces is discussed in AWWA D100 and API 650.

## Slide 80: Nonbuilding Structures Not Similar to Buildings
This example illustrates the calculation of the base shear and the required freeboard using the procedure outlined in API 650 for a petrochemical storage tank in a refinery tank farm (Figure 17-7).
The vertical design response spectral acceleration, Sav, for use in the determination of shell hoop stress will also be calculated according to the provisions of ASCE 7-16 Sections 11.9 and 15.1.4.
An impoundment dike is not provided to control liquid spills.
According to Standard Section 15.7.8.1, the governing reference document for this tank is API 650.
Notes: Slide 80 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
API 650 is written in terms of allowable stress design (ASD) while the seismic requirements of the ASCE 7-16 are written in terms of strength design. API 650 translates the force equations from the ASCE 7-16 by substituting Rw for R, where Rw is equal to 1.4R. For the purposes of this example, all loads are calculated in terms of strength design. Where appropriate, API 650 equations are referenced for the determination of impulsive and convective (sloshing) masses.

## Slide 81: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Risk Category (Section 1.5.1) = III (The tank is used for storage of toxic or explosive material based on an LC(50) value of 5.2 mg per liter taken from a typical MSDS for gasoline.)
  Importance Factor, Ie (Table 1.5-2) = 1.25
  Short-period Response, SS = 1.236
  One-second Period Response, S1 = 0.406
  Long-period Transition Period, TL = 6 sec.
  Site Class = C
Notes: Slide 81 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 82: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Design Spectral Acceleration Response Parameters
    SDS = 0.824
    SD1 = 0.376
  Seismic Force-resisting System (Table 15.4-2)
    Flat-bottom, ground-supported, self-anchored steel tank
  Response Modification Coefficient, R = 2.5
Notes: Slide 82 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 83: Nonbuilding Structures Not Similar to Buildings
Based on ASCE 7-16 Section 15.7.6 Note a, the impulsive acceleration is set equal to SDS. Sai = SDS = 0.824
Seismic (impulsive) weight. Wtank = 490.0 kips
WGas = π(60 ft)2(33 ft)(0.0474 kip/ft3)(Wi/Wp) = 17,691 kips (0.316) = 5,590 kips
Notes: Slide 83 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
API 650 Section E.4.5.1 does not require the computation of the natural period for the first mode of vibration. The impulsive acceleration is assumed to be equal to SDS.

## Slide 84: Nonbuilding Structures Not Similar to Buildings
The ratio Wi/WT (= 0.316) was determined from Equation E.6.1.1-1 (only valid for D/H ≥ 1.333) of API 650 for a diameter-to-liquid height ratio of 3.636 as shown below:
Wi = Wtank + Wiwater = 490 + 5590 = 6,080 kips
Notes: Slide 84 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 85: Nonbuilding Structures Not Similar to Buildings
Base Shear. According to ASCE 7-16 Equation 15.7-5:
Notes: Slide 85 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 86: Nonbuilding Structures Not Similar to Buildings
Convective Response
Natural period for the first mode of sloshing. Using ASCE 7-16 Equation 15.7-12:
Notes: Slide 86 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 87: Nonbuilding Structures Not Similar to Buildings
Spectral acceleration. Using ASCE 7-16 Equation 15.7-11 with Tc > TL = 6 seconds:
Seismic (convective) weight. Wc = WGAS (Wc/Wp) = 17,691 (0.640) = 11,322 kips
Notes: Slide 87 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 88: Nonbuilding Structures Not Similar to Buildings
The ratio Wc/Wp (= 0.640) was determined from Equation E.6.1.1-3 (valid for all D/H) of API 650 for a diameter-to-liquid height ratio of 3.636 as shown below:
Base shear. According to ASCE 7-16 Equation 15.7-6:
Notes: Slide 88 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
Item b of Standard Section 15.7.2 indicates that impulsive and convective components may, in general, be combined using the SRSS method. ASCE 7-16 Equation 15.7-4 requires that the direct sum be used for ground-supported storage tanks for liquids. Note b under ASCE 7-16 Section 15.7.6.1 allows the use of the SRSS method in lieu of using ASCE 7-16 Equation 15.7-4.

## Slide 89: Nonbuilding Structures Not Similar to Buildings
Minimum Freeboard δs = 0.42DiISac = 0.42(120 ft)(1.25)(0.0433) = 2.73 ft Required freeboard = 0.7 δs = 1.91 ft
Notes: Slide 89 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
Because the tank is assigned to Risk Category III and SDS is greater than 0.50, the freeboard provided must be at least 70 percent of the full value of the theoretical wave height (based on TL = 4 s). For the case of Risk Category III tanks, the wave height is calculated based on the convective acceleration using a value of TL equal to 4 seconds and an importance factor of 1.25 according to ASCE 7-16 Section 15.7.6.1, Note (d). ASCE 7-16 Table 15.7-3 indicates that a minimum freeboard equal to 0.7δs is required for this tank. Using ASCE 7-16 Equation 15.7-13 and Note (d) (sets Ie = 1.25 and TL to 4 seconds for Risk Category III for wave height determination) from Standard Section 15.7.6.1:
The 7 feet of freeboard provided also includes a 3-foot allowance for an aluminum internal floating roof and the roof framing. The seismic freeboard must be sufficient to avoid forcing the floating roof into the fixed roof framing. The freeboard provided is adequate. The reduced freeboard requirement recognizes that providing seismic freeboard for Risk Category I, II, or III tanks is an economic decision (reducing damage) and not a life-safety issue. Because of this, a reduced freeboard is allowed. If secondary containment were provided, no freeboard would be required based on ASCE 7-16 Table 15.7-3, Footnote (b).
ASCE 7-16 Table 15.7-3, Section 15.7.6.1, and Section 15.7.6.1.2 have been reorganized for increased clarity. No technical changes have occurred relative to the discussions above. Note (d) referenced above has become subsection (c) and placed in Section 15.7.6.1.2. Footnote (b) of ASCE 7-16 Table 15.7.3 has been moved to ASCE 7-16 Section 15.7.6.1.2 (d)(3).

## Slide 90: Nonbuilding Structures Not Similar to Buildings
Vertical Seismic, Ev
  ASCE 7-16 Section 15.1.4 requires that the design vertical response spectral acceleration, Sav, used to determine hydrodynamic hoop forces in cylindrical tanks be determined using the requirements of ASCE 7-16 Section 15.7.2c(2).
  Natural vertical period. Using ASCE 7-16 Equation C15.7-2:
Notes: Slide 90 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
ASCE 7-16 Section 11.9 defines the vertical response spectrum at the MCER level. Only ASCE 7-16 Chapter 15 invokes the provisions of Section 11.9. Specifically, ASCE 7-16 Section 15.1.4 requires the use of the provisions of Section 11.9 for tanks, vessels, hanging structures, and nonbuilding structures incorporating horizontal cantilevers.

## Slide 91: Nonbuilding Structures Not Similar to Buildings
Vertical Seismic, Ev
  Using ASCE 7-16 Equation 11.9.2-4 for the natural vertical period Tv = 0.182 s, the vertical response spectral acceleration at the MCER is:
  Cv = 1.15
Notes: Slide 91 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
The coefficient Cv is determined from ASCE 7-16 Table 11.9.2-1 and is based on the value of SS and the site class. According to ASCE 7-16 Section 11.9.3, the design vertical response spectral acceleration, Sav, is taken as two-thirds of SaMv.

## Slide 92: Nonbuilding Structures Not Similar to Buildings
Example 17.7 Vertical Vessel
Figure 17-7 Vertical vessel (1.0 ft = 0.3048 m)
Notes: The figure shows an elevation view of a vertical pressure vessel with a cylindrical shell 10 feet in diameter with two hemispherical heads.
Slide 92 shows Example 17.7 – Vertical Vessel. The illustration shows an elevation view of a vertical pressure vessel with a cylindrical shell 10 feet in diameter with two hemispherical heads. The vessel is supported on by a 3/8 inch thick support skirt. The overall height of the vessel above grade is 100 feet.

## Slide 93: Nonbuilding Structures Not Similar to Buildings
This example illustrates the calculation of the base shear using the ELF procedure for a flexible vertical vessel (Figure 17-8). The vertical vessel contains highly toxic material (Risk Category IV).
The weight of the vertical vessel plus contents is 300,000 pounds.
Notes: Slide 93 is a continuation of Example 17.7 – Vertical Vessel.
Large boilers in coal-fired electric power plants generally are suspended from the supporting steel near the roof level. Additional lateral supports (called buck stays) are provided near the bottom of the boiler. The buck stays resist lateral forces but allow the boiler to move vertically. Lateral seismic forces are resisted at the roof and at the buck stay level. Close coordination with the boiler manufacturer is required in order to determine the proper distribution of seismic forces.

## Slide 94: Nonbuilding Structures Not Similar to Buildings
ASCE 7-16 Section 15.4.4 allows the fundamental period of a nonbuilding structure to be determined using a properly substantiated analysis.
The period of the vertical vessel is calculated using the equation for a uniform vertical cylindrical steel vessel as found in Appendix 4.A of ASCE (2011).
where: T = period (s)
W = weight (lb/ft)
H = height (ft)
D = diameter (ft)
T = shell thickness (in.)
Notes: Slide 94 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 95: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Risk Category (Section 1.5.1) = IV (Highly toxic material)
  Importance Factor, Ie (Table 1.5-2) = 1.5
  Site Class (Standard Sec. 11.4.2) = D
  Design Spectral Acceleration Response Parameters
    SDS = 1.86
    SD1 = 0.79
Notes: Slide 95 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 96: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Seismic Force-resisting System (Table 15.4-2)
    Elevated tanks, vessels, bins, or hoppers: Single pedestal or skirt supported – welded steel with special detailing.
  Response Modification Coefficient, R = 3
Notes: Slide 96 is a continuation of Example 17.7 – Vertical Vessel.
The vertical vessel used in this example is a skirt-supported distributed mass cantilevered structure. There are three possible entries in ASCE 7-16 Table 15.4-2 that describe the vessel in question:
Elevated tanks, vessels, bins, or hoppers: Single pedestal or skirt supported – welded steel.
Elevated tanks, vessels, bins, or hoppers: Single pedestal or skirt supported – welded steel with special detailing.
All other steel and reinforced concrete distributed mass cantilever structures not covered herein including stacks, chimneys, silos and skirt-supported vertical vessels that are not similar to buildings.
All three options are keyed to the detailing requirements of Standard Section 15.7.10. Two of the options specifically require that Items (a) and (b) of ASCE 7-16 Section 15.7.10 be met. The intent of ASCE 7-16 Section 15.7.10 and ASCE 7-16 Table 15.4-2 is that skirt-supported vessels be checked for seismic loads based on R/Ie = 1.0 if the structure is assigned to Risk Category IV or if an R factor of 3.0 is used in the design of the vessel. Skirt-supported vessels fail in buckling, which is not a ductile failure mode, so a more conservative design approach is required. The R/Ie = 1.0 check typically will govern the design of the skirt over using loads determined with an R factor of 3 in a moderate to high area of seismic activity. The only benefit of using an R factor of 3 in this case is in the design of the foundation. The foundation is not required to be designed for the R/Ie = 1.0 load. For the R/Ie = 1.0 load, the skirt can be designed based on critical buckling (factor of safety of 1.0). The critical buckling strength of a skirt can be determined using a number of published sources. The two most common methods for determining the critical buckling strength of a skirt are ASME BVPC Section VIII, Division 2, Paragraph 4.4 using a factor of safety of 1.0 and AWWA D100 Section 13.4.3.4. An example of calculating the critical buckling strength of the skirt using ASME BVPC Section VIII, Division 2, Paragraph 4.4 is provided.

## Slide 97: Nonbuilding Structures Not Similar to Buildings
Seismic response coefficient. Using ASCE 7-16 Equation 12.8-2:
From analysis, T = 0.762 seconds. Using ASCE 7-16 Equation 12.8-3, CS does not need to exceed:
Notes: Slide 97 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 98: Nonbuilding Structures Not Similar to Buildings
Using ASCE 7-16 Equation 12.8-5, Cs must not be less than:
  Cs = 0.044IeSDS ≥ 0.03 = 0.044(1.5)(1.86) = 0.123
ASCE 7-16 Equation 12.8-3 controls; Cs = 0.518.
Base shear. Using Standard Equation 12.8-1:
  V = CsW = 0.518(300 kips) = 155.4 kips
Notes: Slide 98 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 99: Nonbuilding Structures Not Similar to Buildings
Design in the North-South Direction
  Seismic weight. Calculate the total seismic weight, W, as follows:. W = WDL + WBoiler = 16,700 kips + 31,600 kips = 48,300 kips
  Base shear. Using ASCE 7-16 Equation 12.8-1: V = CsW = 0.143(48,300 kips) = 6,907 kips
Notes: Slide 99 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 100: Nonbuilding Structures Not Similar to Buildings
Figure 17-9 Vertical distribution of seismic forces
Notes: The figure shows the vertical distribution of seismic forces on a vertical vessel of height H for the period of the vessel ranging between 0.5 and 2.5 seconds.
Slide 100 is a continuation of Example 17.7 – Vertical Vessel. The illustration shows three figures. The figure on the left shows the vertical distribution of seismic forces on a vertical vessel of height H if the period of the vessel is 0.5 s or less. The distribution is an inverted triangle (k = 1). The centroid of the seismic forces is shown as 2/3H. The figure in the center shows the vertical distribution of seismic forces on a vertical vessel of height H if the period of the vessel falls between 0.5 s and 2.5 s. The distribution is an inverted curve (k between 1 and 2). The centroid of the seismic forces is shown as [(k+1)/(k+2)]H. The figure on the right shows the vertical distribution of seismic forces on a vertical vessel of height H if the period of the vessel is 2.5 s or greater. The distribution is an inverted parabola (k = 2). The centroid of the seismic forces is shown as 3/4H.
ASCE 7-16 Section 12.8.3 defines the vertical distribution of seismic forces in terms of an exponent, k, related to structural period. If the structural period is less than or equal to 0.5 second, k = 1 and results in an inverted triangular distribution of forces. If the structural period is greater than or equal to 2.5 seconds, k = 2 and results in a parabolic distribution of forces. For periods between 0.5 second and 2.5 seconds, the value of k is determined by linear interpolation between 1 and 2. The significance of the distribution requirements of ASCE 7-16 Section 12.8.3 is that the height of the centroid to the horizontal seismic force increases (thus increasing the overturning moment) as the period increases above 0.5 second (Figure 17-9).

## Slide 101: Nonbuilding Structures Not Similar to Buildings
Referring to Figure 17-9
  Once k is determined, the height to the centroid, , of the horizontal seismic force is equal to:
  For the vessel period of T = 0.762 second:
Notes: Slide 101 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 102: Nonbuilding Structures Not Similar to Buildings
Referring to Figure 17-9
  The value of is then calculated as:
  The overturning moment is then calculated as: M = = 155.4(68.1) = 10,583 ft-kips
Notes: Slide 102 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 103: Nonbuilding Structures Not Similar to Buildings
Critical Buckling Check
  Seismic response coefficient with R/Ie = 1.0. Using ASCE 7-16 Equation 12.8-2:
  Using ASCE 7-16 Equation 12.8-3, Cs does not need to exceed:
  ASCE 7-16 Equation 12.8-3 controls; Cs = 1.037
Notes: Slide 103 is a continuation of Example 17.7 – Vertical Vessel.
The intent of ASCE 7-16 Section 15.7.10 and ASCE 7-16 Table 15.4-2 is that skirt-supported vessels be checked for seismic loads based on R/Ie = 1.0 (critical buckling check) if the structure is assigned to Risk Category IV or if an R factor of 3.0 is used in the design of the vessel. For the R/Ie = 1.0 load, the skirt can be designed based on critical buckling (factor of safety of 1.0). The critical buckling strength of a skirt can be determined using a number of published sources. In this example, the method described in ASME BVPC Section VIII, Division 2, Paragraph 4.4 using a factor of safety of 1.0 will be used.

## Slide 104: Nonbuilding Structures Not Similar to Buildings
Base shear. Using ASCE 7-16 Equation 12.8-1: V = CsW = 1.037(300 kips) = 311.0 kips
Vertical distribution of seismic forces. Moment arm from Figure 17-9:
The overturning moment is then calculated as: M = = 311.0(68.1) = 21,181 ft-kips
Notes: Slide 104 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 105: Nonbuilding Structures Not Similar to Buildings
Stresses at base of skirt.
  Axial stress (fa) = P/A = 300,000/(π(10)12(0.375)) = 2,122 psi
  Bending stress (fb) = M/S = 21,181(1,000)12/[(0.375)π(10(12))2/4] = 59,930 psi
  Shear stress (fv) = 2V/A = 2(311.0)(1,000) /(π(10)12(0.375)) = 4,400 psi
Notes: Slide 105 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 106: Nonbuilding Structures Not Similar to Buildings
Evaluation of combined axial stress, bending stress, and shear stress.
  Uniform Axial Compression (governed by column buckling):
    Allowable longitudinal stress = Fca = 23,081 psi
  Axial compression due to bending moment:
    Allowable bending stress = Fba = Fxc = 25,770 psi
Notes: Slide 106 is a continuation of Example 17.7 – Vertical Vessel.
The procedures outlined in ASME BVPC Section VIII, Division 2, Paragraph 4.4 using a factor of safety of 1.0 will be used below to determine the adequacy of the vessel support skirt under seismic loads based on R/Ie = 1.0. The ASME procedures check many different limit states to arrive at the allowable stress for a particular loading. The example below only identifies the governing conditions for this particular vessel. Please note that all “allowable” stresses shown below are based on a factor of safety of 1.0. Nomenclature is defined in ASME BVPC Section VIII, Division 2.

## Slide 107: Nonbuilding Structures Not Similar to Buildings
In-plane shear: av = 0.8 Cv = 0.2967 Do/t = 320 nv = 0.8197 Allowable shear stress = Fva = nvFve = 17,631 psi
Notes: Slide 107 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 108: Nonbuilding Structures Not Similar to Buildings
Combination of uniform axial compression, axial compression due to bending moment, and shear in the absence of hoop compression:
Notes: Slide 108 is a continuation of Example 17.7 – Vertical Vessel.
The support skirt in this example is inadequate for the seismic loads based on R/Ie = 1.0. The thickness of the support skirt must be increased and the critical buckling check repeated.

## Slide 109: Questions?
Notes: Slide 109 is the “question” slide.

## Slide 110: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.