## Slide 1: Wood Design
Disclaimer
by S. K. Ghosh, PhD
Wood Diaphragm Design Examples
Includes materials developed by Peter Somers S.E. and Steve Pryor, S.E.
Kelly Cobeen, S.E.
Notes: Graphic shows cover of the NEHRP Provisions FEMA P-1052.
This presentation addresses the wood design problems in Chapter 14 of the FEMA P-1051 NEHRP Recommended Design Provisions: Design Examples, as well as wood diaphragm examples included in Section 6.3 of Chapter 6.

## Slide 2: Context in the Provisions
NEHRP Recommended Seismic Provisions for New Buildings and Other Structures
FEMA P-1050-1, 2015 Edition
as adopted into
ASCE 7-16
Minimum Design Loads for Buildings
and Other Structures
2016 Edition
Notes: These examples are based on the 2015 Edition of the NEHRP Provisions as adopted into ASCE 7-16. Unless noted otherwise, section numbers cited in these slides refer to ASCE 7-16.

## Slide 3: Other Primary Standards
AWC NDS with Supplement, 2015 Edition – wood framing and connections
AWC SDPWS, 2015 Edition – shear walls and diaphragms
Notes: The figures are the covers of the 2015 Editions of the American Wood Council (AWC) National Design Specification (NDS) and Special Design Provisions for Wind and Seismic (SDPWS).
In addition to ASCE 7-16 the two primary standards used in these examples problems are the 2015 Editions of the American Wood Council (AWC) National Design Specification (NDS) and Special Design Provisions for Wind and Seismic (SDPWS). Both standards are adopted by ASCE 7-16 and the International Building Code. Other standards noted in the example problems are cited at the beginning of Chapter 14.

## Slide 4: Wood Problem Presentation
Chapter 14 – Wood Design
Problem 14.1 – Three story wood light-frame apartment building in Seattle, Washington
Problem 14.2 - Diaphragm and wall anchorage design for warehouse building with masonry walls. Masonry wall design is provided in Problem 13.1.
Chapter 6 – Horizontal Diaphragm Design
Section 6.3.1 – One-Story Wood Assembly Hall
Section 6.3.2 – Three-Story Multi-Family Residential
Notes: The two problems addressed by Chapter 14 and these slides are …
Both of the problems are solved using strength level forces and LRFD procedures. These problems address seismic design only.
In addition, two example problems from Section 6.3 of Chapter 6 are included. These examples address design of wood diaphragms, and are most relevant in combination with Chapter 14 examples.

## Slide 5: Problem 14.1: Three-Story Apartment Building
Notes: Graphic shows a drawn elevation of the three-story apartment building used as the basis for Example 14.1. Graphic shows a drawn elevation of the three-story apartment building used as the basis for Example 14.1.
Let use now begin with Problem 14.1, illustrating the seismic design of a three-story wood light-frame apartment building.

## Slide 6: Problem 14.1
Will Illustrate:
Seismic design forces determined using the simplified procedure of ASCE 7 Section 12.14
Design of wood diaphragms
Design of wood segmented shear walls
Design of wood perforated shear walls
Notes: These slides will illustrate the following four parts of the seismic design…
See the example problems for additional items not addressed in these slides.

## Slide 7: Problem 14.1
Notes: This slide shows a longitudinal section and longitudinal elevation of the apartment building, which is three stories over a crawl space. Note that the exterior walls have some sections that are sheathed walls and other sections that are noted to be “glazed walls,” using a curtain wall type of system rather than light-frame stud walls.

## Slide 8: Problem 14.1
Notes: This slide shows a typical floor plan for the building, with a central longitudinal corridor, and rooms symmetrically on either side of the corridor.

## Slide 9: Problem 14.1
Apartment Building Characteristics:
Three stories above grade plane
Crawlspace surrounded by concrete stem walls – first floor is treated as the base for seismic design
Wood light-frame bearing wall system
Wood joist floor system with light-weight (nonstructural) concrete topping slab (acoustics, fire rated assembly)
Residential occupancy – Risk Category II
Roof and floor framing Douglas Fir-Larch (DF-L)
Typical wall framing Hem-Fir (HF) No. 2
Tie-down posts DF-L No. 1
Notes: Characteristics of the apartment building include:

## Slide 10: Simplified Seismic Force Provisions
“Simplified Alternative Structural Design Criteria for Simple Bearing Wall or Building Frame Systems”
Intent:
Applicable to smaller, more regular buildings
Reduced seismic force complexity
Without reduced performance
Simplified seismic forces permit designer to focus on load path
Methodology relies on scoping limitations
Notes: Rather than using the seismic force provisions of Chapter 12 of ASCE 7, this example uses the simplified provisions of Section 12.14.
These provisions were developed with the following intent …
The simplified method relies on scoping provisions to identify buildings eligible for use

## Slide 11: Simplified Seismic Force Provisions
ASCE 7 Section 12.14.1.1 scoping limitations:
Risk Category I or II – OK Category II
Site Class NOT E or F – will verify
3 stories or less above grade plane - OK
Bearing wall or building frame system – OK
Minimum two lines of lateral resistance in each direction, minimum one line on each side of center of weight
Notes: There are 12 scoping limitations that need to be met to qualify for use of the simplified provisions. We will go through each of the 12:
Read through list…

## Slide 12: Simplified Seismic Force Provisions
ASCE 7 Section 12.14.1.1 scoping limitations:
Notes: Graphic shows building floor plan with four shear wall lines in the longitudinal direction marked using red lines, and three shear wall lines in the transverse direction marked using green lines.
In order to evaluate limitation 5, this plan locates each of the primary shear wall lines. There are four lines of shear wall in the longitudinal direction, shown by the four red lines. These are symmetric to the building plan, with two lines on each side of the center of weight. There are three lines of shear wall in the transverse direction, with a slight offset in the two sections that make up each line. These are also close to symmetric on the building plan, and meet the requirement of limitation 5.

## Slide 13: Simplified Seismic Force Provisions
ASCE 7 Section 12.14.1.1 scoping limitations:
Risk Category I or II – OK Category II
Site Class NOT E or F – will verify
3 stories or less above grade plane - OK
Bearing wall or building frame system – OK
Minimum two lines of lateral resistance in each direction, minimum one line on each side of center of weight – OK
Center of weight in each story located not further than 10% of diaphragm length from geometric center
Notes: Limitation 5 can be marked as OK. For limitation 6 we go back to the building plan

## Slide 14: Simplified Seismic Force Provisions
Center of weight and geometric center
ASCE 7 Section 12.14.1.1 scoping limitations:
Notes: Graphic shows the building floor plan, with a circle locating the coincident center of weight and geometric center.
Limitation 6 requires that the distance between the center of weight and the geometric center be not more than 10% of the building length in that direction. This will be evaluated once in the longitudinal direction and once in the transverse direction. For this building plan the center of weigh is for practical purposes coincident with the building geometric center, so meets the criterion.

## Slide 15: Simplified Seismic Force Provisions
ASCE 7 Sec. 12.14.1.1 scoping limitations:
Risk Category I or II – OK Category II
Site Class NOT E or F – will verify
3 stories or less above grade plane - OK
Bearing wall or building frame system – OK
Minimum two lines of lateral resistance in each direction, minimum one line on each side of center of weight – OK
Center of weight in each story located not further than 10% of diaphragm length from geometric center – OK
Structures with cast-in-place diaphragms – not applicable
Notes: So limitation 6 can be marked OK.
The balance of the limitations are…

## Slide 16: Simplified Seismic Force Provisions
ASCE 7 Sec. 12.14.1.1 scoping limitations:
Buildings with diaphragm that is not flexible – not applicable
Shear wall lines at no more than 15 degrees from major orthogonal axes – not applicable, shear wall lines align with major x and y axes
Simplified seismic force procedure used in both horizontal directions – OK
Irregularities – in-plane and out-of-plane offsets of vertical shear wall elements not permitted – OK shear walls will stack in all three floors
Lateral load resistance at any story not less than 80% of resistance in story above – OK
Notes: With the exception of the site class, which will be discussed shortly, all limitations for use of the simplified method have been met

## Slide 17: Simplified Seismic Force Provisions
Mapped spectral response parameters
SS = 1.34 (from USGS web site)
S1 = 0.67 (from USGS web site)
Site Class = D (from soils report)
Design spectral response parameter
Base shear based on SDS (Sec. 12.14.8.1)
Fa = 1.0 per Sec. 11.4.3 (alternate is default per Sec. 12.14.8.1)
SDS = 2/3 (Fa) SS = 2/3 (1.0) 1.34 = 0.89g
SDS <= 1.5 (Sec. 12.14.8.1) OK
Notes: Variables needed for the seismic design now need to be determined. The following information is provided…
The site class of D is the last of the 12 criteria for use of the simplified method, so we are ok to proceed.
From this information SDS can be calculated

## Slide 18: Simplified Seismic Force Provisions
Seismic Design Category
Per Section 11.6
Based on Table 11.6-1 only where S1 <= 0.75
Seismic Design Category = D
Response Modification Factor (R) = 6.5 (Table 12.14-1)
Simplified method coefficient (F) = 1.2 (Sec. 12.14.8.1)
Base Shear V = F(SDS)W / R
= 1.2 (0.89) W / 6.5
= 0.164 W (strength design level)
Notes: Next the SDC can be determined.
Because S1 is less than 0.75, only SDS needs to be considered in determining the base shear.
SDC is assigned as D per Table 11.6-1
In order to calculate the base shear, two additional variables are needed.
R is assigned as 6.5 from Table 12.14-1. Note that use of Table 12.2-1 is not permitted when using simplified method
F is a factor specific to the simplified method. It increases with number of stories and makes up for not using the vertical distribution of seismic forces used in the Section 12.8 ELF procedure.
The base shear is then calculated.

## Slide 19: Simplified Seismic Force Provisions
Weight take-off for base shear:
Calculate unit dead load for roof, floor, and wall assembles
Sum dead loads tributary to each floor and roof level
Sum over floor and roof levels for total building seismic weight
Notes: Important to the seismic design is an accurate take-off of the building weight. Typical steps include:
The designer is cautioned to evaluate the weight of interior an exterior walls, as the weight can be a significant contributor to overall building weight.

## Slide 20: Simplified Seismic Force Provisions
Weight take-off for base shear:
Notes: This table, taken from the example problem shows some of the detail of a weight take-off, arriving at a weight tributary to each roof and floor and a total building weight.

## Slide 21: Simplified Seismic Force Provisions
Base Shear V = F(SDS)W / R
= 1.2 (0.89) W / 6.5
= 0.164 W (strength design level)
= 0.164 (751 kips) = 123.4 kips
Notes: With the building weight known, the base shear can be calculated.

## Slide 22: Simplified Seismic Force Provisions
Vertical distribution of base shear:
Fx = wx (V) /W (Sec. 12.14.8.2)
  This means incremental seismic force at each level is calculated as weight acting at that level times the base shear coefficient 0.164g
Notes: Graphic shows a section of the three story apartment building with seismic forces applied at each story.
Unlike ASCE 7 Section 12.8 ELF procedures, there is no vertical redistribution of the seismic forces. The seismic force at each level can be calculated as the weight tributary to that level times the base shear coefficient.

## Slide 23: Simplified Seismic Force Provisions
  Seismic Force (strength level) Summed Story Shear
  FROOF = 182.8(123.4)/751 = 30.0 kips = 30.0 kips
  F3RD = 284.2(123.4)/751 = 46.7 kips = 76.7 kips
  F2ND = 284.2(123.4)/751 = 46.7 kips = 123.4 kips
Notes: Graphic shows a section of the three story apartment building with seismic forces applied at each story.
The incremental seismic force and summed story force can be calculated as shown:

## Slide 24: Simplified Seismic Force Provisions
Horizontal distribution of seismic force
Idealized as flexible, idealized as rigid, or semi-rigid?
ASCE 7 - Diaphragms of wood structural panels are permitted to be considered flexible (Sec. 12.14.5)
ASCE 7 – Seismic design story shear shall be distributed to the vertical elements of the SFRS using tributary area rules (Sec. 12.14.8.3.1)
SDPWS – Additional requirements may apply to diaphragms with torsional irregularities or diaphragms that cantilever more than six feet
For this reason for this problem - collectors to shear walls should be added to avoid diaphragm cantilevers at building ends
Notes: An important early step in the seismic design is the categorization of the diaphragm as rigid, flexible or semi-rigid. This significantly affects distribution of seismic forces to vertical elements, diaphragm shears, and the level of complexity of the seismic analysis. Where possible, most designers of wood buildings try to keep designation to be “flexible” as this allows for simpler analysis based on tributary area methods. The simplified method specifically permits wood structural panel diaphragms to be idealized as flexible. SDPWS, in the 2015 addition, includes additional limits for diaphragms with torsional irregularities or cantilevers greater than six feet. Because both of these can be avoided in the example problem, a flexible diaphragm assumption can be used. Note that sections of the diaphragm at the stairwells at each end will need to be provided with collectors so that the diaphragm does not have an eight foot cantilever.

## Slide 25: Simplified Seismic Force Provisions
Combination of Load Effects (Sec. 12.14.3)
Combined horizontal (QE) and vertical (0.2SDSD) seismic:
E = QE + 0.2SDSD (controls overturning downward)
E = QE – 0.2SDSD (controls overturning uplift)
Strength level load combinations:
(1.2 + 0.2SDS)D + 1.0QE + 0.5L + 0.2S
= 1.38D + 1.0QE + 0.5L + 0.2S
(0.9 – 0.2SDS)D – 1.0QE = 0.72D – 1.0QE
Note that for much of diaphragm and shear wall design, vertical loads do not effect demand, so this will be simplified to 1.0QE
Notes: Seismic load effects are specified in Section 12.14.3, as shown here. Note that much of the design of the diaphragms and shear walls for shear effects will only need to consider QE. The load combinations become important for overturning effects when seismic and gravity loads interact.

## Slide 26: Diaphragm Design
W = 0.202 klf
SPAN = 88 ft
Horizontal distribution of seismic force at roof:
VROOF = 30 kips - wTRANS = 30/ 148 ft. = 0.202 klf
Notes: Graphic shows the roof plan with a diaphragm span of 88 feet at the right hand side of the plan. A uniform seismic load of 0.202 klf is shown to be applied, and reactions at each end of the 88 foot span.
As a first step in the seismic design, we will look at the seismic loading on one span of the roof diaphragm, using tributary area or simple-span beam analogies.
Because of the simple building geometry, the weight is considered to be uniformly distributed along the length of the building. A uniform seismic load in the transverse direction can be calculated as the seismic force to the roof divided by the building length.

## Slide 27: Diaphragm Design
Horizontal distribution of seismic force at roof:
VROOF = 30 kips
wTRANS = 30/ 184 ft. = 0.202 klf
For 88 foot span shown
R = w(L)/2 = 0.202(88 ft)/2 = 8.93 kips
Unit Shear vROOF = 8.93 kips/56 ft = 0.160 klf
This is strength level demand
Notes: From this the reaction in kips and unit shear in klf for the roof diaphragm can be calculated.

## Slide 28: Diaphragm Design
For 88 foot span shown
Unit Shear vROOF = 8.93 kips/56 ft = 0.160 klf
This is strength level demand
Capacity From SDPWS Table 4.2C for unblocked wood structural panel diaphragms
Construct as load case 1 for transverse load direction, since this is longest span
15/32 rated sheathing on 2x DF-L framing
Nominal unit shear capacity vs = 0.480 klf
F = 0.80 (SDPWS Sec. 4.2.3)
Adjusted capacity = (0.8)(0480) = 0.384 > 0.160 OK
Notes: The calculated LRFD/strength level shear of 0.160 klf can then be compared to an allowable LRFD unit shear determined in accordance with SDPWS Section 4.2.
Because of the very low calculated unit shear demand, an unblocked diaphragm is chosen. While providing lower capacity, the labor required to building this diaphragm type is notable less, so it is preferred by builders.
Steps in determining the unit shear capacity are…

## Slide 29: Diaphragm Design
15/32 RATED SHEATHING, 8d COMMON @ 6” O.C. SUPPORTED EDGES, 12” O.C. OTHER EDGES. NAIL 6” O.C. ALL DIAPHRAGM BOUNDARIES, COLLECTORS AND OVER SHEAR WALLS BELOW
Notes: Graphic shows building plan with layout of 4 ft. by 8 ft. wood structural panel sheathing laid out with the long dimension in the longitudinal building direction, and stagger between rows of panels.
This slide shows the roof plan with the load case 1 sheathing layout projected on top and the chosen sheathing and nailing called out. Note that in addition to typical nailing, it is important to have edge nailing at all diaphragm boundaries, interior collectors, and to interior shear walls.

## Slide 30: Diaphragm Design
For 88 foot span shown
M = (w)L2 /8 = 0.202 klf (88 ft)2/8 = 197 ft-kip
Chord = M/56 ft = 197/ 56 ft = 3.51 kips T/C
Use 2- 2x6 top plates as chord. Splice top plates with 16d common nails
Notes: Next, the diaphragm chord forces can be calculated.

## Slide 31: Diaphragm Design
SPLICE IN TOP PLATE
TWO ROWS 16d @ 6” O.C. EA. ROW, STAGGER (14 NAILS MINIMUM)
TWO ROWS 16d @ 6” O.C. EA. ROW, STAGGER (14 NAILS MINIMUM)
For 88 foot span shown
Chord = M/56 ft = 197/ 56 ft = 3.51 kips T/C
Use 2- 2x6 top plates as chord. Splice top plates with 16d common nails
Reference (tabulated) nail capacity Z = 0.122 kips/nail (NDS Table 12N)
Z’ = ZKFFl = (0.122)(3.32)(0.65)(1.0) = 0.263 kips/nail
Number of nails = 3.51 kips/ 0.263 = 13.3, use 14 min
Notes: Graphic shows a double top plate. There is a break in the upper top plate. To each side of the top plate break, the calculated 14 nails are shown.
For the span shown, the double top plate can be used as the chord member. This will require that fastening at splices in the top plates are designed to carry the chord force. In this case the number of 16 penny common nails is calculated using NDS Table 12N.

## Slide 32: Segmented Shear Wall Design
R = 50% Seismic Force
W KLF
Horizontal distribution of seismic forces to center shear wall by tributary area methods
Notes: Graphic shows plan of the building with two diaphragm spans designated for loading in the transverse direction. A uniform transverse seismic load is applied, and three reactions are shown, corresponding to the three transverse wall lines. The reaction at the center shear wall line is noted as 50% of the story seismic force.
Next we will look at shear wall design, and start with one of the two segmented shear walls in the transverse direction at the center of the building. Using seismic force distribution based on tributary area, 50 percent of the seismic shear is assigned to the center shear wall line.

## Slide 33: Segmented Shear Wall Design
  Seismic Story Force to Center 50% Each Wall (strength level) x0.50 x0.50
  FROOF = 30.0 kips = 15.0 kips = 7.50 kips
  F3RD = 46.7 kips = 23.35 kips = 11.68 kips
  F2ND = 46.7 kips = 23.35 kips = 11.68 kips
Notes: Graphic shows a transverse section of the building, with seismic forces at each level applied.
From the seismic force at each story, the portion to the center shear wall line is calculated. This is then divided by two as there are two shear walls, 25 foot long each, at the center of the building.

## Slide 34: Segmented Shear Wall Design
First floor design for shear:
V = 7.5 + 11.68 + 11.68 = 30.86 kips
For 25 foot shear wall shown
Unit Shear v1st = 30.86 kips/25 ft = 1.236 klf
This is strength level demand
Notes: We will look at shear design of the first floor shear wall.
For design of the first floor shear wall, the forces from each of the levels are added.
The unit shear can then be calculated by dividing by length.

## Slide 35: Segmented Shear Wall Design
Capacity From SDPWS Table 4.3A for blocked wood structural panel shear walls
19/32 rated sheathing on Hem-Fir studs at 16” o.c.
Nominal unit shear capacity vs = 1.740 klf
F = 0.80 (SDPWS Sec. 4.3.3)
Adjustment for stud species with S.G. = 0.43
  = 1 – (0.5 – 0.43) = 0.93 (SDPWS Table 4.3A footnote)
Adjusted capacity = (0.93)(0.8)(1.740) = 1.294 > 1.236 OK
This shear wall requires 3x or stitched 2-2x framing members at abutting panel edges to avoid framing splitting during nail driving (SDPWS Sec. 4.3.7.1, Item 4)
Design shear anchorage to the foundation
Notes: Similar to the diaphragm, the unit shear capacity of the shear wall is determined in accordance with SDPWS Section 4.3.
Because the problem statement identified the stud species as Hem-Fir, and tabulated nominal capacities are for DF-L or Southern Pine, an adjustment to capacity bust be made for species. In addition, the nominal capacity is multiples by a phi factor of 0.8. The adjusted capacity is determined to be greater than the demand, so OK.
There are additional details of construction that should be noted…

## Slide 36: Segmented Shear Wall Design
Strength level load combinations:
= 1.38D + 1.0QE + 0.5L + 0.2S (compression critical)
= 0.72D – 1.0QE (tension and uplift critical)
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting.
Once shear design is complete, design for overturning and uplift is required. This involves the interaction of seismic forces and gravity loads, and so the applicable load combinations must be used as seen here. Note that the upper combination is generally found to be critical for compression load path design, and the lower for uplift/tension load path design.

## Slide 37: Segmented Shear Wall Design
Tension and Uplift forces = 0.72D – 1.0QE
At first floor shear wall QE overturning moment =
3rd to roof: (7.5)(8 ft) +
2nd to 3rd: (7.5 + 11.68)(8 ft) +
1st to 2nd: (7.5 + 11.68 + 11.68)(8ft)
= 60 + 153 + 247 = 460 ft-kips
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting.
We will look first at overturning design using the uplift and tension critical load combination. We will first calculate the overturning moment using the applied seismic forces. Note that the overturning moment multiples the shear wall story force times the eight foot clear height of the story (eight feet) ignoring the additional foot that corresponds to the depth of the floor framing. This is based on standard design practice.

## Slide 38: Segmented Shear Wall Design
Resisting dead load 0.72D =
Shear wall self weight (8+8+8ft)(25ft)(11psf) = 6.60 kips
Tributary roof + floor (10ft)(25ft)(15+20+20psf) = 13.75 kips
Tributary longitudinal Wall (8+8+8ft)(10ft)(11psf)2 = 5.28
Sum = 25.63 kips x 0.72 x 25ft/2 = 230 ft-kips
Net uplift = (460-230)/25ft = 9.4 kips
0.72D
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting. The dead load resisting is 0.72D
The dead load resisting overturning and the resisting moment can then be calculated as shown.

## Slide 39: Segmented Shear Wall Design
0.72D
Select tie-down anchor from manufacturer’s catalog
Net uplift = (460-230)/25ft = 9.4 kips
Tie-down anchor with ASD capacity of 12.1 kips @ CD=1.6
Convert to strength design = KF = 2.88/1.6 (AF&PA, 1996)
ZKFFl = 12.1(2.88/1.6)(0.65)(1.0) = 14.2 kips > 9.4 OK
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting.
From the overturning and resisting moments, the net uplift can be calculated. A tie-down is then selected from a manufacturer’s catalog, and the tabulated strength design capacity turned into an LRFD adjusted resistance.

## Slide 40: Segmented Shear Wall Design
Additional tension and net uplift checks:
Check post in tension with net area (subtract bolt hole area if applicable)
Check bolt fastener capacity for connection to post using NDS Chapter 12
Check foundation for tie-down anchorage forces
Check foundation for tie-down shear and flexure forces
Notes: In addition to the tie-down devices, the following much also be checked at each end of each shear wall…

## Slide 41: Segmented Shear Wall Design
1.38D+0.5L+0.2S
Compression and downward forces = 1.38D + 1.0QE + 0.5L + 0.2S
At first floor shear wall QE overturning moment
= (7.5)(8 ft) + (7.5 + 11.68)(8 ft) + (7.5 + 11.68 + 11.68)(8ft) = 60 + 153 + 247 = 460 ft-kips
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting.
Following completion of the design for uplift and tension, design for the compression end of the shear wall needs to occur. In this case the compression critical load combination is used. The overturning moment is calculated as previously done.

## Slide 42: Segmented Shear Wall Design
1.38D+0.5L+0.2S
D = 25.63, L = 15.00, S = 6.25
Resisting dead load 1.38D = 1.38 (25.63) = 35.36 kips
Resisting live load = 0.5L = 0.5(15.00) = 7.50 kips
Resisting Snow load = 0.2S = 0.2 (6.25) = 1.25 kips
Sum = 44.11 kips x 25ft/2 = 551 ft-kips > 460 no net uplift
C = load mobilized for 460 ft-kips = 460/12.5 ft = 36.8 kips
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting. In this case the vertical force is 1.38D + 0.5L + 0.2S.
The resisting moment is again calculated. In this case live and snow loads need to be considered in addition to dead and seismic loads. Using a free-body diaphragm, the compression resultant is calculated for the first story shear wall. Note that it I quite a bit higher than the 9,4 kips net tension.

## Slide 43: Segmented Shear Wall Design
Compression member check:
C = load mobilized for 460 ft-kips = 460/12.5 ft = 36.8 kips
Check chosen 6x6 post for C = 36.8 kips
Note that other studs at the end of the shear wall can be added to the post compression capacity
Check bearing of post and studs on sill – bearing perpendicular to grain
Check post and stud axial compression capacity
Check foundation for concentrated compression load
Notes: Some of the compression checks that need to be done include…

## Slide 44: Perforated Shear Wall Design
Horizontal distribution of seismic forces to exterior longitudinal shear wall by tributary area methods
Notes: Graphic shows floor plan with a green rectangle and arrow indicating the wall line where the perforated shear wall is located.
We will next take a look at design of a perforated shear wall. This shear wall is located on the building exterior on the longitudinal face of the building.

## Slide 45: Perforated Shear Wall Design
Horizontal distribution of seismic forces to exterior longitudinal shear wall by tributary area methods
Notes: Graphic shows the exterior elevation of the building, with the center shear wall designated with arrow.
Of the three perforated shear walls along this elevation, we will look at the center wall with an overall length of 30 feet.

## Slide 46: Perforated Shear Wall Design
SEGMENT 1 – FULLY ANCHORED FOR UPLIFT. DEVELOPS HIGH UNIT SHEAR
SEGMENT 2 – PARTIALLY ANCHORED FOR UPLIFT. DEVELOPS REDUCED UNIT SHEAR
SEGMENT 3 – PARTIALLY ANCHORED FOR UPLIFT. DEVELOPS REDUCED UNIT SHEAR
TIE-DOWN ANCHOR
Notes: Graphic shows a wall elevation, with three full-height wall piers shaded and designated as piers 1, 2 and 3. One tie-down is shown at each end of the overall shear wall, and seismic load is shown to be applied from left to right.
In the wood chapter background material, the three types of shear walls permitted by SDPWS were introduced, including the perforated shear wall. As a brief reminder, the design addresses the entire wall including both full-height sheathed segments and openings. Tie-downs are only provided at the extreme ends of the shear wall. As a result, Segment 1 is fully fixed for overturning and will have a high unit shear. Segments 2 and 3 are partially fixed for overturning in the load direction shown, and will develop smaller unit shears. The overturning fixity for segments 2 and 3 comes from a combination of the anchor bolts at the wall base and the sheathing above and below the window openings.

## Slide 47: Perforated Shear Wall Design
What is different with perforated shear wall design?
Scoping requirements limit use
Capacity is lower due to not all segments being fully effective
C0 is used to adjust from average shears to peak segment shears
Tie-downs used at extreme ends of perforated shear wall
Compression posts provided at each end of each wall segment
Bottom of wall connection provided for unit uplift load equal to unit shear load
Notes: The things that are different with a perforated shear wall are:

## Slide 48: Perforated Shear Wall Design
R = 0.223 x STORY SHEAR
R = 0.277 x STORY SHEAR
R = 0.277 x STORY SHEAR
R = 0.223 x STORY SHEAR
Horizontal distribution of seismic forces to exterior longitudinal shear wall by tributary area methods
Notes: Graphic shows a plan of the building with loading assigned to the four shear wall lines in the longitudinal direction. The exterior wall lines are assigned 0.223 times the story shear. The interior wall lines are assigned 0.277 times the story shear. The exterior wall to be designed is designated.
The shear to be assigned to the exterior wall line is calculated using tributary area as shown.

## Slide 49: Perforated Shear Wall Design
V = 0.223 (30 ft/75 ft)
= 0.0892 x STORY SHEAR
Horizontal distribution of seismic forces to exterior longitudinal shear wall by tributary area methods
Notes: Graphic shows same plan as before, and identifies the center of the three walls in the exterior wall elevation as the one to be designed. The seismic load to this wall is determined in an approximate fashion by using the 30 foot wall length as a proportion of the 75 foot total along this exterior wall line. The wall will be designed for 0.0892 times the story shear.

## Slide 50: Perforated Shear Wall Design
  Seismic Story Force
  (strength level)
  FROOF = 0.0892(30.0 kips)
  = 2.67 kips
  F3RD = 0.0892(46.7 kips)
  = 4.16 kips
  F2ND = 0.0892(46.7 kips)
  = 4.16 kips
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting.
Given this portion of the story shear, shear wall forces at the roof, 3rd and 2nd stories are calculated.

## Slide 51: Perforated Shear Wall Design
SDPWS Section 4.3.5.3 scoping limitations:
A full-height segment meeting aspect ratio requirements is required at each end of the designated wall used for calculation
Aspect ratio limits must be met in full height segments that are counted in calculations
Nominal unit shear capacity not to exceed 1740 plf for seismic
Perforated shear wall must be in one plane. If out of plane offsets occur, portions on each side of the offset are to be considered separate perforated shear walls
Notes: There are a series of scoping limits that must be met in order to use the perforated shear wall design method. These include…

## Slide 52: Perforated Shear Wall Design
SDPWS Section 4.3.5.3 scoping limitations:
Collectors for force distribution to be provided for full length of perforated shear wall
Uniform top of wall and bottom of wall elevations
Maximum story height “h” of 20 feet
Notes: The balance of the limitations include. It should be possible to meet all of these limitations within this shear wall design, so we will proceed with the design.

## Slide 53: Perforated Shear Wall Design
Perforated shear wall shear capacity adjustment factor
SDPWS Sec. 4.3.3.5):
Vwall = (v C0) S Li
T = C = V(h) / (C0 S Li)
Vmax = V / (C0 S Li)
v = factored shear resistance (SDPWS Table 4.3A)
C0 = shear capacity adjustment factor (SDPWS Table 4.3.3.5)
S Li = sum of full-height shear wall segment lengths
Notes: Key to the use of perforated shear wall design is the capacity adjustment factor, C0. This variable, found in SDPWS Table 4.3.3.5, provides an adjustment between the average unit shear in the full height wall segments, and the peak unit shear in the segments with full overturning restraint. It can be thought of as a measure of the efficiency of the perforated shear wall relative to segmented shear walls with tie-downs at each end of each full height wall segment. This factor is used to:
-Reduce the capacity of the overall wall
-Increase the tension overturning effect to account for the most highly loaded segment
-Increase the compression overturning effect similarly.

## Slide 54: Perforated Shear Wall Design
  Shear capacity adjustment factor (SDPWS Table 4.3.3.5):
  h = 8 ft
  All segments meet aspect ratio
  Maximum opening height = 4 ft/ 8 ft = h/2
  Percent full-height sheathing = 18 ft/ 30 ft
  = 60%
  C0 = 0.83
Notes: Graphic shows an elevation of the shear wall with seismic forces applied at each story and a vertical force acting.
The capacity adjustment factor for the shear wall being designed is determined as a function of the height of the maximum opening as a portion of the wall clear height, and the percentage of the overall wall length that has full height sheathing. With the values of h/2 and 60%, C0 can be looked up in table 4.3.5 to be 0.83.

## Slide 55: Perforated Shear Wall Design
First floor design for shear:
V = 2.67 + 4.16 + 4.16 = 10.99 kips strength level
Vwall = (v C0) S Li
Capacity From SDPWS Table 4.3A for blocked wood structural panel shear walls
15/32 rated sheathing 10d@3 on Hem-Fir studs at 16” o.c.
Nominal unit shear capacity vs = 1.20 klf
F = 0.80 (SDPWS Sec. 4.3.3)
Adjustment for stud species with S.G. = 0.43
  = 1 – (0.5 – 0.43) = 0.93 (SDPWS Table 4.3A footnote)
Adjusted capacity = (0.93)(0.8)(1.20) = 0.893 klf
Notes: The first story shear wall demand is calculated from information on previous slides.
The unit shear capacity of selected sheathing and nailing is determined from SDPWS Section 4.3, as was done with the segmented shear wall.

## Slide 56: Perforated Shear Wall Design
First floor design for shear:
V = 2.67 + 4.16 + 4.16 = 10.99 kips strength level
Vwall = (v C0) S Li
V = 0.893 klf
C0 = 0.83
S Li = 4 +10 + 4 = 18 ft
Vwall = 0.893 (0.83) 18 = 13.34 kips > 10.99 kips OK
Notes: The adjusted capacity of the perforated shear wall can then be compared to the demand.

## Slide 57: Perforated Shear Wall Design
Tension and Uplift forces = 0.72D – 1.0QE
Treated differently than segmented shear wall because perforated shear wall does not overturn globally, uplift on critical individual segment is checked
Shear wall gross uplift T = V(h) / (C0 S Li)
Cumulative gross uplift:
3rd T = 2.67(8 ft)/(0.83)(18ft)=1.42 kips
2nd T =1.42+(2.67+4.16)(8ft)/(0.83)(18ft)=5.08 kips
1st T =5.08+(2.67+4.16+4.16)(18ft)/(0.83)(18ft)=11.50 kips
Notes: Next we will look at overturning of the perforated shear wall it is important to note that overturning and resistance are conceptually different than in the segmented shear wall because:
The gross uplift at each story is calculated per the perforated shear wall formula as shown. Note that the cumulative uplift forces are shown here.

## Slide 58: Perforated Shear Wall Design
Gross uplift force = 11.5 kips
Resisting load for first segment, based on judgement
Resisting dead load = 0.72D
Notes: Graphic shows an elevation of the perforated shear wall, with a very limited area of dead load resisting depicted in the immediate vicinity of the tie-down and uplift force. The gross uplift is labeled as 11.5 kips.
Because the wall is not globally overturning, the dead load that can be used to resist the uplift is limited to a very local tributary area as shown.

## Slide 59: Perforated Shear Wall Design
Resisting dead load 0.72D =
Exterior wall weight = (8+8+8ft)(4ft)(9psf)=0.86 kips
Tributary roof = (8ft)(4ft)(15psf) = 0.48 kips
Tributary floor = 2(8ft)(4ft)(20psf) = 1.28 kips
Sum = 2.62 kips
Net uplift = 11.5 – 2.62(0.72) = 9.61 kips
See segmented shear wall similar for design of tie-down, tie-down post, etc.
Notes: Here the resisting dead load is calculated using the very limited tributary area, resulting I there being limited reduction to the gross uplift calculated. Design and detailing of the uplift load path is the same as discussed for the segmented shear wall.

## Slide 60: Perforated Shear Wall Design
Gross uplift force = 11.5 kips
Uplift resisting load for first segment, based on judgement
Compression reaction C
Compression critical resisting load = 1.38D + 0.5L + 0.2S
Notes: Graphic shows an elevation of the perforated shear wall, with a very limited area of dead load resisting depicted in the immediate vicinity of the tie-down and uplift force. The gross uplift is labeled as 11.5 kips, and a compression reaction is shown at the compression end of the first perforated shear wall segment, close to the tension uplift.
The compression reaction must next be calculated, It is important that a complete load path for gravity loads already exist prior to the design for seismic overturning loads. Because very little gravity load is used to reduce the uplift load path, very little will be added to the compression load path.

## Slide 61: Perforated Shear Wall Design
D = 2.62, L = 1.92, S = 0.60
Resisting dead load 1.38D = 1.38 (2.62) = 3.62 kips
Resisting live load = 0.5L = 0.5(1.92) = 0.96 kips
Resisting snow load = 0.2S = 0.2 (0.60) = 0.12 kips
Sum = 4.69 kips
Tnet = 11.5 – 4.69 = 6.81 kips (other load combination controls for uplift load path design)
Cnet = 6.81 + 4.69 = 11.5 kips
Notes: The resisting gravity loads are calculated, and the net compression load is determined. Note that posts or studs must be provided for this in addition to for the gravity loads tributary to that location.

## Slide 62: Perforated Shear Wall Design
Gross uplift force = 11.5 kips
Net uplift force = 6.81 kips
Uplift resisting load for first segment, based on judgement
Net compression reaction = 11.5 kips
Resisting load = 1.38D + 0.5L + 0.2S
Notes: The diaphragm of overturning tension and compression loads is shown. Graphic shows an elevation of the perforated shear wall, with a very limited area of dead load resisting depicted in the immediate vicinity of the tie-down and uplift force. The gross uplift is labeled as 11.5 kips gross and 6.81 kips net. The compression reaction is identified as 11.5 kips.

## Slide 63: Perforated Shear Wall Design
Compression member check:
Check post for C = 11.5 kips
Provide studs in addition to post at the end of the shear wall segment to resist local dead, live and snow loads
Check bearing of post and studs on sill – bearing perpendicular to grain
Check post and stud axial compression capacity
Check foundation for concentrated compression load
Notes: The balance of the checks needed for compression are:

## Slide 64: Perforated Shear Wall Design
Shear wall unit shear and tension anchorage:
t = v = V / (C0 S Li)
Unit shear and unit uplift at bottom of each shear wall segment at each floor level
Resisted by anchor bolts at first floor resisted by other fasteners at upper levels
V = 10.99 kips
First floor t = v = 10.99/ (0.83)(18 ft) = 0.736 klf
Check anchor bolts for shear
Check anchor bolts and plate washers for uplift
Provide ADDITIONAL fastening as required to resist these forces
Notes: In addition to the overturning design, and unique to perforated shear walls, the base of the shear wall at each level must be designed for both unit shear transfer AND unit tension transfer. This makes sure that the base of the shear wall has the ability to provide distributed uplift resistance, similar to what might be provided by anchor bolts at the foundation. This is done as follows:

## Slide 65: Perforated Shear Wall Design
Uplift anchorage at each end of perforated shear wall - edge nail sheathing to tie-down post
Compression post at each end of each shear wall segment – edge nail sheathing to post
Unit shear, v, and unit tension, t, anchorage at each full-height segment
Provide for perforated shear wall:
Notes: Graphic shows each of the force transfer types that need to be designed for at the interface between the first story shear wall and the foundation.
-At each end, tie-downs provide uplift anchorage. These are shown by red arrows at each end of the overall shear walls
-At each end of each full-height sheathing segment a compression reaction occurs, These are shown by green arrows at each end of each full-height sheathed wall segment.
-At each full-height wall segment, the unit shear transfer and unit uplift transfer need to be provided. These are shown by pairs of horizontal and vertical blue arrows at each of the three full-height segments.

## Slide 66: Load Path Detailing
Notes: Graphic depicts framing at a floor level, with nailing required to transfer shear from the shear wall and diaphragm above to the shear wall below the floor.
Load path detailing is critical to performance of wood light-frame construction.

## Slide 67: Load Path Detailing
Notes: Graphic depicts framing at a floor level, with nailing required to transfer shear from the shear wall and diaphragm above to the shear wall below the floor.
Load path detailing is critical to performance of wood light-frame construction.

## Slide 68: Load Path Detailing
Notes: Graphic depicts framing at a floor level, with nailing required to transfer shear from the shear wall and diaphragm above to the foundation below.
Load path detailing is critical to performance of wood light-frame construction.

## Slide 69: Questions?

## Slide 70: Problem 14.2: One-Story Masonry Wall Warehouse Building
Notes: Graphic shows an elevation of the building to be designed.
Next, the one-story masonry shear wall building from Problem 14.2 will be presented. Note that the seismic design of this building was started in Problem 13.1, where the base shear was determined and the masonry walls designed.

## Slide 71: Problem 14.2
Will Illustrate:
Design of wood diaphragm
  Using basic ASCE 7 method
  Using new alternate ASCE 7 method
Design of masonry wall anchorage to wood diaphragm
Notes: The items to be illustrated in this problem include…

## Slide 72: Problem 14.2
Notes: This slide shows a roof plan for the building to be designed. Graphic shows roof plan with overall dimension of 100 feet transverse and 200 feet longitudinal. Exterior masonry walls, glulam beam and plywood roof sheathing are noted.

## Slide 73: Problem 14.2
Notes: Graphic shows exterior elevation of the building on a wall perforated by five door openings.

## Slide 74: Problem 14.2
Masonry Wall Building Characteristics:
Single-story warehouse building
100 ft. by 200 ft.
Masonry exterior walls 28 feet tall, 8 inch thick longitudinal, 12 inch transverse
Essentially flat wood structural panel diaphragm
Roof framing Douglas Fir-Larch (DF-L)
Initial seismic design shown in Problem 13.1
No irregularities
Redundancy factor, r, equal to 1.0
Notes: Some characteristics of the building of note are…

## Slide 75: Seismic Force Provisions
Mapped spectral response parameters
SS = 2.14 (from Problem 13.1)
S1 = 0.74 (from Problem 13.1)
Site Class = C (from soils report)
Design spectral response parameter
Base shear based on SDS (Sec. 12.14.8.1)
Fa = 1.0
SDS = 2/3 (Fa) SS = 2/3 (1.0) 2.14 = 1.43g
Notes: Some of the variables related to seismic forces are…

## Slide 76: Seismic Force Provisions
Response Modification Factor (R) = 5
Base Shear V = Cs W
= (SDS)W / R
= 1.43 W / 5
= 0.286 W (strength design level)
Cs = 0.286
Notes: As done in Problem 13.1, the base shear for this structure is calculate as…

## Slide 77: Seismic Force Provisions
Weight take-off for base shear:
Calculate unit dead load for roof, floor, and wall assembles
Sum dead loads tributary to each floor and roof level
Sum over floor and roof levels for total building seismic weight
With heavy wall structures, only weight of walls perpendicular to load is included in forces to diaphragm
Notes: The next step is to perform a weight take-off of the building. This includes…

## Slide 78: Seismic Force Provisions
Weight take-off for base shear:
Roof = 20 psf
8-inch wall = 65 psf, 16 ft height tributary to roof
12-inch wall = 105 psf, 18.7 ft height tributary to roof
Seismic mass acting at roof:
Roof = 20psf(100ft)(200ft) = 400 kips
Side wall = 65psf(200ft)(16ft) = 209 kips per wall
End wall = 105psf(100ft)(18.7ft) = 196 kips per wall
Total mass at roof = 400 + 2(209) + 2(196) = 1210 kips
Notes: The weight takeoff is …
Arriving at a total mass of 1210 kips acting at the roof.
Note that because weight from masonry walls parallel to and perpendicular to direction of load will be treated differently. The full weight of 1210 kips will not show up in the typical calculations.

## Slide 79: Seismic Force Provisions
SIDE WALL MASS = 209 KIPS
SIDE WALL MASS = 209 KIPS
ROOF MASS = 400 KIPS
END WALL MASS = 196 KIPS
END WALL MASS = 196 KIPS
Notes: Graphic shows roof plan with circle at center corresponding to mass of roof, and circle on each of the four exterior walls corresponding the mass from those walls. This helps visualize which mass is acting on the wood diaphragm for load in each direction.

## Slide 80: Seismic Force Provisions
Horizontal distribution of seismic force
Idealized as flexible, idealized as rigid or semi-rigid?
ASCE 7 - Diaphragms of wood structural panels used with masonry shear walls are permitted to be idealized as flexible (Sec. 12.3.1.1)
SDPWS – Additional requirements may apply to diaphragms with torsional irregularities or diaphragms that cantilever more than six feet – not applicable to this problem
Notes: As previously discussed, the ASCE 7 and SDPWS rules for classification of diaphragms need to be checked. In this case, idealization of the diaphragm as flexible is permitted.

## Slide 81: Seismic Force Provisions
Combination of Load Effects (Sec. 12.14.3)
Combined horizontal (QE) and vertical (0.2SDSD) seismic:
E = QE + 0.2SDSD (controls overturning downward)
E = QE – 0.2SDSD (controls overturning uplift)
Strength level load combinations (from Problem 13.1):
1.486D + 1.0QE
0.614D – 1.0QE
Note that for much of diaphragm and wall anchorage design, vertical loads do not effect demand, so this will be simplified to 1.0QE
Notes: As in Problem 14.1, the applicable load combinations are…
As in Problem 14.1, much of the design need only consider the horizontal effects of the seismic load

## Slide 82: Diaphragm Design
Diaphragm Design Forces – BASIC (Sec. 12.10.1.1)
Cs = 0.286
Fpx = wpx
For a single-story structure, this simplifies to:
Froof = CsWroof = 0.286 Wroof
Check upper and lower bounds for diaphragm forces:
Lower = 0.2 SDS Ie Wroof = 0.286 Wroof - OK
Upper = 0.4 SDS Ie Wroof = 0.572 Wroof - OK
Notes: Diaphragm design forces are calculated in accordance with ASCE 7 Section 1.210.1.1. for a single story building, the diaphragm force coefficient is the same as the base shear, except that upper and lower bounds much also be checked.

## Slide 83: Diaphragm Design
Diaphragm Design Forces – BASIC (Sec. 12.10.1.1)
For Longitudinal roof design:
W = 400 + 196 + 196 = 792 kips
Froof = 0.286(792) = 226 kips
For transverse roof design:
W = 400 + 209+ 209 = 818 kips
Froof = 0.286(818) = 234 kips
Notes: The seismic force to the diaphragm can then be calculated. Note that this differs in the longitudinal and transverse direction, as the mass being used in each direction is different.

## Slide 84: Diaphragm Design
w = 1.17 klf
SPAN = 200 ft
Transverse diaphragm seismic force at roof:
Wroof = 234 kips/200 ft = 1.17 klf
Notes: Graphic provides a plan of the roof with a uniform load applied in the transverse direction, and reactions shown at each end of the 200 foot diaphragm span.

## Slide 85: Diaphragm Design
On large diaphragms, zone concept used for nailing so not all areas have to be nailed for highest demand:
Notes: Graphic shows a plan of the roof with different areas of the roof designated as Zone A and Zone B. Zone A is located towards the ends of the 200 foot diaphragm span, and Zone B towards the middle. This is typical practice for this type of long-span diaphragm. It is not uncommon to see four to five nailing zones designated.

## Slide 86: Diaphragm Design
For 200 foot span shown
R = w(L)/2 = 1.17(200 ft)/2 = 117 kips
Peak Unit Shear vRoof = 117 kips/100 ft = 1.17 klf
This is strength level demand – use for Zone A
Capacity From SDPWS Table 4.2A for blocked wood structural panel diaphragms
15/32 Structural I 10d@2 on 2x DF-L framing
Nominal unit shear capacity vs = 1.64 klf
F = 0.80 (SDPWS Sec. 4.2.3)
Adjusted capacity = (0.8)(1.64) = 1.31 > 1.17 OK
Notes: Fro Zone A, the peak unit shear at the diaphragm reaction is calculated, and compared to adjusted nominal shear, as was done in Problem 14.1.

## Slide 87: Diaphragm Design
Try 15/32 Structural I with 10d@4” for Zone B
Capacity From SDPWS Table 4.2A for blocked wood structural panel diaphragms
15/32 Structural I 10d@4 on 2x DF-L framing
Nominal unit shear capacity vs = 0.85 klf
F = 0.80 (SDPWS Sec. 4.2.3)
Adjusted capacity = (0.8)(0.85) = 0.68 klf
Use similar triangles to figure out to what distance from diaphragm center (X) this diaphragm can be used
(0.68 klf/1.17 klf)(100 ft) = 58 ft from center
Notes: This is repeated for Zone B near the center of the diaphragm.

## Slide 88: Diaphragm Design
Zone A: 15/32 STR I w/ 10@2
Zone B: 15/32 STR I w/ 10@4
Notes: Graphic shows the same roof plan with Zones A and B designated as previously. The sheathing and nailing designations for Zones A and B are provided.

## Slide 89: Diaphragm Design
See example problem for balance of design:
Diaphragm nailing at boundary, continuous edges and other edges
Chord design
Load path detailing
Notes: Other portions of the diaphragm design, as discussed in the published problem and Problem 14.1 need to be completed, including:

## Slide 90: Seismic Force – Alternate Provisions
Diaphragm Design Forces – NEW ALTERNATIVE (Sec. 12.10.3)
Seismic forces in the diaphragm are influenced by both the type of vertical elements and the type of diaphragm, but the Basic Method (Section 12.10.1.1) only recognizes the vertical elements as an influence
Section 12.10.3 takes into account the displacement capacity of the specific diaphragm type used
Diaphragm forces start from near-elastic level, and are divided by Rs diaphragm design force reduction factor, specific to the diaphragm type
Notes: The 2016 edition of ASCE 7 adds a new alternative calculation of diaphragm design forces. The new formulation specifically considerers the ductility and deformation capacity of each type of diaphragm system. The new methodology is explained in detail in Chapter 6 of the NEHRP Design Examples publication. The next few slides will briefly calculate diaphragm design forces using this method.

## Slide 91: Seismic Force – Alternate Provisions
Diaphragm Design Forces – NEW ALTERNATIVE
Fpx = (Cpx/Rs) wpx
Cpx = Cpn (Figure 12.10-2)
Cpn = [(Gm1W0Cs)2 + (Gm2Cs2)2]1/2
For a single story structure with no higher mode behavior, this reduces to:
Cpn = Gm1W0Cs
Already defined are Cs = 0.286 and W0 = 2.5
Notes: The diaphragm force calculation using the alternative methods uses the formula Fpx…
A primary variable in this formulation is Cpn, that calculates the force coefficient for the diaphragm given near elastic behavior, combining the effects of first mode and higher modes.

## Slide 92: Seismic Force – Alternate Provisions
Diaphragm Design Forces – NEW ALTERNATIVE
Cpn = Gm1W0Cs
Gm1 = 1 + (zs/2)(1 – 1/N)
Where
Zs = 1.0 (Sec. 12.10.3.2.1 for not BRB or MRF)
N = number of stories = 1
Gm1 = 1.0
Cpn = 1.0(2.5)(0.286) = 0.715
This is the near-elastic estimated demand, prior to reduction based on diaphragm displacement capacity
Notes: For this one-story structure with only one primary mode in each direction for the primary elements, Cpn simplifies to only the first mode term, and is calculate to be 0.715.

## Slide 93: Seismic Force – Alternate Provisions
Diaphragm Design Forces – NEW ALTERNATIVE
Fpx = (Cpx/Rs) wpx
Cpx = Cpn = 0.715
Rs = Diaphragm design force reduction factor = 3.0 (Table 12.10-1)
Fpx = (0.715/3.0) wpx = 0.238 wpx
Check lower bound for diaphragm forces:
Lower = 0.2 SDS Ie Wroof = 0.286 Wroof – USE LOWER BOUND
Notes: The diaphragm design force reduction factor is determined to be 3.0, applicable to wood structural panel diaphragms. This results in a calculated diaphragm force coefficient of 0.238, which is slightly below the lower bound and the lower bound must be used. In this case with diaphragm design forces from his method and the basic method of Section 12.11.1 match, In other cases they will differ.

## Slide 94: Wall Anchorage Design
For walls anchored to flexible diaphragms, wall anchorage force per ASCE 7-05 Sec. 12.11.2.1 and Eq. 12.11-1 is:
Fp = 0.4SDSkaIeWp
Where
ka = 1.0 + Lf/100 <= 2.0
Lf = diaphragm span = 200 ft
Ka = 1.0 + 200/100 = 3.0, use 2.0 max
Notes: Graphic shows top of masonry shear wall anchored to a wood roof diaphragm.

## Slide 95: Wall Anchorage Design
Fp = 0.4SDSkaIeWp
Where
ka = 2.0
SDS = 1.43
Ie = 1.0
Longitudinal walls:
Wp= 65 psf(16ft)= 1.04 klf
Fp = 0.4(1.43)(2.0)(1.0)1.04 = 1.19 klf
Anchors at 4 ft = 1.19 (4.0)= 4.76 kips
Notes: Graphic shows top of masonry shear wall anchored to a wood roof diaphragm.
As a final step, wall anchorage forces are calculated using the formulation added in ASCE 7-10. The variable Ka is a function of the diaphragm span, increasing anchorage forces for longer spans. Here the wall anchorage force for the longitudinal walls are calculated.

## Slide 96: Wall Anchorage Design
Fp = 0.4SDSkaIeWp
Where
ka = 2.0
SDS = 1.43
Ie = 1.0
Transverse walls:
Wp= 105 psf(16ft)= 1.68 klf
Fp = 0.4(1.43)(2.0)(1.0)1.68 = 1.89 klf
Anchors at 4 ft = 1.89 (4.0)= 7.56 kips
Notes: Graphic shows top of masonry shear wall anchored to a wood roof diaphragm.
Here the same calculation is repeated for heavier transverse walls.

## Slide 97: Wall Anchorage Design
Important items for wall anchorage of concrete and masonry walls SDC C and up (Section 12.11.2.2):
Continuous ties required between diaphragm chords
Subdiaphragms permitted as part of continuous tie system provided subdiaphragm aspect ratio <=2.5
Wall anchor forces required through the entire continuous tie system
Forces multiplied by 1.4 for steel elements of anchorage
Diaphragm wood structural panel sheathing not permitted to be loaded intension to provide continuous tie
Embedded tension straps to be wrapped around or anchored to wall reinforcing
Notes: In addition to design for anchorage forces, there are a series of additional design and detailing requirements imposed on anchorage of concrete and masonry walls to diaphragms. These are discussed in the wood background slide set and the published problem.

## Slide 98: Wall Anchorage Design
The subdiaphragm concept:
Cannot run tension ties at 4 ft on center across entire length of building, so develop into subdiaphragm
Design subdiaphragm for anchorage force level
Subdiaphragm reaction goes to major beam line
Design continuous tie connections across major beam lines for anchorage force level
Notes: Most important of these is the requirements for continuous ties from wall anchors across the entire depth of the diaphragm. Subdiaphragms are commonly used to provide this continuous tie.

## Slide 99: Wall Anchorage Design
The subdiaphragm concept:
Wall anchorage to subdiaphragm at 4 ft.
Glulam beams and connections act as continuous ties
Subdiaphragm approx. 20 ft. x 20 ft.
Notes: Graphic shows plan of roof diaphragm with continuous ties in the longitudinal direction. Wall anchorage is shown with blue lines, sub diaphragms are shown with red boxes, and continuous ties on main beam lines are shown with green lines.
In this plan view of the diaphragm, wall anchors (blue) are extended across the depth of the sub diaphragm (red). The sub diaphragms are design for wall anchorage level forces. The subdiaphragms transfer wall anchorage forces into the major beam lines (green) that act as continuous ties across the diaphragm. This approach satisfies the ASCE 7 requirements. The same type of system must be provided in the perpendicular direction for the longitudinal walls.

## Slide 100: Wood Diaphragm Design Examples
Note: Theoretical part of the diaphragm design is presented in Chapter 6
Instructional Slides developed by S. K. Ghosh, PhD
Notes: Wood diaphragm examples included in Section 6.3 of Chapter 6.

## Slide 101: Section 6.3.1: One-Story Wood Assembly Hall
Notes: This is the first of two example problems that illustrate diaphragm seismic forces and design using both the traditional methods of ASCE 7 Section 12.10, and the alternative provisions of Section 12.10.3. These example problems can be found in Chapter 6 of the NEHRP Example Problems publication.

## Slide 102: Building Configuration
(b)
(a)
Notes: The illustration shows two figures. Figure (a) shows a plan view of a gable roof one story wood assembly hall example building. The building is 90’-0” long and 40’-0” wide with 2’-0” overhang roof on each side. A section view mark for Section A-A is shown parallel to the shorter side of the plan. Figure (b) shows Section A-A, i.e. an elevation view of the building. The building has only one bay with a gable roof which hangs 2’-0” on both sides. Lower edges of the roof are 20’-0” high from the base of the building while the roof ridge is 30’-0” high from the base of the building. Also on this illustration, it’s shown that the aspect ratio is equal to 2.25 and the Ta value is approximately equal to 0.2 second for this building.
This slide shows the plan configuration and elevation view for one story wood assembly hall building shown in the example in Section 6.3.1.

## Slide 103: Building Configuration
Public Assembly Occupancy, Ie = 1.25
Mean roof height = 25 ft
Length = 90 ft
Width = 40 ft
SDS = 1.0, SD1 = 0.60
Wood structural panel diaphragm
Wood structural panel shear walls - R= 6.5, Ω0= 3
Roof + ceiling = 15 psf
Roof only = 8 psf
Wall = 10 psf
Notes: This building is assigned to Risk Category III, as it is a public assembly building with greater than 300 occupant. A seismic importance factor of 1.25 is therefore assigned. Other information of use for this design example includes: (read slide)

## Slide 104: Weight for Seismic Analysis
Seismic weight at roof
  Roof: (15 psf)(40 ft)(90 ft) = 54,000 lbs
  Overhang: (8 psf)(2 ft)(41 ft + 91 ft)(2 sides) = 4,200 lbs
  Side walls: (10 psf)(10 ft)(90 ft)(2 sides) = 18,000 lbs
  End walls: (10 psf)(25 ft/2)(40 ft)(2 sides) = 10,000 lbs
  TOTAL = 86,200 lbs acting at roof
Notes: For this one-story building the seismic weight acting at the roof can be easily calculated as:

## Slide 105: ASCE 7-16 Base Shear
V = CsW = (0.192)(86,200) = 16,550 lbs (12.8-1)
0.481 (12.8-3)
Cs need not exceed:
0.192 (12.8-2)
0.22 sec (12.8-7)
Notes: In order to calculate the base shear, the building period is first calculated using the ASCE 7 approximate period formula. The coefficient Cs is then calculated using both SDS and SD1, and the controlling value of Cs is identified as 0.192, allowing the strength level base shear to be calculated as 16,550 lb.

## Slide 106: Diaphragm Weight
Diaphragm weight, wpx, at the roof:
  Total seismic weight – weight of the walls resisting seismic forces
  = 86,200 – 10,000 = 76,200 lbs (for seismic forces acting in transverse direction)
  = 86,200 – 18,000 = 68,200 lbs (for seismic forces acting in longitudinal direction)
Notes: For design of the diaphragm for seismic forces in the transverse and longitudinal directions, it is permissible to subtract the weight of the walls oriented parallel to the direction of loading, as the weight of these walls is not thought to contribute to the diaphragm forces in that direction. This is almost always done for design of buildings with concrete or masonry walls. It is sometimes done with light-frame walls. The subtraction of the weight of parallel walls is demonstrated in this example…

## Slide 107: ASCE 7-16 Traditional Roof Diaphragm Design Force
Strength Level diaphragm design force:
                (Eq. 12.10-1)
  For a single story building, Fpx = V = 16,550 lbs
  The minimum value of Fpx = 0.2SDSIewpx (Eq. 12.10-2)
  = 0.2(1.0)(1.25)(76,200 lbs) = 19,050 lbs (transverse direction)
  = 0.2(1.0)(1.25)(68,200 lbs) = 17,050 lbs (longitudinal direction)
Notes: For the traditional method of calculating roof diaphragm forces, Equations 12.10-1 and 12.10-2 of ASCE 7 give the following…
In this case the diaphragm design forces in both the longitudinal and transverse directions are controlled by the minimum force level…

## Slide 108: ASCE 7-16 Traditional Roof Diaphragm Design Force
Strength Level diaphragm design force:
  The maximum (need not exceed) value of
  Fpx = 0.4SDSIewpx (Eq. 12.10-3)
  = 0.4(1.0) (1.25)(76,200 lbs) = 38,100 lbs (transverse direction)
  = 0.4(1.0) (1.25)(68,200 lbs) = 34,100 lbs (longitudinal direction)
  Governing diaphragm design forces
    = 19,050 lbs (transverse direction)
  = 17,050 lbs (longitudinal direction)
Notes: The maximum required diaphragm design forces are also checked per ASCE 7 Equation 12.10-3, and the minimum forces are confirmed to govern.

## Slide 109: ASCE 7-16 Traditional Roof Diaphragm Design Force
ASD Level diaphragm design force:
  Fpr = 0.7(19,050) = 13,335 lbs (transverse direction)
  Fpr = 0.7(17,050) = 11,935 lbs (longitudinal direction)
Notes: Although strength design methods are available, seismic design of wood structures most often uses ASD level forces. The controlling strength level diaphragm forces are multiplied by 0.7 to convert to ASD level design forces.

## Slide 110: ASCE 7-16 Alternative/ 2015 NEHRP Provisions
Strength Level diaphragm design force:
Notes: For the alternative diaphragm design provisions of ASCE 7-16, the diaphragm force Fpx is calculated using the diaphragm design acceleration coefficient Cpx, the diaphragm design force reduction factor Rs, and the weight tributary to the diaphragm wpx. To designate load at the roof diaphragm Fpx, Cpx and wpx are shown as Fpr, Cpr and wpr.

## Slide 111: ASCE 7-16 Alternative/2015 NEHRP Provisions Roof Diaphragm Design Force
N =1
zs = 1.0 (for wood shear wall buildings)
Rs = 3.0 (from Table 12.10-1)
Calculating the design acceleration coefficient Cpx in buildings with N ≤ 2
Notes: The figure shows a graph identical to the one on the left-hand side of ASCE 7-16 FIGURE 12.10-2. The graph is developed with hx /hn in the y-axis with ascending gradations from 0 to 1, and in the x-axis with gradations left to right of diaphragm design acceleration coefficient for level x, Cpx from 0 to Cpn. hx /hn is the ratio of the height from the base to level x, hx to the vertical distance from the base to the highest level of the seismic force-resisting system of the structure., hn. This graph is only applicable to building two stories or less in height. The design acceleration coefficient curve begins at Cp0,0 and rises linearly to Cpn,1. Cp0 and Cpn are diaphragm design acceleration coefficient at the structure base and diaphragm design acceleration coefficient at the structural height, hn, respectively.
This slide illustrates the diaphragm design acceleration coefficient Cpx in buildings with number of stories, N, ≤ 2 using Figure 12.10-2 from ASCE 7-16. The diaphragm design acceleration coefficient Cpx is an estimation of the acceleration that would occur in the diaphragm, if the diaphragm were to respond in a near-elastic fashion. The value of Cpx varies from Cp0 at ground level to Cpn at the roof level. In order to calculate Cp0 and Cpn, the variables N and zs need to be defined. In this case the number of stories, N, is one, and zs, a mode shape factor, is 1.0 for wood shear wall buildings. In addition, the diaphragm design force reduction factor, Rs, can be defined as 3.0 from Table 12.10-1. This factor is a measure of the inelastic displacement capacity and ductility of the diaphragm, and serves to reduce the diaphragm design force from what would be required for near-elastic behavior.

## Slide 112: ASCE 7-16 Alternative/ 2015 NEHRP Provisions
Cp0 = 0.4SDSIe = 0.4(1.0)(1.25) = 0.50 (Eq. 12.10-6)
Notes: In order to calculate Cp0 and Cpn, it is necessary to calculate the first mode contribution factor Gamma sub m1, and the higher mode contribution factor Gamma sub m2. These are a function of N and zs, as determined on the previous slide. The first mode participation factor is calculated to be 1, and the higher mode zero, as might be anticipated for a single-story building. Cp0 can then be calculated as 0.50, and Cpn as 0.576.

## Slide 113: ASCE 7-16 Alternative/ 2015 NEHRP Provisions
Strength Level diaphragm design force:
Notes: With these values calculated, the longitudinal and transverse diaphragm seismic forces acting at the roof can be calculated as:

## Slide 114: ASCE 7-16 Alternative/ 2015 NEHRP Provisions
Strength Level diaphragm design force:
But not less than:
Fpr = 0.2SDSIewpx (Eq. 12.10-5)
  = 0.2(1.0)(1.25)(76,200) = 19,050 lbs (transverse direction)
  = 0.2(1.0)(1.25)(68,200) = 17,050 lbs (longitudinal direction)
ASD Level diaphragm design force:
Fpr = 0.7(19,050) = 13,335 lbs (transverse direction)
Fpr = 0.7(17,050) = 11,935 lbs (longitudinal direction)
Notes: As in the traditional method, the minimum diaphragm forces must be checked, and again control as they did in the traditional method.

## Slide 115: ASCE 7-16 Traditional & Alternative/ 2015 NEHRP Provisions
Transverse
wASD= 13,335 lbs/90 ft = 148 plf
Reaction = Shear = 148 plf (90 ft/2) = 6660 lbs
Unit shear, v = Shear/b = 6660/40 ft = 167 plf
Longitudinal
wASD = 11,935 lbs/40 ft = 298 plf
Reaction = Shear = 298 plf(40 ft/2) = 5968 lbs
Unit shear, v = V/b = 5968/90 ft = 66 plf
Sheathing Design per SDPWS - Table 4.2C - Unblocked Diaphragms:
3/8-in. Sheathing with 8d common nails at 6-in. supported edge, 12-in. field
Transverse - Load Case 1 - capacity = 430 plf/2 = 215 plf > 167 plf OK
Longitudinal - Load Case 3 - capacity = 320 plf/2 = 160 plf > 66 plf OK
Notes: For this building, the traditional and alternative diaphragm design forces are the same because both are controlled by the minimum force levels. For this rectangular building, the seismic design force can be treated as a uniform distributed force, w, by dividing by the diaphragm span. Modeling the diaphragm as a simple span beam the diaphragm reaction can be calculated, and the peak unit shear then calculated as the reaction divided by the diaphragm depth in the direction of load. This is seen to generate the very modest design shears of 167 plf transverse and 66 plf longitudinal. The AWC Special Design Provisions for Wind and Seismic (SDPWS) are used to determine diaphragm shear capacity and verify that capacity exceeds demand.

## Slide 116: Section 6.3.2: Three-Story Multi-Family Residential
Notes: The illustration shows two figures. Figure (a) shows a plan view of a gable roof three-story multi-family residential example building. The building is 192’-0” long and 54’-0” wide. The longer side of the building is divided into eight 24’-0” spans. Shear walls parallel to the shorter side of the buildings are located at 0’-0”, 48’-0”, 96’-0”, 144’-0”, and 192’-0” along the longer side of the building spanning over the full 54’-0”-long side of the building. The shorter side of the building is divided into three spans; two 24’-0” spans on sides and a 6’-0” span in between. Shear walls parallel to the longer side of the buildings are located at 0’-0”, 24’-0”, 30’-0”, and 54’-0” along the shorter side of the building spanning over the full 192’-0”-long side of the building. Figure (b) shows an elevation view of the building which represents a cut parallel to the shorter side of the building. The building has three bays and three stories. All stories are 9’-0” high and the roof ridge is also 9’-0” higher than the third story ceiling (36’-0” high from the base of the building). The gable roof has no overhand on any side.

## Slide 117: Building Configuration
(a)
(b)
Notes: The illustration shows two figures. Figure (a) shows a plan view of a gable roof three-story multi-family residential example building. The building is 192’-0” long and 54’-0” wide. The longer side of the building is divided into eight 24’-0” spans. Shear walls parallel to the shorter side of the buildings are located at 0’-0”, 48’-0”, 96’-0”, 144’-0”, and 192’-0” along the longer side of the building spanning over the full 54’-0”-long side of the building. The shorter side of the building is divided into three spans; two 24’-0” spans on sides and a 6’-0” span in between. Shear walls parallel to the longer side of the buildings are located at 0’-0”, 24’-0”, 30’-0”, and 54’-0” along the shorter side of the building spanning over the full 192’-0”-long side of the building. Figure (b) shows an elevation view of the building which represents a cut parallel to the shorter side of the building. The building has three bays and three stories. All stories are 9’-0” high and the roof ridge is also 9’-0” higher than the third story ceiling (36’-0” high from the base of the building). The gable roof has no overhand on any side.
This slide shows the plan configuration and elevation view for three-story multi-family residential the example building.

## Slide 118: Building Configuration
Standard Occupancy, Ie = 1.0
Mean roof height = 31 ft
Length = 192 ft
Width = 54 ft
SDS = 1.0, SD1 = 0.60
Wood structural panel diaphragm
Wood structural panel shear walls - R= 6.5, Ω0= 3
Roof + ceiling = 15 psf
Floor + ceiling = 10 psf
Exterior wall = 15 psf
Interior wall = 10 psf
Notes: Some of the information of interest for this standard-occupancy (Risk Category II) structure is:

## Slide 119: Weight for Seismic Analysis
Seismic weight at roof
  Roof: (15 psf)(54 ft)(192 ft) = 155.5 kips
  Longitudinal exterior wall: (15 psf)(192 ft)(4 ft)(2 sides) = 23.0 kips
  Transverse exterior wall: (15 psf)(54 ft)(4 ft)(2 sides) = 6.5 kips
  Longitudinal interior wall: (10 psf)(192 ft)(4 ft.(2 lines) = 15.4 kips
  Transverse interior wall: (10 psf)(24 ft)(4 ft)(14 lines) = 13.4 kips
  TOTAL = 214 kips acting at roof
Notes: We will first calculate the seismic weight tributary to each of the three above grade levels, starting at the roof:

## Slide 120: Weight for Seismic Analysis
Seismic weight at 2nd and 3rd floors
  Floor: (10 psf)(54 ft)(192 ft) = 103.7 kips
  Longitudinal exterior wall: (15 psf)(192 ft)(8 ft)(2 sides) = 46.0 kips
  Transverse exterior wall: (15 psf)(54 ft)(8 ft)(2 sides) = 13.0 kips
  Longitudinal interior wall: (10 psf)(192 ft)(8 ft)(2 lines) = 30.8 kips
  Transverse interior wall: (10 psf)(24 ft)(8 ft)(14 lines) = 26.8 kips
  TOTAL = 220 kips acting at floors
  Seismic weight TOTAL = 214+220+220 = 654 kips
Notes: Seismic weights acting at the second and third floors will essentially be the same:
And the total seismic weight for calculation of the base shear is summed to be 654 kips.

## Slide 121: ASCE 7-16 Base Shear
V = CsW = (0.154)(654) = 101 kips (12.8-1)
0.355 (12.8-3)
Cs need not exceed:
0.154 (12.8-2)
0.26 sec (12.8-7)
Notes: As in the previous example, the code approximate period and coefficient Cs are calculated, giving a base shear of 101 kips.

## Slide 122: Diaphragm Weights
Diaphragm weight, wpx, at the roof:
  Total seismic weight – weight of the walls resisting seismic forces
  = 214 – 6.5 – 13.4 = 194.1 kips (for seismic forces acting in transverse direction)
  = 214 – 23 – 15.4 = 175.6 kips (for seismic forces acting in longitudinal direction)
Diaphragm weight, wpx, at the 2nd and 3rd floors:
  Total seismic weight – weight of the walls resisting seismic forces
  = 220 – 13 – 26.8 = 180.2 kips (for seismic forces acting in transverse direction)
  = 220 – 46 – 30.8 = 143.2 kips (for seismic forces acting in longitudinal direction)
Notes: While it is possible when calculating diaphragm design forces to subtract the weight of walls parallel to the direction of load, this is seldom done in design practice for this type of building. This is partially because it often only makes a modest reduction in design forces, and because the resulting diaphragm shears are so low that minimum construction requirements govern. The subtraction of parallel wall weight is illustrated for this building, and can be seen to reduce the total seismic weight at the level between 10 and 35 percent. To match the FEMA P-1051 publication, reduced weights will be used for the balance of the example, resulting in different transverse and longitudinal forces at each level.

## Slide 123: ASCE 7-16 Traditional Roof Diaphragm Design Force
Vertical distribution of seismic base shear:
  The lateral seismic force at any level is determined as
        Fx = CvxV (Eq. 12.8-11)
  Where
                (Eq. 12.8-12)
For T ≤ 0.5 sec, k = 1.0
Notes: The vertical distribution of base shear will be calculated in accordance with ASCE 7 Equation 12.8-11 and 12.8-12.

## Slide 124: ASCE 7-16 Traditional Roof Diaphragm Design Force
Level x | wx (kips) | hx (ft) | wxhxk (ft-kips) |  | Cvx | Fx (kips) | 
Roof 3rd Fl 2nd Fl ∑ | 214 220 220 654 | 31 18 9 | 6634 3960 1980 12,574 |  | 0.53 0.31 0.16 1.00 | 53.4 31.4 16.2 101 | 
1.0 kip = 4.45 kN, 1.0 ft = 0.3048 m, 1.0 ft-kip = 1.36 kN-m |  |  |  |  |  |  | 
Vertical distribution of seismic base shear:
Notes: The resulting distribution of seismic force is:

## Slide 125: ASCE 7-16 Traditional Roof Diaphragm Design Force
Strength level diaphragm design force:
  Diaphragm design force is given by the larger of Fx determined above and Fpx determined below.
  (Eq. 12.10-1)
Notes: With this information, the vertical distribution of diaphragm design forces can be calculated as a function of weight tributary to the diaphragm wpx.

## Slide 126: ASCE 7-16 Traditional Roof Diaphragm Design Force
Level | wi (kips) | (kips) | Fi (kips) | (kips) | wpx (kips) |  | Fpx (kips) | 
 |  |  |  |  | Trans. | Long. | Trans. | Long.
Roof | 214 | 214 | 53.4 | 53.4 | 194.1 | 175.6 | 48.4 | 43.8
2 | 220 | 434 | 31.4 | 84.8 | 180.2 | 143.2 | 35.2 | 28.0
1 | 220 | 654 | 16.2 | 101 | 180.2 | 143.2 | 27.8 | 22.0
1.0 kip = 4.45 kN. |  |  |  |  |  |  |  | 
Strength level diaphragm design force:
Notes: The table can then be supplemented with diaphragm design forces at the second and third floor levels and roof:

## Slide 127: ASCE 7-16 Traditional Roof Diaphragm Design Force
Strength level diaphragm design force:
  Fpx at roof cannot be less than:
  Fpr = 0.2SDSIewpr (Eq. 12.10-2)
    = 0.2(1.0)(1.0)(194.1) = 38.8 kips (transverse direction)
    = 0.2(1.0)(1.0)(175.6) = 35.1 kips (longitudinal direction)
  Fpx at floor levels cannot be less than:
  Fpx = 0.2SDSIewpx (Eq. 12.10-2)
    = 0.2(1.0)(1.0)(180.2) = 36 kips (transverse direction)
    = 0.2(1.0)(1.0)(143.2) = 28.6 kips (longitudinal direction)
Notes: Again, the minimum diaphragm design force levels must be checked.

## Slide 128: ASCE 7-16 Traditional Roof Diaphragm Design Force
Strength level diaphragm design force:
  Fpx at roof need not exceed:
  Fpr = 0.4SDSIewpr (Eq. 12.10-3)
    = 0.4(1.0)(1.0)(194.1) = 77.6 kips (transverse direction)
    = 0.4(1.0)(1.0)(175.6) = 70.2 kips (longitudinal direction)
  Fpx at floor levels need not exceed:
  Fpx = 0.4SDSIewpx (Eq. 12.10-3)
    = 0.4(1.0)(1.0)(180.2) = 72 kips (transverse direction)
    = 0.4(1.0)(1.0)(143.2) = 57.3 kips (longitudinal direction)
Notes: And the maximum levels

## Slide 129: ASCE 7-16 Traditional Roof Diaphragm Design Force
 | Transverse Direction |  | Longitudinal Direction | 
 | Strength Level | ASD Level | Strength Level | ASD Level
Roof | 53.4 | 37.4 | 53.4 | 37.4
3rd Floor | 36.0 | 25.2 | 31.4 | 22.0
2nd Floor | 36.0 | 25.2 | 28.6 | 20.0
ASD Level diaphragm design force:
  Fpx,ASD = 0.7(Fpx,Strength)
Summary of diaphragm design force (kips):
Notes: The force calculated from the vertical distribution controls at the roof level. For both the second and third floor levels, the minimum design forces control. These forces are multiplied by 0.7 to convert to ASD force level for design purposes.

## Slide 130: ASCE 7-16 Traditional Roof Diaphragm Design Force
Transverse - Roof
wASD= 37,400 lbs/192 ft = 195 plf
Reaction = Shear = 195plf (48 ft/2) = 4680 lbs
Unit Shear, v = Shear/b = 4680/54 ft = 87 plf
Longitudinal - Roof
wASD = 37,400 lbs/54 ft = 693 plf
Reaction = Shear = 693 plf(24 ft/2) = 8316 lbs
Unit Shear, v = V/b = 8316/192 ft = 43 plf
Notes: As in the earlier design example, the seismic force at the roof is divided by the span length to calculated the uniform load, w. Using a simple-span beam assumption for the diaphragm spanning between designated shear wall (see plan), the diaphragm reactions are calculated, and they are then divided by the diaphragm depth parallel to the load to determine the unit shear. The unit shears in the roof diaphragm are seen to be very small. Unit shears for the floor diaphragms are calculated in the same way.

## Slide 131: ASCE 7-16 Traditional Roof Diaphragm Design Force
Sheathing Design per SDPWS - Table 4.2C - Unblocked Diaphragms:
5/16-in. Sheathing with 6d common nails at 6-in. supported edge, 12-in. field
Transverse - Load Case 1 - capacity = 300 plf/2 = 150 plf > 87 plf OK
Longitudinal - Load Case 3 - capacity = 220 plf/2 = 110 plf > 43 plf OK
Same sheathing OK for second and third floors by inspection, thicker than 5/16-in. sheathing will be used based on gravity load requirements.
Notes: As in the earlier example, the unit shear demands are checked against unit shear capacities per the AWC SDPWS standard. With the very low unit shear demands, unblocked wood structural panel diaphragms provide more than adequate capacity.

## Slide 132: ASCE 7-16 Alternative/ 2015 NEHRP Provisions
Strength Level diaphragm design force:
Notes: Diaphragm design forces for this building will now be calculated using the alternate diaphragm provisions of ASCE 7 -16 Section 12.10.3. Once again, for the alternative diaphragm design provisions of ASCE 7-16, the diaphragm force Fpx is calculated using the diaphragm design acceleration coefficient Cpx, the diaphragm design force reduction factor Rs, and the weight tributary to the diaphragm wpx.

## Slide 133: ASCE 7-16 Alternative Diaphragm Design Force
N = 3
zs = 1.0 (for wood shear wall buildings)
Rs = 3.0 (from Table 12.10-1)
Calculating the design acceleration coefficient Cpx in buildings with N ≥ 3
Notes: The figure shows a graph identical to the one on the right-hand side of ASCE 7-16 FIGURE 12.10-2. The graph is developed with hx /hn in the y-axis with ascending gradations from 0 to 1, and in the x-axis with gradations left to right of diaphragm design acceleration coefficient for level x, Cpx from 0 to Cpn. hx /hn is the ratio of the height from the base to level x, hx to the vertical distance from the base to the highest level of the seismic force-resisting system of the structure., hn. This graph is only applicable to building three stories or more in height. The design acceleration coefficient curve begins at Cp0,0 and rises linearly to Cpi,0.8, then rises in a straight line from Cpi,0.8 to Cpn,1. Cp0, Cpi, and Cpn are diaphragm design acceleration coefficient at the structure base, diaphragm design acceleration coefficient at 80 percent of the structural height above the base, hn, and diaphragm design acceleration coefficient at the structural height, hn, respectively.
This slide illustrates calculating the design acceleration coefficient Cpx in buildings with number of stories, N, ≥ 3. using Figure 12.10-2 from ASCE 7-16. The diaphragm design acceleration coefficient Cpx is an estimation of the acceleration that would occur in the diaphragm, if the diaphragm were to respond in a near-elastic fashion. The value of Cpx varies from Cp0 at ground level to Cpi at 80% of the structure height, and then transitioning to Cpn at the roof level. In order to calculate Cp0 , Cpi. and Cpn, the variables N and zs need to be defined. In this case the number of stories, N, is 3, and zs, a mode shape factor, is 1.0 for wood shear wall buildings. In addition, the diaphragm design force reduction factor, Rs, can be defined as 3.0 from Table 12.10.3.5-1. This factor is a measure of the inelastic displacement capacity and ductility of the diaphragm, and serves to reduce the diaphragm design force from what would be required for near-elastic behavior.

## Slide 134: ASCE 7-16 Alternative Diaphragm Design Force
Cp0 = 0.4SDSIe = 0.4(1.0)(1.00) = 0.40 (Eq. 12.10-6)
Cpi = 0.8Cp0 = 0.8(0.40) = 0.32 (Eq. 12.10-8)
Notes: As in the previous example, in order to calculate Cp0, Cpi, and Cpn, it is necessary to calculate the first mode contribution factor Gamma sub m1, and the higher mode contribution factor Gamma sub m2. These are a function of N and zs, as determined on the previous slide. The first mode participation factor is calculated to be 1.33, and the higher mode 0.4. These values show the start of higher mode effects in this three-story building, where there was no higher mode contribution for the single-story building. Cp0 can then be calculated as 0.40. There are two equations for calculation of Cpi , the larger value of the two is used. The first is 0.8 Cp0 = 0.32.

## Slide 135: ASCE 7-16 Alternative Diaphragm Design Force
Cpi = 0.9Γm1Ω0Cs = 0.9(1.33)(3.0)(0.154) = 0.55 (Eq. 12.10-9)
Notes: The second equation for Cpi gives a value of 0.55, and this larger value controls. Next, Cs2 is assigned as the smallest value from the three equations provided, resulting in a value of 0.7. with these variables defined, Cpn can be calculated.

## Slide 136: ASCE 7-16 Alternative Diaphragm Design Force
But not less than:
Fpr = 0.2SDSIewpr (Eq. 12.10-5)
  = 0.2(1.0)(1.0)(194.1) = 38.8 kips (transverse direction)
  = 0.2(1.0)(1.0)(175.6) = 35.1 kips (longitudinal direction
Strength level diaphragm design force:
Notes: Returning to our primary equation, Cpr shows the estimated acceleration level at the roof with near-elastic diaphragm behavior, and Rs of three accounts for reduction of the design force based on the significant displacement capacity of the wood structural panel diaphragm. This results in a strength level seismic design force of 48.5 kips at the roof level. This is greater than the minimum force level and controls.

## Slide 137: ASCE 7-16 Alternative Diaphragm Design Force
But not less than:
Fp3 = 0.2SDSIewp3 (Eq. 12.10-5)
  = 0.2(1.0)(1.0)(180.2) = 36 kips (transverse direction)
  = 0.2(1.0)(1.0)(143.2) = 28.6 kips (longitudinal direction)
Strength level diaphragm design force:
Notes: Similarly, at the third floor level, Cp3 represents the anticipated acceleration level at near-elastic behavior. With the second floor occurring at 18 feet above the base, Cp3 is calculated by interpolation between Cp0 and Cpi. With Cp0 of 0.40 at the base and Cpi of 0.55 at 0.8(31)=25 feet above the base, Cp3 is calculated to be 0.51. Again, this strength force needs to be checked against the minimum diaphragm design level, which in this case is found to control.

## Slide 138: ASCE 7-16 Alternative Diaphragm Design Force
But not less than:
Fp2 = 0.2SDSIewp2 (Eq. 12.10-5)
  = 0.2(1.0)(1.0)(180.2) = 36 kips (transverse direction)
  = 0.2(1.0)(1.0)(143.2) = 28.6 kips (longitudinal direction)
Strength level diaphragm design force:
Notes: Similarly by interpolation, Cp2 is determined to be 0.46, resulting in Fp2 of 29.3. The minimum diaphragm design force controls.

## Slide 139: ASCE 7-16 Alternative Diaphragm Design Force
 | Transverse Direction |  | Longitudinal Direction | 
 | Strength Level | ASD Level | Strength Level | ASD Level
Roof | 44 | 30.8 | 39.8 | 27.9
3rd Floor | 36 | 25.2 | 28.6 | 20.0
2nd Floor | 36 | 25.2 | 28.6 | 20.0
ASD level diaphragm design force:
  Fpx,ASD = 0.7(Fpx,Strength)
Summary of diaphragm design force (kips):
Notes: The longitudinal and transverse diaphragm seismic design forces are summarized in this table for convenience.

## Slide 140: ASCE 7-16 Alternative Diaphragm Design Force
Transverse - Roof
wASD= 30,800 lbs/192 ft = 160 plf
Reaction = Shear = 160plf (48 ft/2) = 3840 lbs
Unit Shear, v = Shear/b = 3840/54 ft = 71 plf
Longitudinal - Roof
wASD = 27,900 lbs/54 ft = 517 plf
Reaction = Shear = 517 plf(24 ft/2) = 6204 lbs
Unit Shear, v = Shear/b = 6204/192 ft = 32 plf
Notes: Again the seismic force at the roof is divided by the span length to calculated the uniform load, w. Using a simple-span beam assumption for the diaphragm spanning between designated shear wall (see plan), the diaphragm reactions are calculated, and they are then divided by the diaphragm depth parallel to the load to determine the unit shear. The unit shears in the roof diaphragm are again seen to be very small. Unit shears for the floor diaphragms are calculated in the same way.

## Slide 141: ASCE 7-16 Alternative Diaphragm Design Force
Sheathing Design per SDPWS - Table 4.2C - Unblocked Diaphragms:
5/16-in. Sheathing with 6d common nails at 6-in. supported edge, 12-in. field
Transverse - Load Case 1 - capacity = 300 plf/2 = 150 plf > 71 plf OK
Longitudinal - Load Case 3 - capacity = 220 plf/2 = 110 plf > 32 plf OK
Same sheathing OK for second and third floors by inspection, thicker than 5/16-in. sheathing will be used based on gravity load requirements.
Notes: The unit shear demands are again checked against capacities from the AWC SDPWS standard, and shown to be ok. This process is repeated for the floor diaphragms.

## Slide 142: 2015 NEHRP Provisions Diaphragm Design Force
Calculating the design acceleration coefficient Cpx in buildings with N ≥ 3
N = 3
zs = 1.0
Rs = 3.0 (from Table 12.10-1)
Notes: The figure shows a graph identical to the one on the right-hand side of PROVISIONS FIGURE 12.10-2. The graph is developed with hx /hn in the y-axis with ascending gradations from 0 to 1, and in the x-axis with gradations left to right of diaphragm design acceleration coefficient for level x, Cpx from 0 to Cpn. hx /hn is the ratio of the height from the base to level x, hx to the vertical distance from the base to the highest level of the seismic force-resisting system of the structure., hn. This graph is only applicable to building three stories or more in height. The design acceleration coefficient curve begins at Cp0,0 and rises straight up to Cp0,0.8, then rises linearly from Cp0,0.8 to Cpn,1. Cp0, Cpi, and Cpn are diaphragm design acceleration coefficient at the structure base, diaphragm design acceleration coefficient at 80 percent of the structural height above the base, hn, and diaphragm design acceleration coefficient at the structural height, hn, respectively.
This slide illustrates calculation of the design acceleration coefficient Cpx in buildings with N ≥ 3 in accordance with the 2018 NEHRP Provisions. The vertical distribution of forces specified in the NEHRP Provisions for structures of three stories or greater is different from the distribution eventually adopted by ASCE 7. As seen in this figure the coefficient Cp0 is used from the structure base up to 80 percent of the structure height, and the coefficient Cpi is not used.

## Slide 143: 2015 NEHRP Provisions Diaphragm Design Force
(12.10-9)
(12.10-8)
(12.10-12)
(12.10-11)
Notes: These calculations are repeated for the NEHRP calculation, giving the same values as previously.

## Slide 144: 2015 NEHRP Provisions Diaphragm Design Force
(12.10-7)
(12.10-6)
(12.10-10a)
Notes: These calculations are also repeated for the NEHRP calculation, also giving the same values as previously.

## Slide 145: 2015 NEHRP Provisions Diaphragm Design Force
Roof - Strength Level:
(12.10-4)
But not less than:
Fpr = 0.2SDSIewpr = 0.2(1.0)(1.0)(194.1) = 38.8 kips (12.10-5)
Roof - ASD Level:
Fpr = 0.7(44 kips) = 30.8 kips
Notes: Using the NEHRP formulation, seismic design forces at the roof are exactly the same as ASCE 7

## Slide 146: 2015 NEHRP Provisions Diaphragm Design Force
3rd Floor - Strength Level:
Cp3 = 0.40
(12.10-4)
But not less than:
Fp3 = 0.2SDSIewp3 = 0.2(1.0)(1.0)(180.2) = 36 kips (12.10-5)
3rd Floor - ASD Level:
Fp3 = 0.7(36.0 kips) = 25.2 kips
Notes: At the third floor level, Cp3 has decreased from 0.51 to 0.40, however the diaphragm design force is not affected since it is controlled by the minimum design force.

## Slide 147: 2015 NEHRP Provisions Diaphragm Design Force
2nd Floor - Strength Level:
Cp2 = 0.40
(12.10-4)
But not less than:
Fp2 = 0.2SDSIewp2 = 0.2(1.0)(1.0)(180.2) = 36 kips (12.10-5)
2nd Floor - ASD Level:
Fp2 = 0.7(36.0 kips) = 25.2 kips
Notes: Similarly at the second floor level, Cp2 is reduced from 0.46 to 0.40, but the design force remains the same because the minimum design forces controls.

## Slide 148: Comparison Summary
Level | ASCE 7-16 | 2015 NEHRP Provisions
Roof | 30,800 | 30,800
3rd | 25,200 | 25,200
2nd | 25,200 | 25,200
ASD Level Fpx Forces (lbs.)
Notes: In summary, the controlling diaphragm design forces from the NEHRP and ASCE 7 are the same at all levels. Note that this will be true for many buildings, but not in all circumstances.

## Slide 149: Questions?

## Slide 150: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.