## Slide 1: Design for Nonstructural Components Background and Fundamentals Robert Bachman, S.E., John Gillengerten, S.E., and Susan Dowty, S.E.
Disclaimer
18
Notes: Title slide, consisting of an image of the cover of the data disk containing the 2015 NEHRP Recommended Seismic Provisions, and the names of the authors of the 2015 Design Provisions Examples.
This unit covers background and fundamental information on the subject of earthquake resistant design of nonstructural components. The images come from a variety of FEMA publications, especially FEMA E-74, Reducing the Risks of Nonstructural Earthquake Damage – A Practical Guide.
508 tag: an image of the cover of the data disk containing the 2015 NEHRP Recommended Seismic Provisions

## Slide 2: Nonstructural Components
Nonstructural components include equipment, distribution systems such as piping, ducts, and electrical raceways, and architectural components
These items make up the majority of the replacement value of most buildings.
Notes: An image of a suspended acoustical ceiling system missing some of its’ tiles.
The consists of text on the left and an image of a suspended acoustical ceiling system missing some of its’ tiles. The slide describes what constitutes nonstructural components and that the they make up most of the replacement values of a building.
Architectural, mechanical and electrical components are commonly referred to as “nonstructural components.”

## Slide 3: Approach to Nonstructural Components
Building codes have long history of seismic requirements for nonstructural components
Nonstructural components are grouped in broad categories for seismic design based on:
  Function
  Behavior under seismic loading
Requirements vary with the ground motion intensity
Components serving essential functions are subject to more stringent requirements
Notes: An image of a suspended mechanical unit that fell to the floor in an earthquake.
The slide, consists text on the left and an image of a suspended mechanical unit that fell to the floor in an earthquake. The slide describes the way nonstructural components classified and factors that influence the seismic requirements.
The earliest code requirements for nonstructural components are found in an Appendix of the 1927 Uniform Building Code. The requirements have evolved over time to reflect changes in the nonstructural systems found in buildings and advances in earthquake engineering.

## Slide 4: Nonstructural Design Requirements
2015 NEHRP Recommended Provisions:
Part 1, Provisions
ASCE/SEI 7-10 including Supplement 1, Minimum Design Loads for Buildings and Other Structures including Supplement 1, Chapters 11-23 adopted by reference
In ASCE/SEI 7-10
Chapter 13 – Seismic Design Requirements for Nonstructural Components
Section 12.11.2 Anchorage of Concrete and Masonry Structural Walls
Significant revisions in ASCE/SEI 7-16 will be noted
Notes: ASCE 7-10 including Supplement 1 are incorporated in the 2015 NEHRP Recommended Provisions by reference.
Chapter 13 of ASCE/SEI 7-10 also references other Chapters of ASCE 7 for its provisions. For example, it references Chapter 11 for ground motions. Of special interest is the reference to Section 12.11.2 Anchorage of Concrete and Masonry Structural Walls. It references Section 12.11.2 for the application connection requirements of nonstructural concrete and masonry walls for buildings with flexible diaphragms.
The reason Section 12.11.2 is listed is because code users are often confused about what design forces should be applied to structural walls out-of-plane and this is the section that Ch. 13 refers the user to for concrete and masonry walls.
All equation numbers in this presentation are from ASCE/SEI 7-10 including Supplement 1, unless otherwise noted

## Slide 5: Nonstructural Performance Goals
Performance goals for nonstructural components are not explicitly defined
ASCE/SEI 7-10 commentary provides expectations of the anticipated behavior for non-critical components
Notes: an image of a damaged interior office space.
The slide consists text on the left and an image of a damaged interior office space. The slide discusses performance goals of nonstructural components.

## Slide 6: Performance Expectations
ASCE/SEI 7-10 Performance expectations for non-critical component performance for three levels of ground shaking
  Minor earthquake ground motions—minimal damage not likely to affect functionality;
  Moderate earthquake ground motions—some damage that may affect functionality; and
  Design Earthquake ground motions—major damage but significant falling hazards are avoided; likely loss of functionality
Notes: The slide shows the performance expectations for nonstructural components from the ASCE/SEI 7-10 commentary. Only the Design Earthquake shaking level is defined, “minor” and “moderate earthquakes” are qualitative phrases. These expectations are for nonessential components (Ip=1.0).

## Slide 7: Function and Economic Loss
For nonessential components the design provisions focus on reducing the risk to life safety
In some cases the provisions protect functionality and limit economic losses
  Non-critical equipment in mechanical rooms unlikely to topple still requires anchorage although they pose minimal risk to life safety
  The flexible connections between unbraced piping and non-critical equipment serve mainly to reduce the likelihood of leakage
Notes: The slide discuss the impact of the nonstructural design requirements on functionality and economic loss. There are seismic requirements that in some cases are not directly related to protection of life safety.

## Slide 8: ASCE/SEI 7-10 Chapter 13 Organization
ASCE/SEI 7-10 Section | Title
13.1 | General
13.2 | General Design Requirements
13.3 | Seismic Demands on Nonstructural Components
13.4 | Nonstructural Component Anchorage
13.5 | Architectural Component
13.6 | Mechanical and Electrical Components
Notes: This slide provides an abbreviated table of contents of ASCE/SEI 7-10 Chapter 13.

## Slide 9: ASCE/SEI 7-10 Chapter 13 - Organization
Section 13.1: Information on the applicability of the nonstructural design provisions
Section 13.2: General information on determination of:
  Importance of the component or system,
  Methods for establishing the adequacy of the component for seismic forces,
  Certification requirements for items identified as critical to life safety or function
Notes: This slide provides additional detail on the contents of Sections 13.1 and 13.2 of ASCE/SEI 7-10.

## Slide 10: ASCE/SEI 7-10 Chapter 13 - Organization
Section 13.3: Procedures for determining the acceleration and displacement demands on nonstructural components
Section 13.4: Design considerations for attachment of nonstructural components to the structure
Sections 13.5 and 13.6: Detailed design considerations for architectural components, and mechanical and electrical components, respectively
Notes: This slide provides additional detail on the contents of Sections 13.3 through 13.6 of ASCE/SEI 7-10.

## Slide 11: Nonstructural Importance Factor - Ip
ASCE/SEI 7-10 Nonstructural Components are assigned a Component Importance Factor, Ip
The values of Ip is either 1.0 or 1.5
In ASCE/SEI 7-10, the value of Ip is based on
1. Requirement of the component to function after a DBE or
2. Occupancy Category of the structure or facility
In ASCE/SEI 7-10, nonstructural components/systems which are assigned an Ip = 1.5 are called Designated Seismic Systems.
Notes: This slide provides a discussion of the component importance factor, Ip. Nonessential components are assigned an importance factor equal to 1.0. Components with an importance factor of 1.5 must meet more stringent requirements.
For Ip = 1.0, the following behaviors are anticipated:
Minor earthquake ground motions – minimal damage; not likely to affect functionality.
Moderate earthquake ground motions – some damage that may affect functionality
Design earthquake ground motions – major damage but significant falling hazards are avoided; likely loss of functionality
Components with Ip = 1.5, they are expected to remain in place, sustain limited damage, and, when necessary, function following design earthquake level motions.

## Slide 12: Limits of Applicability
ASCE/SEI 7-10 Nonstructural provisions apply throughout the United States
Some components are exempt from the requirements of Chapter 13:
  All components in structures assigned to SDC A
  MEP components in structures assigned to SDC B
  Architectural components in structures assigned to SDC B if Ip = 1.0 (except certain parapets)
  MEP components in structures assigned to SDC C if Ip = 1.0
  Furniture and light or temporary items
  Small piping and ductwork in structures assigned to SDC D-F
Notes: This slide discuss limits on the application of the nonstructural seismic design requirements. Some nonstructural components are exempt from the requirements, depending on the seismic hazard level, component type, and size.
Chapter 13 does not apply to SDC A due to its very low level of seismic hazard; see ASCE/SEI 7-10 Section 11.7 and Section C11.7.
The exceptions applicable to other seismic design categories are based on SDC and Importance Factor.
With the exception of parapets supported by bearing walls or shear walls, all components in SDC B are exempt due to the low level of seismic risk. Parapets are not exempt because experience has shown these items can fail and pose a significant falling hazard even at low shaking levels.
Mechanical and electrical components in Seismic Design Category C with an importance factor (Ip) equal to 1.0 are exempt because they are subject to low levels of seismic hazard, they do not contain hazardous substances, and their function is not required to maintain life safety following an earthquake. Note that fire sprinkler piping is not exempt because it has an importance factor of 1.5
Small components with Ip in SDC D, E, and F also are exempt since they do not contain hazardous substances and are not large enough to pose a life-safety hazard if they fall, slide, or topple. Failures of unbraced distribution systems at or near the point of connection to nonstructural components have been observed in past earthquakes. For this reason, flexible connections such as expansion loops, braided hose, or expansion joints are required to allow for the larger relative displacements associated with unbraced components. Note that the stiffness of flexible connections may be sensitive to internal pressure and length of the connection.

## Slide 13: Nonstructural Demands
Seismic forces for design are computed considering variation of acceleration with relative height within the structure, and reduction in design force based upon estimated ductility of the component or its attachment
Procedures for evaluating nonstructural components subject to imposed deformations, such as story drift are provided
The seismic force demands tend to control the design for vibration-isolated or heavy components
Deformations control the design of elements that are continuous through multiple levels of a structure or across expansion joints between adjacent structures, such as cladding or piping
Notes: In this slide, the seismic demands on nonstructural components are summarized. Nonstructural components may be either acceleration or drift controlled, depending on the nature of the component. The seismic force calculations consider location of the component in the structure, as well as the estimated component ductility..
There are two types of demands on nonstructural components: forces and relative displacements between points of attachment. The forces are associated with the acceleration response of the structure at the points of attachment. Nonstructural demands are based on design earthquake level motions and MCE motions are not considered.

## Slide 14: Nonstructural Force Demands
Several different methods are available for calculating the force demands on nonstructural components
Several new methods for determining force demands were added in the ASCE/SEI 7-16
Equivalent Static Forces – Fp Equations
  Fp Equation 13.3-1 is independent of building structural properties
  Fp Equation 13.3-4 is dependent on building structural properties.
Both Fp equations are subject to the maximum and minimum values of Fp provided in Equations 13.3-2 and 13.3-3.
Notes: There are several different formulas for determining the acceleration demands on nonstructural components: forces and relative displacements between points of attachment. The forces are associated with the acceleration response of the structure at the points of attachment. Nonstructural demands are based on design earthquake level motions and MCE motions are not considered.
Equation 13.3-1 is intentionally conservative to cover the wide range of building structural systems, heights, etc.

## Slide 15: Nonstructural Force Demand
  Equation 13.3-3
  Equation 13.3-2
Fp (max) = 1.6 SDS Ip Wp
Fp (min) = 0.3 SDS Ip Wp
Equation 13.3-1
Notes: This slide presents Equation 13.3-1, the basic equation for seismic forces on nonstructural components. Equation 13.3-1 is intentionally conservative to cover the wide range of building structural systems, heights, etc. Fp forces are typically larger than those used for the design of the building. The minimum and maximum forces are given in Equations 13.3-2 and 13.3-3, respectively.

## Slide 16: Nonstructural Component Factors
ASCE/SEI 7-10 has ap and Rp factors assigned in tables that are used in Fp equation.
ap values range from 1.0 to 2.5 and values of ap can be taken as less than 2.5 based on dynamic analysis.
Rp values range from 1.0 to 12.0.
Importance factor Ip values are 1.0 or 1.5.
Wp is the component operating weight.
z is the height in structure of point of attachment of component with respect to the base.
h = average roof height of structure with respect to the base
Notes: The variables in the seismic force equations are discussed in the slide.
ap values represent the dynamic amplification of component response as a function of the fundamental periods of the structure and component. ap values are based on component behavior that is assumed to be either rigid or flexible. Where the fundamental period of the component is less than 0.06 seconds, dynamic amplification is not expected and the component is considered rigid and ap is equal to 1.
Rp values represent the energy absorption capability of a component and its attachments and is dependent on both overstrength and deformability.

## Slide 17: ap and Rp values for Selected Architectural Components
Architectural Component | ap | Rp
Cantilever Parapets | 2.5 | 2.5
Exterior Nonstructural Walls and Elements (e.g. precast cladding) | 1 | 2.5
Partitions | 1 | 2.5
Ceilings | 1 | 2.5
Penthouses (not an extension) | 2.5 | 3.5
Signs and Billboards | 2.5 | 2.5
Access Floors (special) | 1 | 2.5
Storage Cabinets | 1 | 2.5
Notes: A table containing a partial list of ap and Rp values for architectural nonstructural component values from ASCE/SEI 7-10 Table 13.5-1 is presented.

## Slide 18: Component Amplification Factor
The component amplification factor, ap, represents the dynamic amplification of the component relative to the maximum acceleration of the component support point(s).
This amplification is a function of the fundamental period of the component, Tp and the fundamental period of the supporting structure, T.
Notes: 508A notes: This slide describes the component amplification factor, ap,. Values for ap are tabulated for each component based on the expectation that the component will behave in either a rigid or a flexible manner.
For simplicity, a step function increase based on input motion amplifications is provided to help distinguish between rigid and flexible behavior. If the fundamental period of the component is less than 0.06 second, no dynamic amplification is expected and ap may be taken to equal 1.0. If the fundamental period of the component is greater than 0.06 second, dynamic amplification is expected and ap is taken to equal 2.5.

## Slide 19: Component Amplification Factor ap
Notes: 508A notes: A graph showing an alternate means of determining the component amplification factor is presented. The tabulation of assumed ap values is not meant to preclude more precise determination of the component amplification factor where the fundamental periods of both structure and component are available. The NCEER formulation shown in Figure C13.3-1 may be used to compute ap as a function of Tp/T. This works if the building structure does not have significant higher modes of vibration.

## Slide 20: Explanation of 0.4SDS(1 + 2 z/h)
0.4SDS
1.2SDS
AA= 0.4SDS (1+2zA/h)
AB = 0.4SDS (1+2zB/h)
A
B
zA
zB
h
Floor Acceleration Distribution
Notes: 508A notes: This graphic illustrates the distribution of seismic accelerations over the height of a building, using an elevation of a 5-story building. Equation 13.3-1 represents a trapezoidal distribution of floor accelerations within a structure, varying linearly from the acceleration at the ground (taken as 0.4SDS) to the acceleration at the roof (taken as 1.2SDS). The ground acceleration (0.4SDS) is intended to be the same acceleration used as design input for the structure itself, including site effects. The roof acceleration is established as three times the input ground acceleration based on examination of recorded in-structure acceleration data for short and moderate height structures in response to large California earthquakes. The minimum and maximum acceleration limits of Equations 13.3-2 and 13.3-3 are shown. Two nonstructural components are shown. Component “A” is attached at the second floor at a height of ZA. Component “B”, while at the 4th floor level, is suspended from the floor above. The shaking intensity it will experience is associated with the 5th floor, at a height of ZB.

## Slide 21: Explanation of z/h
h
z/h = 0
z/h = 2/5
z/h = 3/5
z/h = 4/5
z/h = 1
or design both connections for z/h = 3/5
z
Notes: This graphic provides other examples of how the location of the point of attachment of nonstructural component to the building influences the value of the factor z/h in the Equation 13.3-1, using an elevation of a 5-story building. In this example, floors are equally spaced with a story height of h/5.

## Slide 22: Alternative to Fp Equation 13.3-1
ai = acceleration at level i from modal analysis per Section 12.9 with R = 1.0
Ax = torsional amplification factor per Eq. 12.8-14
Linear dynamic or nonlinear response history analysis may be used
Upper and lower limits of Fp per Eqs. 13.3-2 and 13.3-3 apply to dynamic analysis
Equation 13.3-4
Notes: 508A notes: This slide discusses Equation 13.3-4, which permits an alternate determination of the component design forced based on the dynamic properties of the structure.
To use the equation, a modal analysis of the structure must be performed satisfying modal analysis procedures described in Chapter 12 of ASCE/SEI 7-10 including scaling of results assuming R = 1. Significant nonstructural items can be included in the modal analysis model. If the nonstructural item is included the value of ap can also be determined in the analysis. However ap cannot be taken as less than 1.0. Use of this equation can sometimes lead to significantly lower Fp values than Equation 13.3-1 especially in the middle and upper levels of moment frame building with 3 or more stories but requires much more computational effort , which often is impractical.
Where seismic response history analysis is used with at least seven ground motions, ai is taken as the average of the maximum accelerations. When less than seven ground motions are used, the maximum acceleration value for each floor is the maximum value obtained from the ground motions analyzed.

## Slide 23: New Alternatives in ASCE/SEI 7-16
The use of floor response spectra for determination of the seismic design force is now explicitly permitted (ASCE/SEI 7-16 Sec. 13.3.1.4.1).
The floor response spectrum is calculated for each ground motion record analyzed.
The floor acceleration, ai, is the maximum acceleration value from the floor response spectra for the component period, and the value of ap shall be taken as 1.0.
Notes: 508A notes: The use of floor response spectra for determination of the seismic design force is now explicitly permitted (ASCE/SEI 7-16 Sec. 13.3.1.4.1). Application of this approach requires that a floor response spectrum be calculated for the design earthquake at each level of the structure, based on a seismic response history analysis performed in accordance with ASCE/SEI 7-10 Section 12.9 or in accordance with the procedures in ASCE/SEI 7-10 Chapters 16, 17 or 18.

## Slide 24: New Alternatives in ASCE/SEI 7-16
Aix = floor acceleration for mode x at Level i
pix = modal participation factor for mode x at Level i
Sai = spectral acceleration for mode x
Alternate floor response spectra method based on a modal analysis is available (ASCE/SEI 7-16 Sec. 13.3.1.4.2).
The periods/mode shapes of the structure must be calculated for at least the first three modes in each orthogonal direction
The component dynamic amplification factor, DAF, determined by the ratio of the component period, Tp, to the building modal period, Tx
Notes: 508A notes. This slide discusses the use of floor response spectra for determination of the seismic design force, which is now explicitly permitted (ASCE/SEI 7-10 Sec. 13.3.1.4.1). The graph used for determining the dynamic amplification factor, DAF, is shown, Application of this approach requires that a floor response spectrum be calculated for the design earthquake at each level of the structure, based on a seismic response history analysis performed in accordance with ASCE/SEI 7-10 Section 12.9 or in accordance with the procedures in ASCE/SEI 7-10 Chapters 16, 17 or 18.

## Slide 25: Load Combinations
Earthquakes load nonstructural components in both the horizontal and vertical directions
The results of these loads (forces, stresses, displacements, etc.) are called “effects”, defined in ASCE/SEI 7-10 Section 12.4.2
  Horizontal earthquake load effects = Eh
  Vertical earthquake load effects, Ev = 0.2SDS multiplied by the dead load.
Load combinations for overall demand on an item are defined in ASCE/SEI 7-10 Section 12.4
Notes: This slide discusses how the earthquake loads on nonstructural components are combined with other loads to determine load effects. Horizontal earthquake load effects are taken as the equivalent static force, Fp, which may vary depending on the height of the component in the building The vertical earthquake effect is taken as a fraction of the short-period ground acceleration time the dead weight of the component.

## Slide 26: Seismic Relative Displacements
Seismic relative displacements are for use in design of cladding, stairways, windows, piping systems, sprinkler components, and other components connected to one structure at multiple levels or to multiple structures
Notes: The photo shows flexible pipe connections at a rooftop expansion joint.
This slide provides an overview of the displacement requirements for nonstructural components. Components connected to the structure at different levels and components connected to multiple structures are subject to the requirements. The photo on the right shows flexible pipe connections at a rooftop expansion joint.

## Slide 27: Seismic Relative Displacements
  For components connected to the structure at different levels and components connected to multiple structures, two equations for determining the anticipated relative displacements (Dp) at Design Earthquake Level
  Actual relative displacements as determined by elastic analysis, unreduced by the structural response modification factor (R)
  Upper-bound displacements based on the structural drift limit
Notes: 508A notes. This slide discusses the options available for calculating seismic relative displacements at the design earthquake level. The displacement demands can be based on building specific or generic building information.

## Slide 28: Design for Relative Displacement
Design for relative displacements is required for:
  Architectural components themselves which pose a life safety hazard including exterior wall elements and glazing. (ASCE/SEI 7-10 Section 13.5.2)
  Mechanical and electrical components themselves where Ip is greater than 1.0. (ASCE/SEI 7-10 Section 13.6.3)
The design force in the attachments to the structure may be governed by forces generated by relative displacement (ASCE/SEI 7-10 Section 13.4.1)
Notes: This slide identifies cases where design displacements is required for architectural and mechanical components. In some cases, the forces in the attachment to the structure are governed by forces generated when the relative displacement is imposed on the component.

## Slide 29: Seismic Relative Displacements
The seismic relative displacement demands, DpI, are determined using Equation 13.3-6:
DpI = DpIe
  where:
Dp = displacements within or between structures
Ie = the importance factor for the structure (Section 11.5.1)
Notes: This slide shows the formula for calculating seismic relative displacements. The displacement calculated for the structure is multiplied by the Importance factor of the structure to obtain the relative displacement demand. It is not modified by the component importance factor. Glazing acceptance criteria is set forth in ASCE/SEI 7-10 Section 13.9. Except for glazing, no specific displacement acceptance criteria is provided.

## Slide 30: Displacement Acceptance Criteria
The standard does not provide explicit acceptance criteria for the effects of seismic relative displacements, except for glazing
Damage to nonstructural components caused by relative displacement is acceptable, provided the performance objectives are met
Notes: The photo shows stairs that were rendered unusable by relative displacements.
Except for glazing, no specific displacement acceptance criteria is provided. Damage to the component is permissible if the component can still meet it’s performance objective. The photo to the right shows stairs that were rendered unusable by relative displacements. This level of damage is not acceptable.

## Slide 31: Determining Effective Drift Demand
Notes: This drawing shows an elevation of an exterior wall, consisting of a glazing system supported by rigid precast concrete spandrels.
Where nonstructural components are supported between, rather than at, structural levels, as frequently occurs for glazing systems, partitions, stairs, veneers, and mechanical and electrical distributed systems, the height over which the displacement demand, Dp, must be accommodated may be less than the story height, hsx, and should be considered carefully. In this example of an exterior wall with glazing sandwiched between rigid precast concrete panels, the glazing system is subjected to the full story drift, Dp, although its height (hx − hy) is only a fraction of the story height. The design drift must be accommodated by anchorage of the glazing unit, the joint between the precast spandrel and the glazing unit, or some combination of the two.

## Slide 32: Load Combinations
In ASCE/SEI 7-10 Section 12.4,strength and allowable stress design load combinations are provided
Eh is defined as Fp for nonstructural components and Ev is defined as 0.2 SDSD
The redundancy factor, ρ, is specified as 1.0 for nonstructural components. (ASCE/SEI 7-10 Section 13.3.1)
Ωo is specified in Tables 13.5-1 and 13.6-1
The load combinations with Ωo and are used for calculating demands on attachments to concrete and masonry
Allowable stress design methods are addressed in ASCE/SEI 7-10 Section 13.1.7.
Notes: This slide discusses how seismic loads on nonstructural components are combined with other loads using load combinations. The seismic design force on the component, Fp, is required to be combined with other loads as set forth in ASCE/SEI 7-10 Section 12.4. To use Section 12.4, there are certain items that need to be defined and these include Eh, Ev,  and Ωo.

## Slide 33: Attachment of Nonstructural Components
Design seismic forces in the connected parts, Fp, are prescribed in ASCE/SEI 7-10 Section 13.4
  Rp limited to 6 for design of attachments to the structure
  Design capacity for anchors in concrete is determined in accordance with ACI 318
  Design capacity for anchors in masonry is determined in accordance with ACI 530
Notes: This slide discusses the requirements in Section 13.4 for attachment of nonstructural components to the structure. The goal of this section is to ensure that attachments such as anchor bolts exhibit ductile behavior or provide a specified degree of excess strength. The requirements for anchorage to concrete and masonry were revised in the 2010 and 2016 editions of the ASCE 7

## Slide 34: Attachment of Nonstructural Components to Concrete or Masonry
For anchors in concrete and masonry, at least one of the following conditions must be satisfied:
  The component or a support in the load path leading to the structure undergoes ductile yielding at a load level less than the design strength of the corresponding anchor, or
  The anchors are designed to resist the load combinations considering Ω0
Notes: In this slide, the special requirements for attachment of components to concrete an masonry are summarized. Attachments must be designed to behave in a ductile manner or be designed for amplified forces.

## Slide 35: Post-installed Anchors in Concrete or Masonry
Post-installed anchors in concrete must be prequalified for seismic applications in accordance with ACI 355.2 or other approved standards
Post-installed anchors in masonry must be prequalified for seismic applications in accordance with approved qualification procedures
Power actuated fasteners in concrete, masonry, or steel are not permitted for sustained tension or bracing applications in SDC D, E or F unless approved for seismic loading
  Exceptions permit the use of power actuated fasteners in certain conditions when the applied loads are low
Notes: In this slide, the requirements for attachment of components to concrete an masonry using post installed anchors are summarized. Power actuated fasteners are not permitted in high seismic risk regions except in special cases where the applied loads are low.

## Slide 36: Architectural Components (Table 13.5-1)
  Nonstructural walls & partitions
  Parapets & chimneys
  Exterior nonstructural wall elements & connections
  Veneer
  Penthouses
  Ceilings
  Cabinets
  Access floors
  Signs
  Egress Stairs and Ramps
  Appendages
  Glazing
Notes: This slide contains a partial list of architectural components included in ASCE/SEI 7 Table 13.5-1, and an image of a large interior workspace.
The requirements are intended to apply only to permanently attached components – not to furnishings, temporary items, or mobile units. Furnishings such as tables, chairs, and desks may shift but generally pose minimal hazards provided they do not obstruct emergency egress routes. Storage cabinets, tall bookshelves, and other items of significant mass are not exempt and must be anchored or braced in accordance with ASCE/SEI 7.

## Slide 37: Design and Detailing Requirements of Architectural Components
ASCE/SEI 7-10 Section 13.5
Specific demands for exterior nonstructural wall elements and connections (13.5.3)
Suspending Ceilings – CISCA, ASTM C635 and ASTM C636 (13.5.6)
Access Floors (13.5.7)
Tall Partitions – independent bracing (13.5.8)
Glazing – Drift capacity AAMA 501.6 (13.5.9)
Notes: This slide lists some of the sections in ASCE/SEI 7 Section 13.5 that contain specific design requirements for architectural components..
The requirements of Section 13.5 are intended to reduce property damage and life-safety hazards posed by architectural components due to loss of stability or integrity. Architectural components may pose a direct falling hazard to building occupants or to people outside the building (as in the case of parapets, exterior cladding, and glazing). Failure or displacement of interior components (such as partitions and ceiling systems in exits and stairwells) may block egress.

## Slide 38: Acoustical Tile or Lay-In Panel Ceilings
Acoustical tile or lay-in panel ceilings in regions of high seismic risk (Seismic Design Categories D, E, and F) must meet additional requirements relating to the perimeter closure angle
The width of the perimeter supporting closure angle or channel shall be not less than 2.0 in. unless qualified perimeter supporting clips are used.
Closure angles or channels must be screwed or otherwise positively attached to wall studs or other supporting structure
Notes: This slide describes new requirements for acoustical tile or lay0in panel ceilings in regions of high seismic risk. The perimeter supporting clips may no be substituted for the 2 inch wide supporting element, provided they meet certain criteria.

## Slide 39: Lay-In Ceilings Perimeter Clips
Perimeter supporting clips must be qualified in accordance with approved test criteria
Perimeter supporting clips must be attached to the supporting closure angle or channel with a minimum of two screws per clip, and must be installed around the entire ceiling perimeter.
In each orthogonal horizontal direction, one end of the ceiling grid must be attached to the closure angle, or perimeter supporting clip. The other end of the ceiling grid shall have a minimum 0.75 in. clearance and be free to slide on a closure angle, or channel or perimeter supporting clip
Notes: This slide describes the requirements for perimeter ceiling clips. The clips must be qualified by test and must installed around the entire perimeter of the ceiling. Clearance and attachment requirements are described.

## Slide 40: Exterior Wall Panel Connections
Requirements for exterior wall panel connections which accommodate story drift through sliding mechanisms or bending of threaded steel rods were added to ASCE/SEI 7-16
Notes: The image shows precast concrete wall panel connections utilizing threaded steel rods.
This slide introduces requirements for certain types rod connections for exterior wall panels, when story drift is provided by sliding or bending of threaded steel rods. The image to the right shows precast concrete wall panel connections utilizing threaded steel rods. The rods to the right fractured during the 1994 Northridge earthquake.

## Slide 41: Exterior Wall Panel Connections
ASCE/SEI 7-16 Section 13.5.3 requires that threaded rods be fabricated of low-carbon or stainless steel
Cold-worked carbon steel threaded rod as fabricated must meet or exceed the reduction of area, elongation, and tensile strength requirements
Notes: This slide shows requirements the material requirements for threaded steel rods.

## Slide 42: Exterior Wall Panel Connections
Rods used in sliding connections utilizing slotted or oversized holes must have length to diameter ratios of 4 or less, where the length is the clear distance between the nuts or threaded plates
The slots or oversized holes must be proportioned to accommodate the full in-plane design story drift in each direction.
Notes: This slide covers requirements for connections for exterior wall panels, when story drift is accommodated by sliding.

## Slide 43: Exterior Wall Panel Connections
Connections where story drift is accommodated by bending of the threaded rod, it must satisfy Eq. 13.5-1:
(L/d)/DpI ≥ 6.0 [1/in.]
where:
  L = clear length of rod between nuts or threaded plates [in.]
  d = rod diameter [in.]
Notes: This slide covers requirements for connections for exterior wall panels, when story drift is accommodated by bending of the rod.

## Slide 44: Egress Stairs and Ramps
Egress stairs and ramps are an essential part of the system used to evacuate building occupants following an earthquake
Failure of the stairs may trap building occupants on the upper levels of the structure
  Ladders on emergency vehicles can usually only reach the lower floors in mid- and high-rise structures.
In ASCE/SEI 7-16 a new section was added with requirements intended to limit damage and improve functionality of egress stairs and ramps following an earthquake.
Notes: This slide discusses egress stair systems and ramps that are not integral with the building structure. Seismic provisions for egress stairs were added in ASCE/SEI 7-16. It is assumed that the seismic resistance of egress stairs integral with the structural system is addressed in the overall building design.

## Slide 45: Egress Stairs and Ramps
Provisions in Chapter 13 do not apply to stairs that are integral with the building structure
Egress stairs are assigned a component importance factor, Ip =1.5
Amplification factor ap = 1.0
  Ramp fasteners and attachments ap = 2.5
Response factor Rp = 2.5
Displacement demands are increased if the stair bearing supports do not have keeper assemblies or end stops that keep the stair from detaching from the structure if the design displacement is exceeded.
Notes: This slide provides additional information on seismic design of egress stair systems and ramps. It is assumed that the seismic resistance of egress stairs integral with the structural system is addressed in the overall building design. Egress stairs and ramps without detailing to prevent the stair bearing supports from detaching from the structure are subject to higher design displacements.

## Slide 46: Mechanical Components (Table 13.6-1)
OSHPD/FDD
Boilers and furnaces
HVAC
Piping systems
Engines
Turbines
Fans
Furnaces
Chillers
Elevators
Escalators
Notes: An image of a pump that was torn from an inertia pad in the 1994 Northridge earthquake.
This slide contains a partial list of the mechanical components and systems found in ASCE/SEI 7 Table 13.6-1, and an image of a pump that was torn from an inertia pad in the 1994 Northridge earthquake. For both mechanical and electrical components the focus is on the supports and anchorage of the component unless Ip = 1.5, in which case the component itself must be checked.

## Slide 47: Electrical Components (Table 13.6-1)
Conduits
Bus ducts
Cable trays
Lighting fixtures
Motors
Generators
Communication equip.
Inverters
Transformers
Motor control centers
Switch gear
Notes: An image of a worker installing wiring above a suspended ceiling grid.
This slide contains a partial list of the electrical components and systems found in ASCE/SEI 7 Table 13.6-1, and an image of a worker installing wiring above a suspended ceiling grid.

## Slide 48: Design and Detail Requirements for Mechanical and Electrical Equipment
ASCE/SEI 7-10 Section 13.6:
Sprinkler systems – NFPA 13
Escalators and Elevators – ASME A17.1
Vessels – ASME BPVC
Piping – ASME B31
Lighting fixtures – Prescriptive detail requirements
Many specific prescriptive details for mechanical and
electrical Equipment
Notes: This slide lists some of the sections in ASCE/SEI 7 Section 13.6 that contain specific design requirements for mechanical and electrical components..
Many of these components have requirements found in the applicable referenced standard.

## Slide 49: Pre-Manufactured Modular Mechanical and Electrical Systems
ASCE/SEI 7-16 includes provisions for pre-manufactured modular mechanical and electrical systems.
Design of the modular unit itself is covered in ASCE/SEI 7- 16 Chapter 15, Nonbuilding Structures,
Nonstructural components in the modular unit are designed per Chapter 13.
Notes: The image shows factory-built units that are transported to the site and assembled together
This slide discusses provisions for seismic design of pre-manufactured modular mechanical and electrical systems added to the 2016 edition of ASCE/SEI 7. These factory-built units are transported to the site and assembled together. Section 13.1.5 of the Standard directs the user to Standard Chapter 15, Nonbuilding Structures, for the design of the modular unit itself. Nonstructural components installed or supported by the modular unit are designed in accordance with Standard Chapter 13.

## Slide 50: Special Certification Requirements for Certain Designated Seismic Systems (Ip=1.5)
In ASCE/SEI 7-10 Section 13.2.2 - Seismic qualification required in SDC C through F for :
  Active mechanical and electrical equipment that are required to function following a DBE
  Components containing hazardous contents
Qualification to demonstrate functionality after being subject to a DBE to be determined by one of the following:
  Shake table testing – ICC-ES AC-156
  Experience Data
  Analysis (extremely difficult for active equipment)
Certification required by supplier indicating compliance
Notes: This slide lists some of the requirements for Designated Seismic Systems which may be subject to special certification. While the goal of design for most nonstructural components is to prevent detachment or toppling that would pose a hazard to life safety, designated seismic systems (with Ip = 1.5) are intended to meet higher performance goals. In some cases, failure of mechanical or electrical equipment itself poses a significant hazard. This section addresses the design and certification of designated seismic system components and their supports and attachments. Examples of designated seismic systems include fire protection piping, uninterruptible power supplies for hospitals, and certain vessels or piping that contain highly toxic or explosive substances.

## Slide 51: Unbraced Distribution Systems
The conditions where seismic bracing may be omitted from distribution systems such as pipe, conduit, and ductwork have been revised and expanded in ASCE/SEI 7-16
The bracing exemptions are now based on the weight of the components carried and the length and diameter of the hanger rods
The provisions apply to both single rods and trapeze assemblies
Notes: This slide describes revisions to the criteria for unbraced distribution systems such as pipes, ducts, and conduit supported by threaded rods. The exceptions now consider the length and diameter of the rods, and the applied load carried by the rods.

## Slide 52: Unbraced Distribution Systems
Bracing for distribution systems may be omitted where:
Ip = 1.0, and
Flexible connections are provided between the distribution system and associated components to accommodate the relative displacement, and
The distribution system is positively attached to the structure, and
Load and geometry criteria are met.
Notes: This slide describes some of the criteria that must be met in order for a distribution system to be eligible for a bracing exemption. The general criteria is shown in this slide.

## Slide 53: Unbraced Distribution Systems
To meet the geometry criteria, one of the following must apply:
  The distribution system(s) are supported by trapeze assemblies with 3/8-in. diameter rod hangers, length not exceeding 12 in. from the support point to the connection at the supporting structure support the system, and maximum load on any single trapeze is 100 lb or less
  Distribution system is supported by individual rod hangers 3/8-in. or 1/2 in. diameter, each rod is 12 in. or less in length, and the total weight supported by any single rod is 50 lb or less
Notes: This slide lists the eligibility criteria for a lateral bracing exception for distribution systems on trapeze assemblies support by 3/8-in. diameter rod hangers. It also lists the criteria for systems supported by individual rod hangers of 3/8-in. and 1/2-in. diameter.

## Slide 54: Unbraced Distribution Systems
Additional geometry criteria options:
  The distribution system(s) are supported by trapeze assemblies with 1/2-in. diameter rod hangers, length not exceeding 12 in. from the support point to the connection at the supporting structure support the system, and maximum load on any single trapeze is 200 lb or less
  The distribution system(s) are supported by trapeze assemblies with 1/2-in. diameter rod hangers, length not exceeding 24 in. from the support point to the connection at the supporting structure support the system, and maximum load on any single trapeze is 100 lb or less
Notes: This slide lists the eligibility criteria for a lateral bracing exception for distribution systems on trapeze assemblies support by 1/2-in. diameter rod hangers. There are to cases, one for hangers less than 12 inched long, and the other for rod hangers greater than 12 inches by less than 24 inches in length.

## Slide 55: Questions?
Notes: 508A note: Slide prompting participants to ask questions.

## Slide 56: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.