## Slide 1: Nonbuilding Structure Design Fundamentals & Example Problems By J. G. (Greg) Soules, P.E., S.E., SECB Originally developed by Harold O. Sprague, Jr., P.E.
17
Disclaimer
Notes: Introduction slide.
This unit is only a brief introduction to the subject of earthquake resistant design of nonbuilding structures.

## Slide 2: Seismic Design of Nonbuilding Structures
What are Nonbuilding Structures (NBS)?
Use of “Reference Documents”
NBS Sensitive to Vertical Ground Motions
NBS Supported by Other Structures
Example 17.1 - Nonbuilding Structures versus Nonstructural Components
  Example 17.1.1 - Nonbuilding Structure
  Example 17.1.2 - Nonstructural Component
Notes: Slide 2 is the table of contents for the presentation. SDC stands for Seismic Design Category

## Slide 3: Seismic Design of Nonbuilding Structures
Nonbuilding Structures Similar to Buildings
  Example 17.2 - Pipe Rack, SDC D
Nonbuilding Structures Not Similar to Buildings
  Example 17.6 - Tanks and Vessels, SDC D
    Example 17.6.2 - Flat-Bottom Gasoline Tank
  Example 17.7 - Vertical Vessel, SDC D
Notes: Slide 3 is the table of contents for the presentation.

## Slide 4: What are Nonbuilding Structures (NBS)?
Notes: Slide 4 shows pictures of four very different nonbuilding structures to support the section of the presentation titled “What are Nonbuilding Structures?” – an elevated water tower in the shape of a peach, an egg shaped digester, a pipe rack, and a column supported spherical pressure vessel.

## Slide 5: What are Nonbuilding Structures (NBS)?
A nonbuilding structure is any structure that was not designed for continuous human occupancy.
A nonbuilding structure may be supported by the earth or another structure.
Requirements for the seismic design of nonbuilding structures can be found in Chapter 15 of ASCE 7-16.
Notes: Slide 5 begins a discussion of what constitutes a nonbuilding structure.

## Slide 6: What are Nonbuilding Structures (NBS)?
Nonbuilding structures fall into two broad categories:
  those with structural systems similar to buildings and
  those with structural systems not similar to buildings.
Specific requirements for these two categories of nonbuilding structures appear in Sections 15.5 and 15.6 of ASCE 7-16 respectfully.
Notes: Slide 6 continues a discussion of what constitutes a nonbuilding structure.

## Slide 7: Use of “Reference Documents”
Notes: Slide 7 shows representations of three commonly used reference documents – API Standard 650 “Welded Tanks for Oil Storage”, (on the left), ASME Boiler and Pressure Vessel Code (in the middle), and ACI 350.3 “Seismic Design of Liquid-Containing Concrete Structures and Commentary” (on the right).
API stands for American Petroleum Institute. ASME stands for the American Society of Mechanical Engineers. ACI stands for the American Concrete Institute.

## Slide 8: Use of “Reference Documents”
“Reference Documents or Reference Standards” are industry standards (such as API 650) for different NBS that have been accepted by ASCE 7 as modified by the provisions of Chapter 15.
Some of the “Reference Documents” listed in ASCE 7 have well defined seismic design procedures.
Notes: Slide 8 begins a discussion on the use of reference documents.

## Slide 9: Use of “Reference Documents”
The adopted version of the Reference Documents are listed in Chapter 23 of ASCE 7-16.
Unless approval is obtained from the “authority having jurisdiction”, a newer edition of the Reference Document may not be used for the seismic design of the nonbuilding structure.
Notes: Slide 9 continues a discussion on the use of reference documents.

## Slide 10: Use of “Reference Documents”
For the purpose of Chapter 15, material standards such as AISC 360, ACI 318, etc. are not considered “reference documents”.
Material standards are generic in nature and do not contain complete design requirements for specific classes of nonbuilding structures such as steel storage racks or tanks.
The order of precedence is the adopted building code (IBC), then ASCE 7, and finally the reference document (e.g. API 650).
Notes: Slide 10 continues a discussion on the use of reference documents.
The order of precedence of codes and standards is not well understood by many engineers.

## Slide 11: NBS Sensitive to Vertical Ground Motions
The vertical ground motions of NEHRP Provisions Chapter 23, based on the work of Bozorgnia and Campbell (2004), were incorporated in Section 11.9.
These alternate ground motions are currently only used for certain NBS.
0.8CvSMS
0.3CvSMS
0.8CvSMS(0.15/Tv)0.75
Notes: Slide 11 begins a discussion on nonbuilding structures sensitive to vertical ground motions. The right side of the slide shows the vertical response spectrum from ASCE 7-16 Section C11.9 (Figure C11.9-1).
The procedure for defining the MCER vertical response spectrum in ASCE 7 is a modified version of the procedure taken from the 2009 NEHRP Provisions. Unlike the procedure contained in the 2009 NEHRP Provisions, the procedure provided in Section 11.9 is keyed to the MCER spectral response acceleration parameter at short periods, SMS.

## Slide 12: NBS Sensitive to Vertical Ground Motions
Specific provisions added for liquid and granular storage tanks/vessels, suspended structures (such as boilers) and nonbuilding structures incorporating horizontal cantilevers.
These provisions replace the 0.2SDS value incorporated in ASCE 7-05 with Sav determined from the vertical response spectrum and combined with the horizontal effect using prescribed load combinations.
Notes: Slide 12 continues a discussion on nonbuilding structures sensitive to vertical ground motions.

## Slide 13: NBS Supported by Other Structures
Notes: Slide 13 three photographs of nonbuilding structures supported by other structures.

## Slide 14: NBS Supported by Other Structures
Nonbuilding structures supported by other structures see amplified seismic forces in a similar manner as nonstructural components.
Section 15.3 of ASCE 7-16 provides extensive guidance on the design of nonbuilding structures supported by other structures.
There are 3 possible outcomes when the provisions of Section 15.3 are used.
Notes: Slide 14 begins a discussion on nonbuilding structures supported by other structures.

## Slide 15: NBS Supported by Other Structures
15.3.1 Less Than 25 percent Combined Weight Condition
15.3.2 Greater Than or Equal to 25 Percent Combined Weight Condition
  15.3.2 (1) Rigid (T < 0.06 sec) Nonbuilding Structure
  15.3.2 (2) Flexible Nonbuilding Structure
Notes: Slide 15 continues a discussion on nonbuilding structures supported by other structures.
The slide lists the three possible options for designing nonbuilding structures supported by other structures. These options are discussed in detail in the next few slides.

## Slide 16: Nonbuilding Structures vs. Nonstructural Components
  Many industrial structures are classified as either nonbuilding structures or nonstructural components.
  The intent of ASCE 7-16 is to provide a clear and consistent design methodology regardless of whether the structure is a nonbuilding structure or a nonstructural component.
  Central to the methodology is how to determine which classification is appropriate.
Notes: Slide 16 is a discussion of the differences between nonbuilding structures and nonstructural components.

## Slide 17: Nonbuilding Structures vs. Nonstructural Components
  Table 17-1 provides a simple method to determine the appropriate classification.
Table 17-1 Applicability of the Chapters of the Standard |  | 
Supporting Structure | Supported Item | 
 | Nonstructural Component | Nonbuilding Structure
Building | Chapter 12 for supporting structure; Chapter 13 for supported item | Chapter 12 for supporting structure; Chapter 15 for supported item
Nonbuilding | Chapter 15 for supporting structure; Chapter 13 for supported item | Chapter 15 for both supporting structure and supported item
Notes:   Slide 17 shows Table 17-1, which provides a simple method to determine if the structure in question is a nonbuilding structure or a nonstructural component.
  Additional discussion on determining if the structure is a nonstructural component or a nonbuilding structure can be found in Bachman, Robert and Dowty, Susan, “Nonstructural Component or Nonbuilding Structure?”, Building Safety Journal, International Code Council, April-May 2008.

## Slide 18: Nonbuilding Structures vs. Nonstructural Components
Example 17.1.1
  Combustion turbine building.
  Building supports four filter units connected in a fashion that couples their dynamic response.
Example 17.1.2
  Combustion turbine building.
  Building supports four filter units that are independent structures.
Figure 17-1 Combustion turbine building
(1.0 ft = 0.3048 m)
Notes: The figure shows a combustion turbine building, an isometric view of a single story rectangular steel braced frame nonbuilding structure.
Slide 18 introduces Example Problem 17.1 – Nonbuilding Structures vs. Nonstructural Components. The slide shows Figure 17-1, a combustion turbine building, on the right. The illustration shows an isometric view of a single story rectangular steel braced frame nonbuilding structure. The longitudinal direction of the nonbuilding structure is made up of four equal 30-foot long bays with the center two bays braced with chevron bracing. The transverse direction of the nonbuilding structure is made up of three bays with a total length of 80 feet with the center bay braced with chevron bracing. The height of the nonbuilding structure is shown as 25 feet. The roof of the nonbuilding structure is shown supporting 4block shaped inlet filters. One inlet filter is shown centered on each longitudinal bay. All 4 inlet filters are shown centered on the middle bay in the transverse direction.
The following two examples illustrate the difference between nonbuilding structures that are treated as nonstructural components, using ASCE 7-16 Chapter 13, and those which are designed in accordance with ASCE 7-16 Chapter 15. In many instances, the weight of the supported nonbuilding structure is relatively small compared to the weight of the supporting structure (less than 25% of the combined weight) such that the supported nonbuilding structure will have a relatively small effect on the overall nonlinear earthquake response of the primary structure during design level ground motions. It is permitted to treat such structures as nonstructural components and use the requirements of ASCE 7-16 Chapter 13 for their design. Where the weight of the supported structure is relatively large (greater than or equal to 25% of the combined weight) compared to the weight of the supporting structure, the overall response can be affected significantly. In such cases it is intended that seismic design loads and detailing requirements be determined following the procedures of ASCE 7-16 Chapter 15. Where there are multiple large nonbuilding structures, such as vessels supported on a primary nonbuilding structure and the weight of an individual supported nonbuilding structure does not exceed the 25 percent limit but the combined weight of the supported nonbuilding structures does, it is recommended that the combined analysis and design approach of ASCE 7-16 Chapter 15 be used.

## Slide 19: Nonbuilding Structures vs. Nonstructural Components
Example 17.1.1
  Four inlet filters = WIF = 4 x 34 kips = 136 kips
  Support structure = WSS = 288 kips
  WCombined = 136 kips + 288 kips = 424 kips
  Therefore, ASCE 7-16 Section 15.3.2 is applicable and the requirements of Chapter 15 are to be followed.
Notes: Slide 19 shows Example 17.1.1 – inlet filters dynamically coupled.
Because the weight of the inlet filters is 25 percent or more of the combined weight of the nonbuilding structure and the supporting structure (ASCE 7-16 Section 15.3.2), the inlet filters are classified as “nonbuilding structures” and the seismic design forces must be determined from analysis of the combined seismic-resistant structural systems. This would require modeling the filters, the structural components of the filters, and the structural components of the combustion turbine supporting structure to determine accurately the seismic forces on the structural elements as opposed to modeling the filters as lumped masses.

## Slide 20: Nonbuilding Structures vs. Nonstructural Components
Example 17.1.2
  One (effective) inlet filters = WIF = 34 kips
  Support structure = WSS = 288 kips
  WCombined = (4 x 34 kips) + 288 kips = 424 kips
  Therefore, ASCE 7-16 Section 15.3.1 is applicable and the requirements of Chapter 13 are to be followed.
Notes: Slide 20 shows Example 17.1.2 – inlet filters not dynamically coupled.
Because the weight of an inlet filter is less than 25 percent of the combined weight of the nonbuilding structures and the supporting structure (ASCE 7-16 Section 15.3.1), the inlet filters are classified as “nonstructural components” and the seismic design forces must be determined in accordance with ASC 7-16 Chapter 13. In this example, the filters could be modeled as lumped masses. The filters and the filter supports could then be designed as nonstructural components.

## Slide 21: NBS Similar to Buildings
Notes: Slide 21 shows two photographs of nonbuilding structures similar to buildings. The photograph on the left is a process structure used in an LNG facility. The photograph on the right is a suspended boiler in a power plant.

## Slide 22: NBS Similar to Buildings
  Provisions found in Section 15.5.
  Designed and constructed with structural systems similar to buildings.
  Have dynamic response similar to buildings.
  Specific requirements given for:
      Pipe Racks (15.5.2)
      Storage Racks (15.5.3)
      Electrical Power Generating Facilities (15.5.4)
      Structural Towers for Tanks and Vessels (15.5.5)
      Piers and Wharves (15.5.6)
Notes: Slide 22 continues a discussion on nonbuilding structures similar to buildings.

## Slide 23: Nonbuilding Structures Similar to Buildings
Example 17.2 Pipe Rack
Figure 17-2 Pipe rack (1.0 ft = 0.3048 m)
Notes: Slide 23 shows Example 17.2 – Pipe Rack. Three figures are shown. The top figure is a plan view of the pipe rack. The width of the pipe rack is 20 feet. The left side of the pipe rack is made up of six equal 20-foot long bays. The center bay is 20 feet long and contains x-bracing in the horizontal plane. The right side of the pipe rack is made up of five equal 20-foot long bays. Four runs of piping are shown parallel to the longitudinal direction. An expansion loop is shown on the right side of the pipe rack indicating a break in the continuity of the pipe rack. The second figure is an elevation view of the pipe rack in the longitudinal direction. X-bracing in the vertical plane is shown in the same bay as the x-bracing shown in the plan view. Two tiers of piping are shown. The height from grade to the bottom of the upper run of piping is shown as 15 feet. The distance from the bottom of the upper run of piping to the top of the frame is shown as 3 feet. The third figure is an elevation view of the pipe rack in the transverse direction. The transverse direction of the pipe rack is shown as a single bay moment frame with two tiers of piping with four pipes on each tier. The height from grade to the bottom of the lower run of piping is shown as 10 feet. The distance from the bottom of the lower run of piping to the top of the frame is shown as 8 feet.
A two-tier, 12-bay pipe rack in a petrochemical facility has concentrically braced frames in the longitudinal direction and ordinary moment frames in the transverse direction. The pipe rack supports four runs of 12-in.-diameter pipe carrying naphtha on the top tier and four runs of 8-in.-diameter pipe carrying water for fire suppression on the bottom tier. The minimum seismic dead load for piping is 35 psf on each tier to allow for future piping loads. The seismic dead load for the steel support structure is 10 psf on each tier.

## Slide 24: Nonbuilding Structures Similar to Buildings
This example illustrates the calculation of design base shears and maximum inelastic displacements for a pipe rack using the equivalent lateral force (ELF) procedure (transverse direction only).
For this example, the design ground motion parameters are as follows:
  SDS = 0.40
  SD1 = 0.18
Notes: Slide 24 is a continuation of Example 17.2 – Pipe Rack.

## Slide 25: Nonbuilding Structures Similar to Buildings
Risk Category and Importance Factor
  The upper piping carries naphtha.
  Material safety datasheet (MSDS) for naphtha indicates that naphtha has a medium lethal concentration [LC(50)] of 5.2 mg per liter.
  Standard Section C1.5.3 defines a toxic material as a chemical with a LC(50) between 2 mg per liter and 20 mg per liter.
  Naphtha is therefore a toxic material and is assigned to Risk Category III per ASCE 7-16 Table 1.5-1.
Notes: Slide 25 is a continuation of Example 17.2 – Pipe Rack.

## Slide 26: Nonbuilding Structures Similar to Buildings
Risk Category and Importance Factor
  The lower piping is required for fire suppression and is assigned to Risk Category IV per ASCE 7-16 Table 1.5-1.
  Therefore, pipe rack is assigned to Risk Category IV based on the more severe category.
  From ASCE 7-16 Table 1.5-2, Ie = 1.5
Seismic Design Category
  Per ASCE 7-16 Section 11.6 based on Risk Category IV, SDS = 0.40, and SD1 = 0.18, the Seismic Design Category (SDC) is D.
Notes: Slide 26 is a continuation of Example 17.2 – Pipe Rack.
ASCE 7-16 Section 15.4.1.1 directs the user to use the largest value of Ie based on the applicable reference document listed in ASCE 7-16 Chapter 23, the largest value selected from ASCE 7-16 Table 1.5-2, or as specified elsewhere in Standard Chapter 15. It is important to be aware of the requirements of ASCE 7-16 Section 15.4.1.1. While the importance factor for most structures will be determined based on ASCE 7-16 Table 1.5-2, there are reference documents that define importance factors greater than those found in ASCE 7-16 Table 1.5-2.

## Slide 27: Nonbuilding Structures Similar to Buildings
Transverse Direction – R Factor Options
  In ASCE 7-16 Table 12.2-1, ordinary steel moment frames are not permitted in Seismic Design Category D. There are several options for ordinary steel moment frames found in ASCE 7-16 Table 15.4-1 as follows:
  ASCE 7-16 Table 15.4-1, Ordinary moment frames of steel, R = 3.5. According to note c in ASCE 7-16 Table 15.4-1, this system is allowed for pipe racks up to 35’ without limitations on the connection type. Option requires the use of the AISC Seismic Provisions.
Notes: Slide 27 is a continuation of Example 17.2 – Pipe Rack.
According to ASCE 7-16 Section 15.4-1, either ASCE 7-16 Table 12.2-1 or ASCE 7-16 Table 15.4-1 may be used to determine the seismic parameters, although mixing and matching of values and requirements from the tables is not allowed. In ASCE 7-16 Chapter 15, selected nonbuilding structures similar to buildings are provided an option where both lower R values and less restrictive height limits are specified. This option permits selected types of nonbuilding structures which have performed well in past earthquakes to be constructed with fewer restrictions in Seismic Design Categories D, E and F provided seismic detailing is used and design force levels are considerably higher. The R value-height limit trade-off recognizes that the size of some nonbuilding structures is determined by factors other than traditional loadings and result in structures that are much stronger than required for seismic loadings (Soules, 2006). Therefore, the structure’s ductility demand is generally much lower than a corresponding building. The R value-height trade-off also attempts to obtain the same structural performance at the increased heights. The user will find that the option of reduced R value with less restricted height will prove to be the economical choice in most situations due to the relative cost of materials and construction labor. It must be emphasized that the R value-height limit trade-off of ASCE 7-16 Table 15.4-1 applies only to nonbuilding structures similar to buildings and cannot be applied to building structures.

## Slide 28: Nonbuilding Structures Similar to Buildings
Transverse Direction – R Factor Options
  ASCE 7-16 Table 15.4-1, Ordinary moment frames of steel with permitted height increase, R = 2.5. This option is intended for pipe racks greater than 65’ high and limited to 100’ and is not applicable for this example.
  ASCE 7-16 Table 15.4-1, Ordinary moment frames of steel with unlimited height, R=1. Option does not require the use of the AISC Seismic Provisions.
  For this example, option with R = 3.5 is chosen.
Notes: Slide 28 is a continuation of Example 17.2 – Pipe Rack.
Ordinary steel moment frames are retained for use in nonbuilding structures such as pipe racks because they allow greater flexibility for accommodating process piping and are easier to design and construct than special steel moment frames.

## Slide 29: Nonbuilding Structures Similar to Buildings
Transverse Direction – Seismic Response Coefficient
  Using ASCE 7-16 Equation 12.8-2:
  From analysis, T = 0.42 second. Using ASCE 7-16 Equation 12.8-3 for T ≤ TL, Cs does not need to exceed:
Notes: Slide 29 is a continuation of Example 17.2 – Pipe Rack.
For nonbuilding structures, the fundamental period is generally approximated for the first iteration and must be verified with final calculations. ASCE 7-16 Section 15.4.4 makes clear that the approximate period equations of ASCE 7-16 Section 12.8.2 do not apply to nonbuilding structures.

## Slide 30: Nonbuilding Structures Similar to Buildings
Transverse Direction – Seismic Response Coefficient
  Using ASCE 7-16 Equation 12.8-5, Cs must not be less than: Cs = 0.044IeSDS ≥ 0.01 = 0.044(1.5)(0.4) = 0.0264
  ASCE 7-16 Equation 12.8-2 controls; Cs = 0.171.
Notes: Slide 30 is a continuation of Example 17.2 – Pipe Rack.
Always remember to check the minimum base shear value.

## Slide 31: Nonbuilding Structures Similar to Buildings
Transverse Direction – Seismic Weight
  The seismic weight resisted by the moment frame in the transverse direction is shown below based on two levels of piping, a 20 ft bent spacing, a bent width (perpendicular with the piping) of 20 ft, piping dead weight of 35 psf and structure dead weight of 10 psf: W = 2(20 ft)(20 ft)(35 psf + 10 psf) = 36 kips
Notes: Slide 31 is a continuation of Example 17.2 – Pipe Rack.
The piping dead weight includes the weight of the fluid in the pipe. In ASCE 7-16 Chapter 3, this topic is discussed under Section 3.1.3 “Weight of Fixed Service Equipment”.

## Slide 32: Nonbuilding Structures Similar to Buildings
Transverse Direction – Base Shear & Drift
  Using ASCE 7-16 Equation 12.8-1 the base shear V is: V = CsW = 0.171(36 kips) = 6.2 kips
  Drift of the pipe rack in the transverse direction was calculated by elastic analysis using the design forces calculated above. The calculated lateral drift, δxe = 0.328 inch. Using ASCE 7-16 Equation 12.8-15:
Notes: Slide 32 is a continuation of Example 17.2 – Pipe Rack.
The lateral drift must be checked with regard to acceptable limits. The acceptable limits for nonbuilding structures are not found in codes. Rather, the limits are what is acceptable for the performance of the piping. In general, piping can safely accommodate the amount of lateral drift calculated in this example. P-delta effects must also be considered and checked as required in ASCE 7-16 Section 15.4.5.

## Slide 33: Nonbuilding Structures Similar to Buildings
Transverse Direction – Redundancy Factor
  The seismic force-resisting system is an ordinary moment resisting frame with only two columns in a single frame. The frames repeat in an identical pattern.
  Loss of moment resistance at the beam-to-column connections at both ends results in a loss of more than 33% in story strength. Therefore, ASCE 7-16 Section 12.3.4.2 Condition a is not met.
Notes: Slide 33 is a continuation of Example 17.2 – Pipe Rack.
Some nonbuilding structures are designed with parameters from ASCE 7-16 Table 12.2-1 or 15.4-1 if they are termed “nonbuilding structures similar to buildings”. For such structures (assigned to Seismic Design Category D, E, or F) the redundancy factor applies. Pipe racks, being fairly simple moment frames or braced frames, are in the category similar to buildings. Because this structure is assigned to Seismic Design Category D, ASCE 7-16 Section 12.3.4.2 applies.

## Slide 34: Nonbuilding Structures Similar to Buildings
Transverse Direction – Redundancy Factor
  The moment frame as described above consists only of a single bay. Therefore, ASCE 7-16 Section 12.3.4.2 Condition b is not met.
  The value of r in the transverse direction is therefore 1.3.
Notes: Slide 34 is a continuation of Example 17.2 – Pipe Rack.

## Slide 35: NBS Not Similar to Buildings
Notes: Slide 35 shows three photographs of nonbuilding structures not similar to buildings. The photograph on the left is an amusement park structure. The photograph in the center is a Steel Tubular Support Structures for Onshore Wind Turbine Generator (WTG) System. The photograph on the right is a Ground-Supported Cantilever Wall.

## Slide 36: NBS Not Similar to Buildings
  Provisions found in Sections 15.6 and 15.7.
  Designed and constructed with structural systems NOT similar to buildings.
  Have dynamic response NOT similar to buildings.
Notes: Slide 36 begins a discussion on nonbuilding structures not similar to buildings.

## Slide 37: NBS Not Similar to Buildings
  Specific requirements given for:
      Earth-Retaining Structures (15.6.1)
      Chimneys and Stacks (15.6.2)
      Amusement Structures (15.6.3)
      Special Hydraulic Structures (15.6.4)
      Secondary Containment Systems (15.6.5)
      Telecommunication Towers (15.6.6)
      Steel Tubular Support Structures for Onshore Wind Turbine Generator Systems (15.6.7)
      Ground-Supported Cantilever Walls or Fences (15.6.8)
      Tanks and Vessels (15.7)
Notes: Slide 37 continues a discussion on nonbuilding structures not similar to buildings.

## Slide 38: Tanks and Vessels Design Basis
Seismic loads in liquid tanks are made up of three components:
  impulsive (rigid mass of the tank shell, roof, and part of the product)
  convective (sloshing mass of the liquid)
  vertical
Notes: Slide 38 discusses the three seismic load components in liquid storage tanks. The figure to the right is a generalized tank model including the impulsive and convective masses.
Sections 15.7.1 (General) and 15.7.2 (Design Basis) cover the unique aspects of the seismic design of tanks and vessels. The following is the currently accepted method for the dynamic modeling of the tank and its contents:
When a liquid-filled tank is subjected to ground acceleration, the lower portion of the contained liquid, identified as the impulsive component of mass, mi, acts as if it were a solid mass rigidly attached to the tank wall. As this mass accelerates, it exerts a horizontal force, Pi, on the wall; this force is directly proportional to the maximum acceleration of the tank base. This force is superimposed on the inertia force of the accelerating wall itself, Ps. Under the influence of the same ground acceleration, the upper portion of the contained liquid responds as if it were a solid mass flexibly attached to the tank wall. This portion, which oscillates at its own natural frequency, is identified as the convective component, mc, and exerts a horizontal force, Pc, on the wall. The convective component oscillations are characterized by sloshing whereby the liquid surface rises above the static level on one side of the tank and drops below that level on the other side.

## Slide 39: Tanks and Vessels Design Basis
Convective (sloshing) forces to be evaluated at 0.5% damping at convective period Tc.
  1.5 is used to convert 5% damping to 0.5% damping
Impulsive and convective components to be combined by direct sum or SRSS.
Vertical earthquake forces must be considered (hydrodynamic hoop forces and vertical inertia forces).
Notes: Slide 39 continues the discussion of the unique design considerations for tanks and vessels storing liquids.

## Slide 40: Tanks and Vessels Strength and Ductility
There are 4 special considerations for tanks and vessels that will be discussed in the following slides:
  The importance of providing piping flexibility (15.7.4).
  The importance of anchor rod stretch (15.7.5).
  The importance of providing seismic freeboard (15.7.6.1.2).
  Special design requirements for vessel support skirts.
Notes: Slide 40 highlights four special considerations that will be discussed in later slides.

## Slide 41: Nonbuilding Structures Not Similar to Buildings
Example 17.6.2 Flat-Bottom Gasoline Tank
Figure 17-7 Storage tank section (1.0 ft = 0.3048 m)
Notes: The figure shows shows an elevation view of a steel gasoline storage tank.
Slide 41 shows Example 17.6.2 – Flat-Bottom Gasoline Tank. The illustration shows an elevation view of a steel gasoline storage tank. The diameter of the tank is 120 feet and the height of the tank is 40 feet. The high liquid level is shown as 33 feet and the low liquid level is shown as 3 feet. The tank is shown with a cone roof supported by a 20 inch diameter Schedule 10 pipe center column and (54) W14x26 rafters. The cone roof is sloped up to the center of the tank by 3’-9 5/16. The tank is equipped with an aluminum internal floating roof with a high rest position of 6 feet and a low rest position of 3 feet. The steel bottom of the tank is ¼-inch thick and sloped up to the center of the tank by 6 inches. The tank shell is shown with five shell rings. Ring 1 is 0.401 inches thick and rings 2 through 5 are 5/16 inches thick.
The seismic response of tanks and vessels can be significantly different from that of buildings. For a structure composed of interconnected solid elements, it is not difficult to recognize how ground motions accelerate the structure and cause inertial forces within the structure. Tanks and vessels, where empty, respond in a similar manner.
Where there is liquid in the tank, the response is much more complicated. As earthquake ground motions accelerate the tank shell, the shell applies lateral forces to the liquid. The response of the liquid to those lateral forces may be amplified significantly if the period content of the earthquake ground motion is similar to the natural sloshing period of the liquid.
Earthquake-induced impulsive fluid forces are those calculated assuming that the liquid is a solid mass. Convective fluid forces are those that result from sloshing in the tank. It is important to account for convective forces on columns and appurtenances inside the tank, because they are affected by sloshing in the same way that waves affect a pier in the ocean.
Freeboard considerations are critical. Oftentimes, the roof acts as a structural diaphragm. If a tank does not have sufficient freeboard, the sloshing wave can rip the roof from the wall of the tank. This could result in failure of the wall and loss of the liquid within.
Seismic design for liquid-containing tanks and vessels is complicated. The fluid mass that is effective for impulsive and convective seismic forces is discussed in AWWA D100 and API 650.

## Slide 42: Nonbuilding Structures Not Similar to Buildings
This example illustrates the calculation of the base shear and the required freeboard using the procedure outlined in API 650 for a petrochemical storage tank in a refinery tank farm (Figure 17-7).
The vertical design response spectral acceleration, Sav, for use in the determination of shell hoop stress will also be calculated according to the provisions of ASCE 7-16 Sections 11.9 and 15.1.4.
An impoundment dike is not provided to control liquid spills.
According to Standard Section 15.7.8.1, the governing reference document for this tank is API 650.
Notes: Slide 42 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
API 650 is written in terms of allowable stress design (ASD) while the seismic requirements of the ASCE 7-16 are written in terms of strength design. API 650 translates the force equations from the ASCE 7-16 by substituting Rw for R, where Rw is equal to 1.4R. For the purposes of this example, all loads are calculated in terms of strength design. Where appropriate, API 650 equations are referenced for the determination of impulsive and convective (sloshing) masses.

## Slide 43: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Risk Category (Section 1.5.1) = III (The tank is used for storage of toxic or explosive material based on an LC(50) value of 5.2 mg per liter taken from a typical MSDS for gasoline.)
  Importance Factor, Ie (Table 1.5-2) = 1.25
  Short-period Response, SS = 1.236
  One-second Period Response, S1 = 0.406
  Long-period Transition Period, TL = 6 sec.
  Site Class = C
Notes: Slide 43 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 44: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Design Spectral Acceleration Response Parameters
    SDS = 0.824
    SD1 = 0.376
  Seismic Force-resisting System (Table 15.4-2)
    Flat-bottom, ground-supported, self-anchored steel tank
  Response Modification Coefficient, R = 2.5
Notes: Slide 44 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 45: Nonbuilding Structures Not Similar to Buildings
Based on ASCE 7-16 Section 15.7.6 Note a, the impulsive acceleration is set equal to SDS. Sai = SDS = 0.824
Seismic (impulsive) weight. Wtank = 490.0 kips
WGas = π(60 ft)2(33 ft)(0.0474 kip/ft3)(Wi/Wp) = 17,691 kips (0.316) = 5,590 kips
Notes: Slide 45 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
API 650 Section E.4.5.1 does not require the computation of the natural period for the first mode of vibration. The impulsive acceleration is assumed to be equal to SDS.

## Slide 46: Nonbuilding Structures Not Similar to Buildings
The ratio Wi/WT (= 0.316) was determined from Equation E.6.1.1-1 (only valid for D/H ≥ 1.333) of API 650 for a diameter-to-liquid height ratio of 3.636 as shown below:
Wi = Wtank + Wiwater = 490 + 5590 = 6,080 kips
Notes: Slide 46 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 47: Nonbuilding Structures Not Similar to Buildings
Base Shear. According to ASCE 7-16 Equation 15.7-5:
Notes: Slide 47 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 48: Nonbuilding Structures Not Similar to Buildings
Convective Response
Natural period for the first mode of sloshing. Using ASCE 7-16 Equation 15.7-12:
Notes: Slide 48 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 49: Nonbuilding Structures Not Similar to Buildings
Spectral acceleration. Using ASCE 7-16 Equation 15.7-11 with Tc > TL = 6 seconds:
Seismic (convective) weight. Wc = WGAS (Wc/Wp) = 17,691 (0.640) = 11,322 kips
Notes: Slide 49 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank

## Slide 50: Nonbuilding Structures Not Similar to Buildings
The ratio Wc/Wp (= 0.640) was determined from Equation E.6.1.1-3 (valid for all D/H) of API 650 for a diameter-to-liquid height ratio of 3.636 as shown below:
Base shear. According to ASCE 7-16 Equation 15.7-6:
Notes: Slide 50 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
Item b of Standard Section 15.7.2 indicates that impulsive and convective components may, in general, be combined using the SRSS method. ASCE 7-16 Equation 15.7-4 requires that the direct sum be used for ground-supported storage tanks for liquids. Note b under ASCE 7-16 Section 15.7.6.1 allows the use of the SRSS method in lieu of using ASCE 7-16 Equation 15.7-4.

## Slide 51: Nonbuilding Structures Not Similar to Buildings
Minimum Freeboard δs = 0.42DiISac = 0.42(120 ft)(1.25)(0.0433) = 2.73 ft Required freeboard = 0.7 δs = 1.91 ft
Notes: Slide 51 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
Because the tank is assigned to Risk Category III and SDS is greater than 0.50, the freeboard provided must be at least 70 percent of the full value of the theoretical wave height (based on TL = 4 s). For the case of Risk Category III tanks, the wave height is calculated based on the convective acceleration using a value of TL equal to 4 seconds and an importance factor of 1.25 according to ASCE 7-16 Section 15.7.6.1, Note (d). ASCE 7-16 Table 15.7-3 indicates that a minimum freeboard equal to 0.7δs is required for this tank. Using ASCE 7-16 Equation 15.7-13 and Note (d) (sets Ie = 1.25 and TL to 4 seconds for Risk Category III for wave height determination) from Standard Section 15.7.6.1:
The 7 feet of freeboard provided also includes a 3-foot allowance for an aluminum internal floating roof and the roof framing. The seismic freeboard must be sufficient to avoid forcing the floating roof into the fixed roof framing. The freeboard provided is adequate. The reduced freeboard requirement recognizes that providing seismic freeboard for Risk Category I, II, or III tanks is an economic decision (reducing damage) and not a life-safety issue. Because of this, a reduced freeboard is allowed. If secondary containment were provided, no freeboard would be required based on ASCE 7-16 Table 15.7-3, Footnote (b).
ASCE 7-16 Table 15.7-3, Section 15.7.6.1, and Section 15.7.6.1.2 have been reorganized for increased clarity. No technical changes have occurred relative to the discussions above. Note (d) referenced above has become subsection (c) and placed in Section 15.7.6.1.2. Footnote (b) of ASCE 7-16 Table 15.7.3 has been moved to ASCE 7-16 Section 15.7.6.1.2 (d)(3).

## Slide 52: Nonbuilding Structures Not Similar to Buildings
Vertical Seismic, Ev
  ASCE 7-16 Section 15.1.4 requires that the design vertical response spectral acceleration, Sav, used to determine hydrodynamic hoop forces in cylindrical tanks be determined using the requirements of ASCE 7-16 Section 15.7.2c(2).
  Natural vertical period. Using ASCE 7-16 Equation C15.7-2:
Notes: Slide 52 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
ASCE 7-16 Section 11.9 defines the vertical response spectrum at the MCER level. Only ASCE 7-16 Chapter 15 invokes the provisions of Section 11.9. Specifically, ASCE 7-16 Section 15.1.4 requires the use of the provisions of Section 11.9 for tanks, vessels, hanging structures, and nonbuilding structures incorporating horizontal cantilevers.

## Slide 53: Nonbuilding Structures Not Similar to Buildings
Vertical Seismic, Ev
  Using ASCE 7-16 Equation 11.9.2-4 for the natural vertical period Tv = 0.182 s, the vertical response spectral acceleration at the MCER is:
  Cv = 1.15
Notes: Slide 53 is a continuation Example 17.6.2 – Flat-Bottom Gasoline Tank
The coefficient Cv is determined from ASCE 7-16 Table 11.9.2-1 and is based on the value of SS and the site class. According to ASCE 7-16 Section 11.9.3, the design vertical response spectral acceleration, Sav, is taken as two-thirds of SaMv.

## Slide 54: Nonbuilding Structures Not Similar to Buildings
Example 17.7 Vertical Vessel
Figure 17-7 Vertical vessel (1.0 ft = 0.3048 m)
Notes: The figure shows an elevation view of a vertical pressure vessel with a cylindrical shell 10 feet in diameter with two hemispherical heads.
Slide 54 shows Example 17.7 – Vertical Vessel. The illustration shows an elevation view of a vertical pressure vessel with a cylindrical shell 10 feet in diameter with two hemispherical heads. The vessel is supported on by a 3/8 inch thick support skirt. The overall height of the vessel above grade is 100 feet.

## Slide 55: Nonbuilding Structures Not Similar to Buildings
This example illustrates the calculation of the base shear using the ELF procedure for a flexible vertical vessel (Figure 17-8). The vertical vessel contains highly toxic material (Risk Category IV).
The weight of the vertical vessel plus contents is 300,000 pounds.
Notes: Slide 55 is a continuation of Example 17.7 – Vertical Vessel.
Large boilers in coal-fired electric power plants generally are suspended from the supporting steel near the roof level. Additional lateral supports (called buck stays) are provided near the bottom of the boiler. The buck stays resist lateral forces but allow the boiler to move vertically. Lateral seismic forces are resisted at the roof and at the buck stay level. Close coordination with the boiler manufacturer is required in order to determine the proper distribution of seismic forces.

## Slide 56: Nonbuilding Structures Not Similar to Buildings
ASCE 7-16 Section 15.4.4 allows the fundamental period of a nonbuilding structure to be determined using a properly substantiated analysis.
The period of the vertical vessel is calculated using the equation for a uniform vertical cylindrical steel vessel as found in Appendix 4.A of ASCE (2011).
where: T = period (s)
W = weight (lb/ft)
H = height (ft)
D = diameter (ft)
T = shell thickness (in.)
Notes: Slide 56 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 57: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Risk Category (Section 1.5.1) = IV (Highly toxic material)
  Importance Factor, Ie (Table 1.5-2) = 1.5
  Site Class (Standard Sec. 11.4.2) = D
  Design Spectral Acceleration Response Parameters
    SDS = 1.86
    SD1 = 0.79
Notes: Slide 57 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 58: Nonbuilding Structures Not Similar to Buildings
Seismic Parameters
  Seismic Force-resisting System (Table 15.4-2)
    Elevated tanks, vessels, bins, or hoppers: Single pedestal or skirt supported – welded steel with special detailing.
  Response Modification Coefficient, R = 3
Notes: Slide 58 is a continuation of Example 17.7 – Vertical Vessel.
The vertical vessel used in this example is a skirt-supported distributed mass cantilevered structure. There are three possible entries in ASCE 7-16 Table 15.4-2 that describe the vessel in question:
Elevated tanks, vessels, bins, or hoppers: Single pedestal or skirt supported – welded steel.
Elevated tanks, vessels, bins, or hoppers: Single pedestal or skirt supported – welded steel with special detailing.
All other steel and reinforced concrete distributed mass cantilever structures not covered herein including stacks, chimneys, silos and skirt-supported vertical vessels that are not similar to buildings.
All three options are keyed to the detailing requirements of Standard Section 15.7.10. Two of the options specifically require that Items (a) and (b) of ASCE 7-16 Section 15.7.10 be met. The intent of ASCE 7-16 Section 15.7.10 and ASCE 7-16 Table 15.4-2 is that skirt-supported vessels be checked for seismic loads based on R/Ie = 1.0 if the structure is assigned to Risk Category IV or if an R factor of 3.0 is used in the design of the vessel. Skirt-supported vessels fail in buckling, which is not a ductile failure mode, so a more conservative design approach is required. The R/Ie = 1.0 check typically will govern the design of the skirt over using loads determined with an R factor of 3 in a moderate to high area of seismic activity. The only benefit of using an R factor of 3 in this case is in the design of the foundation. The foundation is not required to be designed for the R/Ie = 1.0 load. For the R/Ie = 1.0 load, the skirt can be designed based on critical buckling (factor of safety of 1.0). The critical buckling strength of a skirt can be determined using a number of published sources. The two most common methods for determining the critical buckling strength of a skirt are ASME BVPC Section VIII, Division 2, Paragraph 4.4 using a factor of safety of 1.0 and AWWA D100 Section 13.4.3.4. An example of calculating the critical buckling strength of the skirt using ASME BVPC Section VIII, Division 2, Paragraph 4.4 is provided.

## Slide 59: Nonbuilding Structures Not Similar to Buildings
Seismic response coefficient. Using ASCE 7-16 Equation 12.8-2:
From analysis, T = 0.762 seconds. Using ASCE 7-16 Equation 12.8-3, CS does not need to exceed:
Notes: Slide 59 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 60: Nonbuilding Structures Not Similar to Buildings
Using ASCE 7-16 Equation 12.8-5, Cs must not be less than:
  Cs = 0.044IeSDS ≥ 0.03 = 0.044(1.5)(1.86) = 0.123
ASCE 7-16 Equation 12.8-3 controls; Cs = 0.518.
Base shear. Using Standard Equation 12.8-1:
  V = CsW = 0.518(300 kips) = 155.4 kips
Notes: Slide 60 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 61: Nonbuilding Structures Not Similar to Buildings
Design in the North-South Direction
  Seismic weight. Calculate the total seismic weight, W, as follows:. W = WDL + WBoiler = 16,700 kips + 31,600 kips = 48,300 kips
  Base shear. Using ASCE 7-16 Equation 12.8-1: V = CsW = 0.143(48,300 kips) = 6,907 kips
Notes: Slide 61 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 62: Nonbuilding Structures Not Similar to Buildings
Figure 17-9 Vertical distribution of seismic forces
Notes: The figure shows the vertical distribution of seismic forces on a vertical vessel of height H for the period of the vessel ranging between 0.5 and 2.5 seconds.
Slide 62 is a continuation of Example 17.7 – Vertical Vessel. The illustration shows three figures. The figure on the left shows the vertical distribution of seismic forces on a vertical vessel of height H if the period of the vessel is 0.5 s or less. The distribution is an inverted triangle (k = 1). The centroid of the seismic forces is shown as 2/3H. The figure in the center shows the vertical distribution of seismic forces on a vertical vessel of height H if the period of the vessel falls between 0.5 s and 2.5 s. The distribution is an inverted curve (k between 1 and 2). The centroid of the seismic forces is shown as [(k+1)/(k+2)]H. The figure on the right shows the vertical distribution of seismic forces on a vertical vessel of height H if the period of the vessel is 2.5 s or greater. The distribution is an inverted parabola (k = 2). The centroid of the seismic forces is shown as 3/4H.
ASCE 7-16 Section 12.8.3 defines the vertical distribution of seismic forces in terms of an exponent, k, related to structural period. If the structural period is less than or equal to 0.5 second, k = 1 and results in an inverted triangular distribution of forces. If the structural period is greater than or equal to 2.5 seconds, k = 2 and results in a parabolic distribution of forces. For periods between 0.5 second and 2.5 seconds, the value of k is determined by linear interpolation between 1 and 2. The significance of the distribution requirements of ASCE 7-16 Section 12.8.3 is that the height of the centroid to the horizontal seismic force increases (thus increasing the overturning moment) as the period increases above 0.5 second (Figure 17-9).

## Slide 63: Nonbuilding Structures Not Similar to Buildings
Referring to Figure 17-9
  Once k is determined, the height to the centroid, , of the horizontal seismic force is equal to:
  For the vessel period of T = 0.762 second:
Notes: Slide 63 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 64: Nonbuilding Structures Not Similar to Buildings
Referring to Figure 17-9
  The value of is then calculated as:
  The overturning moment is then calculated as: M = = 155.4(68.1) = 10,583 ft-kips
Notes: Slide 64 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 65: Nonbuilding Structures Not Similar to Buildings
Critical Buckling Check
  Seismic response coefficient with R/Ie = 1.0. Using ASCE 7-16 Equation 12.8-2:
  Using ASCE 7-16 Equation 12.8-3, Cs does not need to exceed:
  ASCE 7-16 Equation 12.8-3 controls; Cs = 1.037
Notes: Slide 65 is a continuation of Example 17.7 – Vertical Vessel.
The intent of ASCE 7-16 Section 15.7.10 and ASCE 7-16 Table 15.4-2 is that skirt-supported vessels be checked for seismic loads based on R/Ie = 1.0 (critical buckling check) if the structure is assigned to Risk Category IV or if an R factor of 3.0 is used in the design of the vessel. For the R/Ie = 1.0 load, the skirt can be designed based on critical buckling (factor of safety of 1.0). The critical buckling strength of a skirt can be determined using a number of published sources. In this example, the method described in ASME BVPC Section VIII, Division 2, Paragraph 4.4 using a factor of safety of 1.0 will be used.

## Slide 66: Nonbuilding Structures Not Similar to Buildings
Base shear. Using ASCE 7-16 Equation 12.8-1: V = CsW = 1.037(300 kips) = 311.0 kips
Vertical distribution of seismic forces. Moment arm from Figure 17-9:
The overturning moment is then calculated as: M = = 311.0(68.1) = 21,181 ft-kips
Notes: Slide 66 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 67: Nonbuilding Structures Not Similar to Buildings
Stresses at base of skirt.
  Axial stress (fa) = P/A = 300,000/(π(10)12(0.375)) = 2,122 psi
  Bending stress (fb) = M/S = 21,181(1,000)12/[(0.375)π(10(12))2/4] = 59,930 psi
  Shear stress (fv) = 2V/A = 2(311.0)(1,000) /(π(10)12(0.375)) = 4,400 psi
Notes: Slide 67 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 68: Nonbuilding Structures Not Similar to Buildings
Evaluation of combined axial stress, bending stress, and shear stress.
  Uniform Axial Compression (governed by column buckling):
    Allowable longitudinal stress = Fca = 23,081 psi
  Axial compression due to bending moment:
    Allowable bending stress = Fba = Fxc = 25,770 psi
Notes: Slide 68 is a continuation of Example 17.7 – Vertical Vessel.
The procedures outlined in ASME BVPC Section VIII, Division 2, Paragraph 4.4 using a factor of safety of 1.0 will be used below to determine the adequacy of the vessel support skirt under seismic loads based on R/Ie = 1.0. The ASME procedures check many different limit states to arrive at the allowable stress for a particular loading. The example below only identifies the governing conditions for this particular vessel. Please note that all “allowable” stresses shown below are based on a factor of safety of 1.0. Nomenclature is defined in ASME BVPC Section VIII, Division 2.

## Slide 69: Nonbuilding Structures Not Similar to Buildings
In-plane shear: av = 0.8 Cv = 0.2967 Do/t = 320 nv = 0.8197 Allowable shear stress = Fva = nvFve = 17,631 psi
Notes: Slide 69 is a continuation of Example 17.7 – Vertical Vessel.

## Slide 70: Nonbuilding Structures Not Similar to Buildings
Combination of uniform axial compression, axial compression due to bending moment, and shear in the absence of hoop compression:
Notes: Slide 70 is a continuation of Example 17.7 – Vertical Vessel.
The support skirt in this example is inadequate for the seismic loads based on R/Ie = 1.0. The thickness of the support skirt must be increased and the critical buckling check repeated.

## Slide 71: Questions?
Notes: Slide 71 is the “question” slide.

## Slide 72: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.