## Slide 1: Foundation and Liquefaction Design Ian McFarlane, S.E. and Stephen K. Harris, S.E. Originally developed by Michael Valley, S.E.
Disclaimer

## Slide 2: FOUNDATION AND LIQUEFACTION DESIGN
TABLE OF CONTENTS:
Overview of Foundation Design
Shallow Footing Example
Combined Footing Example
Pile Foundation Example
Design for Differential Settlement Example
Design for Liquefiable Soil Example
Notes: Table of contents, outline of material that will be presented

## Slide 3: FOUNDATION DESIGN
Proportioning Elements for:
Transfer of Seismic Forces
Strength and Stiffness
Shallow and Deep Foundations
Elastic and Plastic Analysis
Notes: The subtitles are effectively a table of contents, although the topics are not really treated in that specific order. This unit is primarily aimed at the structural engineering of foundations, not at the geotechnical engineering.
This presentation relates to example computations in Chapter 7 of the FEMA P1051, NEHRP Recommended Provisions: Design Examples.

## Slide 4: Load Path and Transfer of Seismic Forces
Force on a pile
EQ on unloaded pile
Pile supporting structure
Inertial force
Unmoving soil
EQ Motion
deflected
shape
soil
pressure
deflected
shape
deflected
shape
soil
pressure
soil
pressure
Notes: The figure shows a representation of a pile supported structure showing deflection and soil pressure on the pile due two effects. First, is forces on the pile due to inertial forces from the structure. Second, is forces on the pile due to soil pressure from the soil field activated by ground motion that is not in phase with the inertial forces. A third portion of the figure shows both effects superimposed with deflected shape and soil pressure.
First model: soil pressures in unmoving soil caused by force at top of deep pile; most of stress resisted at top of pile; only small stresses below about twice the characteristic length of pile. Second model: unloaded pile subject to earthquake ground motion; small stresses induced by upper levels of soil lagging behind deep motion. Note opposing directions of “push”. Third model: both types of force act on pile. The lag of structure induces inertial forces at top of pile similar to static force in first model; net force shape similar to static situation.

## Slide 5: Load Path and Transfer of Seismic Forces foundation force transfer
EQ motion
Passive earth
pressure
Friction
Shallow
Notes: The figure shows a representation of a single story frame structure supported on shallow foundations. Earthquake motion is show as being induced and the deformed shape of the structure is shown. Resistance to the earthquake motion is shown as passive earth pressure on the vertical face of the footing combined with friction on the base of the footing.
As building lags behind ground motion, induced inertial forces must be transferred between footing and soil. Design may consider that inertial forces are transferred as passive earth pressure on face of footing, friction on bottom of footing, or both.

## Slide 6: Load Path and Transfer of Seismic Forces soil to foundation force transfer
Instructional Material Complementing FEMA 1051, Design Examples
Deep
EQ Motion
Motion
Soil
pressure
Bending
moment
Notes: The figure shows a representation of a single story frame structure supported on deep foundations. Earthquake motion is show as being induced and the deformed shape of the structure is shown. Resistance to the earthquake motion is shown as soil pressure against the deep foundation elements with a bending moment diagram from the induces pressure.
Same single story structure; now on deep pile foundation. One leg shows pile displacements; other shows resulting earth pressures; third diagram shows bending moment in pile. One reference that has long been used for laterally loaded piles is the Navy Design Manual 7.2, Foundations and Earth Structures. However, it and most other older methods are based upon assumptions of linear behavior in soil. Over the past two decades considerable progress has been made in developing design tools rooted in the strongly nonlinear behavior of soil. “LPILE” is one widely used example that allows the user to specify soil parameters that model resistance of soil to lateral movement of piles.

## Slide 7: Load Path and Transfer of Seismic Forces vertical pressures - shallow
Instructional Material Complementing FEMA 1051, Design Examples
EQ motion
Overturning moment
Notes: The figure shows a representation of a multi story building on a shallow foundation with an overturning moment that is induced by earthquake motion. Resistance is shown via passive pressure on the vertical face of the footing and a varying bearing pressure underneath the footing.
As aspect ratio of building height to width increases, overturning moment becomes significant; induced vertical forces must be transferred in addition to horizontal pressures. (Similar vertical forces in footing result from column moments not specifically related to overturning.) Slide shows overturning moment being resisted below basement of medium sized building; horizontal pressures are transferred at the basement walls.

## Slide 8: Load Path and Transfer of Seismic Forces vertical pressures - deep
Instructional Material Complementing FEMA 1051, Design Examples
EQ Motion
Overturning
moment
Notes: The figure shows a multi story building supported on deep foundations subjected to earthquake motion that induces an overturning moment in the structure. Resistance to the overturning is shown with an axial force couple between the deep foundation elements.
This example of tall building with shear wall continuing through deep basement shows that the horizontal and vertical forces can be resisted by different portions of foundation structure. Basement wall resists horizontal forces near ground surface; vertical forces resisted by piles at base of wall.

## Slide 9: Allowable Stress Design vs Strength Design
Instructional Material Complementing FEMA 1051, Design Examples
Strength Design
  Permitted in 2015 Standard
  Nominal strength with phi factors
  Allows direct comparison of foundation capacity with superstructure capacity
Allowable Stress Design
  Traditional/historic approach
  Allowable geotechnical values have inherent factor of safety
  Requires separate ASD load combination
Notes: Allowable stress design and strength design are two methods for geotechnical design permitted. ASD is the traditional/historic approach, Strength design is new to the 2015 provisions. Strength design determines capacity via nominal strength with a strength reduction factor (phi). This approach allows direct comparison of foundation capacity with superstructure capacity.

## Slide 10: Allowable Stress Design vs Strength Design
Instructional Material Complementing FEMA 1051, Design Examples
Nominal Strength can be:
  Nominal strength associated with anticipated failure mechanism
  Nominal strength associated with limitation on maximum deformation at failure
Settlement based on sustained loads rather than the loading associated with nominal strength should be considered
Notes: Nominal strength can represent different failure mechanisms of either strength of deformation basis. Be aware that many foundations are controlled by settlement under sustained loads rather than the loading associated with nominal strength.

## Slide 11: Allowable Stress Design vs Strength Design
Instructional Material Complementing FEMA 1051, Design Examples
Nominal Strength Example
  Strength reduction factor Φ=0.45 for compression (bearing pressure)
Allowable Stress Example
  Factor of safety of ~3.0
Notes: Comparison of phi factors associated with nominal strength to allowable stress factor of safety.

## Slide 12: Foundation Design Concepts
Instructional Material Complementing FEMA 1051, Design Examples
Most foundation failures are associated with excessive foundation movement, not loss of load-bearing capacity
Maintaining a reasonably consistent service load-bearing pressure is encouraged to minimize differential settlement
Notes: Most foundation failures are associated with excessive foundation movement, and not loss of load bearing capacity. Keeping bearing pressures consistent can help with minimizing differential settlement.

## Slide 13: Design of Concrete Footings
Instructional Material Complementing FEMA 1051, Design Examples
ACI 318 References
  Chapters 7,8 – One way, Two-way slabs referenced for detailing requirements
  Chapter 13 – General Foundations
  Chapter 18 – Seismic Provisions
  Chapter 22 – Sectional Strength
Notes: Reference to ACI 318 for requirements on design of concrete footings.

## Slide 14: Reinforced Concrete Footings: Basic Design Criteria (concentrically loaded)
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The illustration shows three separate figures. The first shows a plan view of a typical spread footing supporting a single column. The critical section for flexure is highlighted as the entire width of the footing location at the face of the column. The second figure shows the same typical spread footing supporting a single column. The critical section for one-way shear is highlighted as the entire width of the footing at the location d away from the face of the column. The third figure also shows the typical spread footing supporting a single column. The critical section for two-way shear is highlighted as the region at d/2 away from the face of the column on all sides.
Reinforced concrete footings are proportioned according the provisions of ACI 318, Building Code Requirements for Structural Concrete. It is often opined that foundations should not yield, due to the high cost of foundation repair. However, nonlinear soil behavior is common in strong ground shaking, and it is traditional to design foundations for the reduced forces computed with the response modification factor, R, used for the superstructure. Neither the NEHRP Recommended Provisions nor earlier model building codes required the use of amplified forces for foundation design.

## Slide 15: Footing Subject to Compression and Moment: Uplift Nonlinear
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The illustration shows six figures. The first, part (a), shows an isometric view of a rectangular spread footing with dimensions L and B in plan. Applied loading is indicated as P (axial load) and M (moment), with eccentricity e=M/P. The next five figure show a cross section through the footing of part (a) with possible bearing pressure distributions based on the loading indicated. Part (b) indicates elastic bearing pressure distribution with no uplift, varying in magnitude across the section. Part (c) indicates elastic bearing pressure on the verge of uplift, with zero bearing pressure at one side and maximum on the opposite side. Part (d) indicates elastic bearing pressure with uplift on one side of the footing, with elastic bearing pressure over distance L’ only. Part (e) shows a bearing pressure with some plastification. Part (f) shows bearing pressure at the plastic limit over a distance ‘x’.
ASCE 41 has a good discussion of the plastic behavior of soil beneath eccentrically loaded footings. Just as for analysis of structural members, plastic analysis of a footing is simple “by hand”, but not so with a computer.
Both uplift and nonlinear behavior introduce complications in conventional analysis. Many commercially available software packages for structural analysis now handle the uplift case; a smaller set can also handle nonlinear behavior.

## Slide 16: Example 7-story building: shallow foundations designed for perimeter frame and core bracing
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The illustration shows a framing plan of a perimeter steel moment resisting frame with bracing in a central core, of 7 bays in east-west direction and 5 bays in north-south direction.
Title slide for 7-story building showing plan of steel building.

## Slide 17: Shallow Footing Examples
Instructional Material Complementing FEMA 1051, Design Examples
Allowable Bearing (Settlement)
2,000 psf B<20 ft
1,000 psf B<40 ft
Density = 125 pcf
Friction angle = 33o
Bearing Capacity
3,000B psf (Square)
4,000B’ psf (Rectangular)
B = footing width (ft)
B’ = average width of compressed area (ft)
ϕ=0.45
Soil parameters:
Medium dense sand
(SPT) N = 20
Notes: The gravity load allowables are set to control settlements. The values between 20 and 40 feet should be interpolated. The bearing capacity is the classic value from theoretical soil mechanics (normal gravity loads are checked). The subject of strength design in soils is in its infancy, and many geotechnical professionals are not yet comfortable with strength design concepts.
Note that the term phi is Resistance Factor for bearing capacity. B is the footing width.

## Slide 18: Footings proportioned for gravity loads alone
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The size of the square footing is controlled by the allowable bearing pressure at total loads, and the thickness is controlled by two-way shear at the critical section (“punching shear”).
The point of this information is primarily for later comparison with footings designed for seismic loads.

## Slide 19: Design of footings for perimeter moment frame
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The illustration shows a framing plan of a perimeter steel moment resisting frame, of 7 bays in east-west direction and 5 bays in north-south direction. Columns are oriented with strong axis bending in the direction of the frame. Moment connections are indicated between the beam and columns around the perimeter frame.
The only portion of the steel frame that resists lateral forces is at the perimeter, thus, the only footings that will be affected by the seismic load are at the perimeter.

## Slide 20: 7 Story Frame, Deformed
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The diagram shows a three dimensional moment frame analysis of a 7 story building. The undeformed and deformed shape after application of lateral load is shown.
The image is taken from the RAM Frame analysis used to design the steel moment resisting frame for seismic loads.

## Slide 21: Combining Loads
Instructional Material Complementing FEMA 1051, Design Examples
Maximum downward load:
  1.2D + 0.5L + E
Minimum downward load:
  0.9D + E
Definition of seismic load effect E:
  E = r1QE1 + 0.3 r2QE2 +/- 0.2 SDSD
  rx = 1.0 ry = 1.0 and SDS = 1.0
Notes: Load combinations for strength-based design, which is the fundamental method for earthquake resistant design.
Greek rho is the redundancy factor. Q is the effect of horizontal seismic motions. The 0.2SdsD is an approximation for the effect of vertical earthquake motions.
For the footings, the horizontal motions produce vertical and horizontal forces, as well as bending moments, at the base of each column. Dead and Live loads are taken to produce only vertical forces in this example.

## Slide 22: Reactions
Instructional Material Complementing FEMA 1051, Design Examples
Grid |  | Dead | Live | Ex | Ey
A-5 | P Mxx Myy | 203.8 k | 43.8 k | -3.8 k 53.6 k-ft -243.1 k-ft | 21.3 k -1011.5 k-ft 8.1 k-ft
A-6 | P Mxx Myy | 103.5 k | 22.3 k | -51.8 k 47.7 k-ft -246.9 k-ft | -281.0 k -891.0 k-ft 13.4 k-ft
Notes: Grid A-6 is at the lower left corner of the plan, and A-5 is adjacent. (Go back three slides to show the location on the plan.) Recall that the seismic reactions can be positive or negative; what is given here is for motion in the positive x and y directions. Carefully note that subscripts x and y on the load effect E refer to the global north-south and east-west, respectively, but the subscripts x and y on the moments at the column bases refer to the local strong and weak axes, respectively, which is just the opposite as the global directions, unfortunately.
The most significant point of this slide is that seismic uplift at A-6 exceeds the dead load by a considerable margin. It is possible to place a footing with sufficient size to resist the uplift and the overturning moment, but it is much more economical to combine one footing for the two locations. These reactions include the effects of horizontal torsion on the system. Also recall that the footing must resist horizontal forces.

## Slide 23: Reduction of Overturning Moment
Instructional Material Complementing FEMA 1051, Design Examples
NEHRP Provisions allow base overturning moment to be reduced by 25% at the soil-foundation interface
For a moment frame, the column vertical loads are the resultants of base overturning moment, whereas column moments are resultants of story shear
Thus, use 75% of seismic vertical reactions
Notes: The Provisions allow an overturning moment reduction of 25% at the soil-foundation interface.

## Slide 24: Additive Load w/ Largest eccentricity
Instructional Material Complementing FEMA 1051, Design Examples
Combining loads on footings A-5 and A-6, applying the 0.75 multiplier for overturning effects to the axial loads, and neglecting the weight of the foundation and overlying soil,
P = 688 kips
Mxx = -6,717 ft-kips
Myy = -126 ft-kips (which is negligible)
Notes: None of these loads include the weight of the footing.
P is positive in compression. M is positive by the local right hand rule.
This is not the maximum downward load; it is the maximum ratio of moment to axial load for the additive combos.

## Slide 25: Counteracting Load w/ Largest e
Instructional Material Complementing FEMA 1051, Design Examples
Again combining loads on footings A-5 and A-6, including the overturning factor, and neglecting the weight of the footing and overlying soil,
P = 332 kips
Mxx = -5,712 ft-kips
Myy = -126 ft-kips (negligible)
Notes: Note that the net vertical load is upward without the weight of the footing. It so happens that this combo also gives the maximum eccentricity, when combined with the weight of footing and soil.

## Slide 26: Elastic Response
Instructional Material Complementing FEMA 1051, Design Examples
P
M
W
R
L
e
Objective is to set L and W to satisfy equilibrium and avoid overloading soil
Successive trials usually necessary
Notes: A section of a shallow foundation is show of with L, with applied axial load P and overturning moment M. Weight of the footing is shown as a downward force vector W. Resistance is shown by a resultant upward force vector R at an eccentricity e which is shown as a triangular distribution of soil pressure.
Slide is drawn for the case with substantial moment, such that uplift will occur at the heel. Note that eccentricity e changes as W changes.
For our footing, L will exceed 25 feet by some margin, given that the two columns are 25 feet apart.

## Slide 27: Additive Combination
Instructional Material Complementing FEMA 1051, Design Examples
Given P = 688 k, M =6717 k-ft
e = M / P = 9.76 ft
Try L = 40 ft, B = 9 ft
L/6 < e < L/2 therefore elastic with some uplift
L’ = 3 (L/2-e) = 30.7’
qmax = 2 P / [3 B(L/2-e)]
qmax = 4.98 ksf
Notes: The illustration shows a section through a spread footing supporting two columns. An applied load of P (axial) and M (moment) are indicated. The resulting bearing pressure under the footing is shown as an elastic bearing pressure that varies from 0 ksf to qmax of 4.98 ksf over length L’=30.7 feet.
Initial approximation of W is simply to keep the resultant of earth pressure within the footing. It must be somewhat larger in order to control the bearing pressures.
Note that the load factor on W does not include the amplifier for vertical seismic acceleration; this is the author’s interpretation of the NEHRP Provisions.
The minimum B used to find the nominal bearing capacity is found by comparing the width of the footing and the half length of the loaded area. The half length is used because the soil pressure is not uniform.

## Slide 28: Additive Combination
Instructional Material Complementing FEMA 1051, Design Examples
Bearing Capacity:
Qns = 4,000B’ = 4,000 min (B, L’/2)
Qns = 4,000 min (9, 30.7/2) = 36,000 psf
Design bearing capacity:
ϕQns = 0.45 (36,000 psf)
ϕQns = 16.2 ksf > 4.98 ksf
OK by elastic analysis
Notes: The illustration shows a section through a spread footing supporting two columns. An applied load of P (axial) and M (moment) are indicated. The resulting bearing pressure under the footing is shown as an elastic bearing pressure that varies from 0 ksf to qmax of 4.98 ksf over length L’=30.7 feet.
Initial approximation of W is simply to keep the resultant of earth pressure within the footing. It must be somewhat larger in order to control the bearing pressures.
Note that the load factor on W does not include the amplifier for vertical seismic acceleration; this is the author’s interpretation of the NEHRP Provisions.
The minimum B used to find the nominal bearing capacity is found by comparing the width of the footing and the half length of the loaded area. The half length is used because the soil pressure is not uniform.

## Slide 29: Plastic Response
Instructional Material Complementing FEMA 1051, Design Examples
P
M
W
R
L
e
R
Same objective as for elastic response
Smaller footings can be shown OK thus
Notes: A section of a shallow foundation is show of with L, with applied axial load P and overturning moment M. Weight of the footing is shown as a downward force vector W. Resistance is shown by a resultant upward force vector R at an eccentricity e which is shown as a uniform plastic distribution of soil pressure.
Slide shows basis of plastic design of foundation.

## Slide 30: Counteracting Case
Instructional Material Complementing FEMA 1051, Design Examples
Given P = 332 k; M = 5712 k-ft
e = M / P = 17.2 ft
Try L = 40 ft, B = 9 ft
Try elastic solution:
  L’ = 3(40/2 – 17.2) = 8.4 ft
  qmax = 2 P / [3 B(L/2-e)] = 8.82 ksf
Bearing Capacity:
  Qns = 4,000 min (9,8.4/2) = 16,800 psf
  ϕQns = 0.45 (16.8 ksf) = 7.56 ksf < qmax NG
Notes: Note how much larger the footing must be for the counteracting case. Also, it would have been even larger if the elastic solution were used in lieu of the plastic solution.

## Slide 31: Counteracting Case
Instructional Material Complementing FEMA 1051, Design Examples
Try plastic solution:
L’ = 4.54 ft
Qns = 4,000 min (9,4.54)
Qns = 18,120 psf
ϕQns = 0.45(18.12) = 8.15 ksf
Check equilibrium:
(8.15 ksf)(4.54’)(9’) = 332 kips = P, satisfied
OK by plastic analysis
Notes: The illustration shows a section through a spread footing supporting two columns. An applied load of P (axial) and M (moment) are indicated, using a load combination to maximum uplift. The resulting bearing pressure under the footing is shown as an elastic distribution and also as a plastic distribution. The elastic distribution varies from 0 ksf to qmax of 8.82 ksf, over a length of L’=8.4 feet. The plastic distribution is a uniform distribution of 8.15 ksf over a distance L’=4.45 feet.
Note how much larger the footing must be for the counteracting case. Also, it would have been even larger if the elastic solution were used in lieu of the plastic solution.

## Slide 32: Settlement Analysis
Instructional Material Complementing FEMA 1051, Design Examples
Long term settlement verification
Load combination: D+0.5L per Appendix C Commentary (ASCE 7)
P = 340 kips
Qsustained = 340,000 / (9’ x 40’) = 945 psf
Qallowable = 2,000 psf
OK for settlement
Notes: Notes for additional checks for foundation design.

## Slide 33: Additional Checks
Instructional Material Complementing FEMA 1051, Design Examples
Moments and shears for reinforcement should be checked for the overturning case
Plastic soil stress gives upper bound on moments and shears in concrete
Horizontal equilibrium: Hmax< fm(P+W)
in this case friction exceeds demand; passive could also be used
Notes: Notes for additional checks for foundation design.

## Slide 34: Results for all Seismic Resistant System Footings
Instructional Material Complementing FEMA 1051, Design Examples
Corner: 9'x40'x5'-0" w/
top of footing 2'-0" below grade
Middle:
5'x30'x4'-0"
Side:
8'x32'x4'-0"
Notes: The illustration shows a foundation plan for the moment resisting frame shown in Figure 7.1-4. The foundation plan shows footings that are combined to support two columns per rectangular footing around the perimeter, with varying sizes depending on location and demands. Corner footings are noted as 9’x40’x5’ with top of footing 2’ below grade. Middle edge footings are noted as 5’x30’x4’. Side edge footings are noted as 8’x32’x4’. Interior column footings are shown as single concentrically loaded footings.
Given the combined footing strategy, footing sizes are more strongly influenced by the uplift on columns at the ends of frames than by the moments transmitted by the columns. Note that a complete perimeter grade beam would be a very feasible solution for this project, especially in cold climates where a continuous perimeter wall for frost control is necessary. A 4 ft by 4 ft continuous grade beam would be sufficient.

## Slide 35: Design of footings for core-braced 7 story building
Instructional Material Complementing FEMA 1051, Design Examples
25 foot square bays at center of building
Notes: The figure on the left shows an analysis model of a 7 story braced core structure. Two identical braced cores are shown which are 25 feet square. The undeformed and deformed shape under application of lateral load is shown. The figure on the right shows a framing plan for a braced frame system for the building shown in Figure 7.1-1. Two square brace frame cores are shown (Grid C-D, 3-4, and Grid E-F,3-4), with each core consisting of four bays of bracing (all sides of a square bay). The braced cores are separated by one bay with no frames to connect the braced cores. Wide flange columns are oriented with strong axis in east-west direction.
The screen capture is from the RAM Frame analysis of the structure, and the small plan is based on the same grids used for the 7 story moment frame. The braced frames appear to be 8 stories high, because there is a small penthouse over the core.

## Slide 36: Solution for Central Mat
Instructional Material Complementing FEMA 1051, Design Examples
Very high uplifts at individual columns; mat is only practical shallow foundation
Notes: The illustration shows a foundation plan view for the braced frame system identified in Figure 7.1-8. A single combined mat footing captures both bays of bracing, encompassing grids C through D and 3 through 4. All other footings are shown as single concentrically loaded footings.
The fundamental method is the same as used in the previous example: Determine the total applied vertical and horizontal loads and the moments. The complicating factor here is that the bending is significant about two axes simultaneously. Elastic solutions can be found from software that has the capacity for compression-only springs; SAP2000 was used in this case. Plastic solutions typically need to be done “by hand,” although spreadsheets are a great asset for the successive trial nature of the solution.

## Slide 37: Bearing Pressure Solution
Instructional Material Complementing FEMA 1051, Design Examples
Plastic solution is satisfactory; elastic is not
Notes: The illustration shows two diagrams of bearing pressures resulting from applied loads under a mat foundation. The first diagram (a) shows a plastic bearing pressure distribution with a uniform pressure of 12.2 ksf under the loaded edge (north edge). The second diagram (b) shows an elastic solution to the same configuration as the first diagram, which shows a varying pressure distribution with at peak of approximately 16 ksf under the loaded edge.
Slide shows the results from “hand” analysis for plastic distribution and for SAP2000 elastic solution. See Chapter 7 of FEMA P-1051 for more detail on the solution, as well as the design of the footing cross section for moment and shear.

## Slide 38: Central Mat Bearing
Instructional Material Complementing FEMA 1051, Design Examples
Design bearing capacity:
ϕQns = 0.45 (27.12 ksf) = 12.21 ksf OK
Notes: The diagram shows a plastic bearing pressure distribution with a uniform pressure of 12.2 ksf under the loaded edge (north edge).
Slide shows the results from “hand” analysis for plastic distribution and for SAP2000 elastic solution. See Chapter 7 of FEMA P-1051 for more detail on the solution, as well as the design of the footing cross section for moment and shear.

## Slide 39: Central Mat Bearing
Instructional Material Complementing FEMA 1051, Design Examples
Verify equilibrium:
(12.21)(6.78)(95) = 7864 kips ≈ Axial Load (1749 kips)
(7849)(5.42) = 42,542 ft-kips ≈ Off-axis moment (42,544 ft-kips)
Notes: The diagram shows a plastic bearing pressure distribution with a uniform pressure of 12.2 ksf under the loaded edge (north edge).
Slide shows the results from “hand” analysis for plastic distribution and for SAP2000 elastic solution. See Chapter 7 of FEMA P-1051 for more detail on the solution, as well as the design of the footing cross section for moment and shear.

## Slide 40: Central Mat Bearing
Instructional Material Complementing FEMA 1051, Design Examples
Verify equilibrium:
(12.21 ksf)(6.78 ft)(95 ft) = 7864 kips ≈ Axial Load (1749 kips)
(7849 kips)(5.42 ft) = 42,542 ft-kips ≈ Off-axis moment (42,544 ft-kips)
Notes: The diagram shows a plastic bearing pressure distribution with a uniform pressure of 12.2 ksf under the loaded edge (north edge).
Slide shows the results from “hand” analysis for plastic distribution and for SAP2000 elastic solution. See Chapter 7 of FEMA P-1051 for more detail on the solution, as well as the design of the footing cross section for moment and shear.

## Slide 41: Central Mat Flexural Reinforcement
Instructional Material Complementing FEMA 1051, Design Examples
Use moment contours to define areas of flexural reinforcement density
Notes: The illustration shows four figures of the mat foundation described in Figure 7.1-10 with contour plots showing in plane flexural demands. The moment countor diagrams are shown for the region between grid C-D and 3-4. The figures show enveloped demands for Mx positive, Mx negative, My position, and My negative. Mx positive shows a peak of 881 ft-kip/ft, Mx negative shows a peak of 669 ft-kip/ft, My positive shows a peak of 884 ft-kip/ft, My negative shows a peak of 484 ft-kip/ft. Designations of A through D are indicated where reinforcement is selected in accordance with the capacities calculated in Table 7.1-4.
Slide shows the results from “hand” analysis for plastic distribution and for SAP2000 elastic solution. See Chapter 7 of FEMA P-1051 for more detail on the solution, as well as the design of the footing cross section for moment and shear.

## Slide 42: Central Mat Shear Design
Instructional Material Complementing FEMA 1051, Design Examples
Critical section at d/2 (two-way) and d (one-way)
Be aware of size-effect in thick foundation elements
Notes: The illustration shows two figures indicating contour plots of shear stresses in orthogonal directions of Vx and Vy respectively. The critical section for two-way shear is dashed at each column location. The contour plots show shaded areas where stresses exceed 2. In general, the shaded areas are smaller than the critical perimeter section.
Slide shows the results from “hand” analysis for plastic distribution and for SAP2000 elastic solution. See Chapter 7 of FEMA P-1051 for more detail on the solution, as well as the design of the footing cross section for moment and shear.
Slide shows the results from “hand” analysis for plastic distribution and for SAP2000 elastic solution. See Chapter 7 of FEMA P-1051 for more detail on the solution, as well as the design of the footing cross section for moment and shear.
[Figure Description]: The illustration shows two figures indicating contour plots of shear stresses in orthogonal directions of Vx and Vy respectively. The critical section for two-way shear is dashed at each column location. The contour plots show shaded areas where stresses exceed 2√(〖𝑓′〗_𝑐 ). In general, the shaded areas are smaller than the critical perimeter section.

## Slide 43: Pile/Pier Foundations
Instructional Material Complementing FEMA 1051, Design Examples
View of cap with column above and piles below
Notes: The figure on the left shows a schematic model of a pile cap with piles. The pile cap is shown with a horizontal spring representing the passive soil resistance. The piles are shown with horizontal springs along the length to indicate p-y springs representing the soil resistance. The figure on the right shows isometric view of a rectangular pile cap with a square configuration of two by two for a total of four piles. The piles are circular in cross section. The cross section of a square column is shown on top of the pile cap.
Title slide for pier foundations.

## Slide 44: Pile/Pier Foundations
Instructional Material Complementing FEMA 1051, Design Examples
Soil Stiffness
  Linear springs – nomographs e.g. NAVFAC DM7.2
  Nonlinear springs – LPILE or similar analysis
Pile Stiffness:
  Short (Rigid)
  Intermediate
  Long
Cap Influence
Group Action
Notes: Most pile analysis for lateral loads is performed assuming linear response in the pile itself, although it is now common to consider nonlinear soil response. Some “by-hand” plastic techniques do make use of the classic pile stiffness idealizations.

## Slide 45: Sample p-y Curves
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The diagram shows representative p-y curves of soil resistance p (lbs/in) on the vertical logarithmic axis and pile deflection y (in) on the horizontal axis. Four curves are shown for Site Class C and Site Class E soils, with iterations on 10 feet and 30 feet depths below grade for each site class.
Note the logarithmic scale on the vertical axis.

## Slide 46: Passive Pressure
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The diagram shows passive pressure mobilization with load ratio of applied load over ultimate passive resistance on the vertical axis (P/Pult), and pile head displacement divided by pile cap height (δ/H) on the horizontal axis. The curve is nonlinear but shows 100% passive pressure mobilization at 0.06δ/H imposed displacement.
This passive pressure mobilization is useful for inclusion of the pile cap. It is from ASCE 41. Delta/H is the imposed displacement as a fraction of the minimum dimension of the face being pushed into the soil mass.

## Slide 47: Group Effect
Instructional Material Complementing FEMA 1051, Design Examples
Group Effect Factor
Notes: The diagram shows the group effect factor versus pile group size. The vertical axis shows the average group reduction factor (p-y multiplier), and the horizontal axis shows the pile group size from 2 to 8 pile rows. The diagram shows curves plotted for pile center to center spacing varying from 2 diameters to 7 diameters. The curve for piles spaced at 7D shows a maximum group effect reduction factor of approximately 0.95, whereas the curve for piles spaced at 2D show a group effect reduction factor that varies from 0.5 (2 piles in row) to 0.3 (8 piles in a row).
Plots of group effect factors computed based on Rollins et al., “Pile Spacing Effects on Lateral Pile Group Behavior: Analysis,” Journal of Geotechnical and Geoenvironmental Engineering, October 2006. The plot shows four curves, each for a different spacing (in terms of pile diameter). The horizontal axis is the number of rows of piles, and the vertical axis is the Group Effect Factor.

## Slide 48: Pile Shear: Two Soil Stiffnesses
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The diagram shows shear diagrams along the length of a single laterally loaded pile. The vertical axis shows depth below grade starting at 0 feet and ending at 30 feet below grade. The horizontal axis shows shear ranging from 15 kips to a shear maximum reversal of -5 kips. The diagram shows curves for both Site Class C and Site Class E response. The Site Class C response shows a shear reversal at closer to top of the pile due to the stiffer soil response when compared to the Site Class E response.
Note that the shear forces in the pile (as well as deformations and bending moments) carries to greater depths in soft soils than in firm soils. Pile (or pier) foundations are often used in stiff soils to control settlement of heavy structures or heave of expansive soils.

## Slide 49: Pile Moment vs Depth
Instructional Material Complementing FEMA 1051, Design Examples
Notes: The diagram shows moment diagrams along the length of a single laterally loaded pile. The vertical axis shows depth below grade starting at 0 feet and ending at 30 feet below grade. The horizontal axis shows moment ranging from -1000 in-kips to 500 in-kips. The diagram shows curves for both Site Class C and Site Class E response. The Site Class C response shows a moment reversal closer to the top of the pile due to the stiffer soil response when compared to Site Class E response.
See Chapter 7 of FEMA P-1051.

## Slide 50: Pile Reinforcement
Instructional Material Complementing FEMA 1051, Design Examples
Site Class C
Larger amounts where moments and shears are high
Minimum amounts must extend beyond theoretical cutoff points
“Half” spiral for 3D
Notes: The figure shows an elevation view of a pile embedded into a pile cap. The pile is detailed with three sections, with varying density of spiral pitch and vertical reinforcement to meet loading and minimum prescriptive detailing requirements. The lower portion of pile, Section C, is 21’ long and is detailed with (4) #5 longitudinal bars and #4 spiral reinforcement at 9 inch pitch. The middle portion of the pile, Section B, is 23’ long and is detailed with (6) #5 longitudinal bars and #4 spiral reinforcement at 9 inch pitch. The top portion of the pile, Section A, is 6’ long and is detailed with (6) #5 longitudinal bars and #4 spiral reinforcement at 4.5 inch pitch. The pile is embedded 4” into the pile cap, with longitudinal and transverse reinforcement extended into the cap for development.
Diagram and notes indicate requirements for pile reinforcement. “D” is pile diameter.

## Slide 51: Pile Design
Instructional Material Complementing FEMA 1051, Design Examples
Site Class E
Substantially more reinforcement
“Full” spiral for 7D
Confinement at boundary of soft and firm soils (7D up and 3D down)
Notes: The drawing shows one of the piles with detail of reinforcement. “D” is pile diameter.
See Chapter 7 of FEMA P-1051.

## Slide 52: Other Topics for Pile Foundations
Instructional Material Complementing FEMA 1051, Design Examples
Foundation Ties: F = PG(SDS/10)
Pile Caps: high shears, rules of thumb; look for 3D strut and tie methods in future
Liquefaction: another topic
Kinematic interaction of soil layers
Notes: Additional considerations for Pile Foundations. The equation is from ASCE 7-10 Section 12.13.5.2, where F is the design tension/compression force in the foundation tie beam and PG is the load in the pile.

## Slide 53: Tie between pile caps
Instructional Material Complementing FEMA 1051, Design Examples
Designed for axial force (+/-)
Pile cap axial load times SDS/10
Oftentimes use grade beams or thickened slabs on grade
(3) #6 top bars
(3) #6 bottom bars
#4 ties at 7" o.c.
2" clear
at sides
3" clear at
top and bottom
Notes: The figure shows a section through a grade beam designed as a foundation tie. Top and bottom longitudinal reinforcement is shown to meet the tie demands, and minimum closed stirrups are detailed. 3” clear is indicated at top and bottom, and 2” clear at sides. Top bars are (3) #6, bottom bars are (3) #6. Ties are indicated as #4 at 7” on center.
Required in higher seismic design categories for softer soils. It is designed for “pure” axial force. Fundamental objective is to prevent relative lateral displacement between column bases. It “fixes” the column bases for translation, but it is not intended to restrain rotation at the column bases.

## Slide 54: Example: Differential Settlement
Predicted differential settlement exceeds limit in Table 12.13-3
Structure must be shown to perform acceptably when subject to imposed settlement
Notes: The figure shows a two-dimensional sketch of a single-story, two-bay frame, with three columns and spread footings at each column. The bay length is indicated as “L.” The leftmost footing has settled by an amount indicated as delta-v, bringing the supported column down with it. This movement has created distortions in the remainder of the frame.
For multi-story Risk Category II steel-frame structures, the differential settlement limit is 0.010L. The structure must resist collapse, but need not remain elastic under this displacement.

## Slide 55: Structural Requirements
Analysis is required to use shallow foundations
No loss of gravity support permitted
Residual member strength at least 2/3 of undamaged nominal strength
  If demands exceed nominal strength consideration of nonlinear behavior is required
Notes: This structure at this site could be supported on deep foundations – the analysis in this example would not be required. If we can show through analysis, or modify the design in order to do so, we can use shallow foundations. The idea behind the 2/3 strength requirement is simply that no significant degradation of strength should occur.

## Slide 56: Floor Framing Plan
Steel SMF frame building
Two conditions studied
  Interior
  Perimeter
Expected Settlement, dv=8”
Notes: The figure shows floor framing diagram for a multi-story steel-frame building. The plan shape is essentially rectangular, with the bays at each of the four corners removed to create notches in the rectangular shape. There are 5 bays from left to right, with gridlines A through F, and 4 bays from bottom to top, with gridlines 1 through 5. There are wide-flange columns at each grid intersection. Girders run parallel to the lettered gridlines, and beams run parallel to the numbered gridlines, with three beam spaces per bay. There are special moment frames in the perimeter bays inboard of the corner notches. Two conditions are indicated for evaluation: Condition 1 at the end of a SMF girder at a corner notch, and condition 2 at a typical interior column.
This is a multi-story steel-frame building (the number of stories is not relevant, as long as it’s more than one. The floors are concrete on metal deck supported by steel beams. The beams are not considered composite in this example. We consider two locations: One exterior and one interior. Condition 1 (F/2) is at the end of a Special Moment Frame. Condition 2 (C/2) is a gravity-only column. Beams are W16s, girders are W24s. The 8” settlement indicated in the relative settlement, specified as occurring over a distance of a 25-foot bay length.

## Slide 57: Rotation Demand
25 ft.
Exceeds 0.01 rad limit in Table 12.13-3
Settlement dv=8”
Bay width 25 ft.
Notes: The figure is a repeat of that shown in the previous slide, with the beam length of a typical bay dimensioned as 25 feet.
The rotation demand is simply the relative settlement divided by the bay length, which is this case exceeds the permissible value in Table 12.13-3 by nearly a factor of 3. This is a large amount of relative settlement.

## Slide 58: Condition 1
W16x36
SMF members and connection can sustain 0.04 rad.
Must assess:
  Simple shear tab connection to web
  Gravity beam
  Column weak axis
Notes: The figure shows a magnified view of the framing at condition 1, with the SMF girder indicated as W33x141, framing into the flange of the column and the perpendicular beam as a W16x36, framing into the column web.
Because of the large seismic ductility capability of the SMF system, we don’t need to check the frame members and connections explicitly. We need to assess the gravity framing, the standard designs are not designed for this kind of rotation.

## Slide 59: Check of W16x36 Beam
D
MD
VD
MD
VD
Consider the beam fixed-ended with an imposed displacement
Notes: The figure shows a diagram of a fixed-fixed beam with its ends subject to a relative vertical displacement of “delta.” Standard formulas for the shear and moment are presented and evaluated based on the beam properties and dimensions.
Even though the gravity framing was designed originally as pinned-ended, we know that the ends are not “true” pins. If the beams were “true” pins, there would be no moments or shears produced by the differential settlement. But we know that some moment will develop at these connections when the settlement occurs. When we presume fixed-fixed behavior, we can assess the maximum possible moments that can occur, then determine which condition is actually the weak link – where the yielding will actually occur – by a comparison of the relative strengths.

## Slide 60: Add gravity loading
Compute the gravity shear and moment
  85 psf dead load, 50 psf live load
  4.17 feet tributary width
Notes: We consider the load combination including dead load, partial live load and seismic effects. The moments are again in consideration of fixed-end behavior. We add the two moments and the two shears to compute the Mu and Vu values for our check.

## Slide 61: Compare to design values
Shear capacity fVn = 141 kip
  Beam is adequate for shear
Flexural capacity fMn = 174 kip-ft
  Demand exceeds flexural capacity
  Either the beam will yield in flexure or the connection will yield
Notes: The beam shear capacity from AISC Table 3-6. The beam flexural capacity for negative moment, Lb = 12.5 feet, braced at mid-span, from Table 3-10. We’ll check the connection next and compare the strengths.

## Slide 62: Check Connection
Shear capacity fVn = 78.3 kip
Flexural capacity fMn = 21 kip-ft
Connection will yield in flexure
Notes: The figure shows a connection detail for a W16 beam framing into the web of a wideflange column. The detail is a single-plate shear connection, with four bolts (3 spaces) from the shear tab to the beam web and stiffener plates top and bottom to engage the shear tab to the column flanges. The bolts are indicated as ¾-inch diameter A325x. Welds are not indicated.
Connection shear capacity from AISC Table 10-10a. For the connection’s flexural capacity based on the bolt group, we look up in Table 7-6 and Table 7-1. The flexural demand of 622kip-ft far exceeds the connection’s flexural capacity, so we know this is the weak link. Not surprising, since it was designed as a pinned condition.

## Slide 63: Check Connection
Check plate thickness to ensure ductile behavior (plate yielding)
Check permissible rotation per ASCE 41
Notes: The figure from the previous slide is repeated.
Although the bolt group has limited flexural strength, we want to make sure that the bolt shear is not actually the lowest capacity limit state, as this would be less ductile than plate yielding.

## Slide 64: Check Connection
Maximum plate thickness is acceptable
  But not if it were 50 ksi steel
Notes: The figure from the previous slide is repeated.
We employ the single-plate connection design check in Chapter 10 of the AISC Manual. In this check, the thickness of the shear tab is limited to promote flexural yielding in the shear tab and minimize the likelihood of bolt fracture. Here, d is the depth of the shear tab. We have a grade 36 plate. In this instance, increasing the strength to 50 ksi would not be desirable. The use of higher strength (A490) bolts would allow the use of a 50-grade plate. Note also that this design check does not indicate an acceptable chord rotation for the connection; it only ensures the connection will yield in a ductile manner.

## Slide 65: Check Connection
Check plastic rotation to provide collapse resistance per ASCE 41
  Acceptable
Notes: The figure from the previous slide is repeated.
To check the acceptability of the rotation, we will employ Table 9-6 of ASCE 41-13 to obtain an acceptable plastic rotation capacity for simple shear connections, incorporating a value of dbg = 9 inches
for four bolts with 3-inch spacing. We consider the acceptable plastic rotation as the value stated in ASCE 41-13 for Collapse Prevention. The rotation demand was 0.027 rad. Note that we have conservatively taken the plastic rotation as the total rotation. We could use a sharper pencil if necessary by subtracting the yield rotation from the total rotation demand, but this is not necessary here.

## Slide 66: Bi-Axial bending of column F/2
Considered acceptable, because:
  SMF column is known to be able to resist any moment the beam can impart
  Yield moment of weak axis connection is so small as to be considered negligible
Notes: We note that the differential settlement will also cause weak-axis bending in the SMF column, but this is small relative to the column strength, so we consider it acceptable by inspection.

## Slide 67: Condition 2
W16x36
Must assess:
  Gravity girder
Notes: The figure shows a magnified view of the framing at condition 2, with the girder indicated as W24x62, framing into the flange of the column and the perpendicular beam as a W16x36, framing into the column web.
Moving on to Condition 2, with beams and girders framing in to an interior column. We note that the beam condition was addressed in Condition 1. We’ll check the girder and its connection. The calculations are similar to those employed for the beam.

## Slide 68: Check of W24x62 Girder
D
MD
VD
MD
VD
Consider the beam fixed-ended with an imposed displacement
Notes: The figure shows a diagram of a fixed-fixed beam with its ends subject to a relative vertical displacement of “delta.” Standard formulas for the shear and moment are presented and evaluated based on the beam properties and dimensions.
The shear and moment calculations are similar to those for the beam – considering fixed-end behavior, but with the larger value of the moment if inertia applicable to the girder.

## Slide 69: Add gravity loading
Compute the gravity shear and moment
  85 psf dead load, 50 psf live load
  Two equal point loads of 208 sq. ft. each
Notes: The gravity moment is computed based on the two symmetrically located 1/3-point loads form the beams. We use the same load combination as before.

## Slide 70: Compare to design values
Shear capacity fVn = 306 kip
  Girder is adequate for shear
Flexural capacity fMn = 482 kip-ft
  Demand exceeds flexural capacity
  Either the girder will yield in flexure or the connection will yield
Notes: The beam shear capacity from AISC Table 3-6. The beam flexural capacity for negative moment, Lb = 8.33 feet (1/3 of the bay), from Table 3-10. We’ll check the connection next and compare the strengths.

## Slide 71: Check Connection
Shear capacity fVn = 133 kip
  Short slotted holes req’d
Flexural capacity fMn = 63 kip-ft
Connection will yield in flexure
Notes: The figure shows a connection detail for W24 girders framing into both flanges of a wideflange column. There is a W16 beam framing into the web. The details are single-plate shear connections, with seven bolts (6 spaces) from each shear tab to the beam web. The bolts are indicated as ¾-inch diameter A325x. The shear tab is indicated as A36 material. Welds are not indicated.
We obtain the connection shear capacity from AISC Table 10-10a and the flexural capacity from Table 7-6 and Table 7-1. The flexural demand of 2,215 kip-ft far exceeds the connection’s flexural capacity based on the bolts. Again, we know this element is the weak link. We note the additional consideration that short-slotted holes are required. This may point to the desirability of using a different connection type, such as a bolted double-angle, which would have added rotational capacity without the need for short slots. However, the single plate will work in this condition, so we continue.

## Slide 72: Check Connection
Check plate thickness to ensure ductile behavior (plate yielding)
Check permissible rotation per ASCE 41
Notes: The figure from the previous slide is repeated.
We still need to ensure that the connection will behave in a ductile manner and to ensure the rotation is within the applicable limits.

## Slide 73: Check Connection
Maximum plate thickness is acceptable
  But not if it were 50 ksi steel
Notes: The figure from the previous slide is repeated.
Again, the 3/8” grade 36 plate meets the thickness requirement. The use of higher strength (A490) bolts would allow the use of a 50-grade plate.

## Slide 74: Check Connection
Check plastic rotation to provide collapse resistance per ASCE 41
  Acceptable
Notes: The figure from the previous slide is repeated.
To check the acceptability of the rotation, we will employ Table 9-6 of ASCE 41-13 to obtain an acceptable plastic rotation capacity for simple shear connections, incorporating a value of dbg = 18 inches
for seven bolts with 3-inch spacing. We consider the acceptable plastic rotation as the value stated in ASCE 41-13 for Collapse Prevention. The rotation demand was 0.027 rad. Again, we have conservatively taken the plastic rotation as the total rotation.

## Slide 75: Conclusions
The building can sustain the differential settlements imposed by the liquefaction
Acceptable to use shallow foundations
  This assessment was primarily concerned with connection ductility
  Other systems may have different concerns
    Concrete systems must be checked for shear and remain essentially elastic
    Non SMF steel moment connections may not have sufficient ductility
    Must consider load reversals causing the need for added bracing
Notes: There is no need to check the column for bending in this case because of the symmetrical layout and loading. Note that nonlinear behavior of the connection plates is permitted by the provisions, but may not be acceptable to the owner or the user of the building. Selection of foundation type should consider the owner’s expectations of post-earthquake serviceability, which may point to the use of deep foundations.

## Slide 76: Foundations on Liquefiable Soil
Effects of Liquefaction on Structures
  Differential settlement leading to damage in the superstructure
  Lateral spreading leading to damage to foundations and superstructure
Notes: Liquefaction is a geological effect of earthquakes that is not mitigated solely by the design of the superstructure. Liquefaction can cause structure settlement and also lateral spreading. Both can be damaging to structures, so the provisions require explicit analysis to consider these effects, but include limits on the amount of differential settlement and the amount of lateral spread to be permitted without analysis.

## Slide 77: Performance Goals of Provisions
Structures are intended to resist collapse due the liquefaction effects
  MCEG ground motions.
Distinct from remainder of Provisions
  2/3 of MCER ground motions
Notes: Liquefaction is assessed directly under MCEG earthquake motions. This differs from the seismic design approach in most of the Provisions, wherein designs are accomplished at MCER earthquake motions that have been reduced for design by a factor of 2/3. The intent of the design is the same – to provide protection against collapse in the MCE – but the specifics of the approach are different.

## Slide 78: Nonlinear Behavior
Settlement or lateral spreading due to liquefaction may cause nonlinear behavior
This behavior must be addressed where applicable
Complete nonlinear analysis not required, provided that nonlinear behavior is assessed appropriately.
Notes: Because the design for liquefaction addresses higher levels of shaking directly, and its specific performance goal allows for more damage to occur, it becomes necessary to consider nonlinear effects. Such considerations are not common in designs based on these Provisions. Accordingly, these examples make use of the information in ASCE 41-13 and other resources in order to assess the acceptability of element demands and capacities. The Provisions do not require the use of any specific nonlinear procedures or criteria.

## Slide 79: Liquefaction
Occurs in loose, saturated sands and silts with poor drainage
  Differential settlement
Notes: The figure shows severe differential settlement that occurred to mid-rise concrete shear-wall structures in the 1964 Niigata earthquake in Japan. Although the buildings were not severely damaged due to the ground shaking, several of them tilted over at extreme angles from the vertical.
Cyclic loading has a ratcheting-up effect on pore pressure as soil densifies. When pore pressure exceeds effective stress, grains separate - soil loses shear strength.
The loss of shear strength in the soil allows upper soils and foundations to settle. Sand boils can also form at the surface, but these are only a symptom of liquefaction, not a direct cause of settlement.

## Slide 80: Lateral Spreading
Can occur when liquefaction occurs adjacent to a scarp, channel or riverbank.
Picture by NISEE-PEER, Univ. of California, Berkeley. Used by permission.
Notes: The Figure shows damage to a port facility due to lateral spreading. The soil moved towards the water’s edge, severely damaging the wharf structure.
Liquefied soil can spread laterally when adjacent to an unconfined edge. Structures can’t resist this movement, they simply must sustain it or move with it.

## Slide 81: Example: Lateral Spreading
Structure is on deep foundations
Lateral displacements exceed Table 12.13-2 limits
Notes: The figure shows a section of a column resting on a four-pile cap (only two piles are visible in the section). The cap is 5 feet deep below the slab. A layer of liquefiable soil continues for 30 feet below the cap, below which is competent soil. The piles extend an unspecified distance into the competent soil. The axial load on the column is indicated as 1,000 kips.
We will investigate a foundation for a building on deep foundations, where the site is subject to lateral spreading. The deep foundations will protect the building from damage due to ground settlement, but they can’t protect it from lateral displacement. The provisions allow Risk Category II buildings to be constructed on sites that are subject to lateral spreading with up to 18 inches of displacement without further analysis. Where the displacements in Table 12.13-2 are exceeded, it’s necessary to demonstrate acceptable behavior through analysis.

## Slide 82: Structural Requirements
Analysis is required to demonstrate acceptable pile behavior
Nonlinear behavior is permitted
  No loss of gravity support permitted
  Residual member strength at least 2/3 of undamaged nominal strength
  Prescriptive detailing for ductility
  Nominal shear capacity must not be exceeded
Notes: The analysis must show that the foundation will maintain the building in a condition that will resist collapse. The piles are allowed to behave nonlinearly and may be damaged, but must sustain gravity support.

## Slide 83: Pile Foundation
24 in.
30 ft.
Lateral displacement 24 in
  Exceeds 18 in limit
Occurs over depth of 30 ft.
Factored loads per pile 250k
Notes: The figure shows a kinematic diagram of a pile subject to lateral spreading of a 30-foot deep liquefiable layer. The pile is idealized to behave rigidly between rotations at plastic hinge points at the pile head and the top of the competent soil below. The lateral deformation at the pile head is indicated as 24 inches. The applied axial load at the pile head, Pu, is resisted in the competent soil below. The total rotation at each plastic hinge is indicated as Theta-t, which is the sum oy Theta-y (yield rotation) and Theta-p (plastic rotation)
Here we see an idealized diagram of the pile behavior. The total load on the foundation is 1,000 kips and there are four piles: 250 kips each. As the lateral spreading occurs, the spreading layer will deform in shear. The piles will deform beyond their elastic moment capacity and will develop plastic hinges at the cap and at the competent soil boundary. The lower hinge may occur at a deeper depth; consideration of its location at the boundary is conservative.

## Slide 84: Pile Diameter
Improved flexural ductility at low axial loads
Choose diameter, such that
Choose 30 in. diameter
Notes: We know that there is a significant flexural ductility demand on the piles. We turn to ASCE 41 for guidance in improving the ductility capacity. Table 10-12 of this document indicates that the most advantageous conditions occur at low axial loads, specifically, less than 10% of the gross capacity based on the area and concrete strength alone. We choose a diameter rounded up to the next 6-inch size larger than 25.2 inches.

## Slide 85: Flexural Demand
Consider fixed-fixed behavior between the bottom of the cap and the top of the competent soil.
  Half of P-Delta moment occurs at two locations
Notes: This assessment neglects any lateral resistance provided by the laterally spreading soil itself. It may be acceptable to incorporate this additional resistance, provided that the Geotechnical Investigation Report includes recommendations accordingly. The P-Delta moment must be resisted in order to maintain stability.

## Slide 86: Axial-Moment Interaction
Consider fairly light reinforcing and concrete strength of 5ksi
Notes: The figure shows an interaction diagram for a 30-inch diameter pile reinforced with (8) #8 longitudinal bars. The vertical axis is axial load in kips, ranging from -1000 to 5000. The horizontal axis is moment in kip-inches, ranging from 0 to 14,000.
Here we see an interaction diagram for the preliminary pile design. This is the nominal strength diagram with no strength-reduction factors incorporated. The applied axial load is shown with a red dashed line. The required flexural strength to resist the P-Delta moment is indicated with a black dash-dot line at 3,000 kip-in. The pile’s flexural strength at the applied axial load (6,730 kip-in) is shown with a black dot.
The pile has sufficient axial and flexural strength to resist the P-delta moment at the applied axial load. Flexural demands will increase beyond this limit when the pile bends laterally and plastic hinges form.

## Slide 87: Rotation and Curvature
Rotation is computed from displacement and effective length
Curvature depends on presumed hinge length: ½ pile diameter
Notes: We calculate the curvature of the cross section as θt. The section curvature depends on the length of the plastic hinge. Various methods exist for estimation of the plastic hinge length, lp, depending on factors such as the effective length of the element, the section depth, and the size of the reinforcing bars. For the purpose of simplicity, we will use an estimate of half the section depth, in this case 15 inches. More detailed methods may result in longer lengths and thus smaller curvature.

## Slide 88: Moment-Curvature
Strength at imposed curvature remains above 67% limit
Imposed curvature is less than limit due to bar fracture
Notes: The figure shows a moment curvature diagram at the design axial load of 250 kips per pile. The horizontal axis is curvature in reciprocal inches, ranging form 0 to 0.006. The vertical axis is moment in kip-inches, ranging from 0 to 8,000. A single curve is shown, increasing to a nominal strength of 6,730 kip-inches at a curvature of approximately 0.0005, at which point the strength decreases slightly and then increases due to strain hardening. The 67% nominal strength value is shown as a dashed horizontal line at 4,500 kip inches.
We compare the computed curvature of 0.0044 with the moment curvature relationship for the proposed pile section, at the design axial load. The computed curvature is less than the ultimate curvature (due to bar fracture) at about 0.005. The moment strength at the design point exceeds the nominal strength due to strain-hardening. The requirement that the strength has not degraded to less than 67 percent of the nominal value is satisfied.

## Slide 89: Moment-Curvature
Consider whether smaller pile diameters would be acceptable
Smaller diameters result in earlier bar fracture
  Not acceptable
  Use 30” initial design
Notes: The figure shows a moment curvature diagrams at the design axial load of 250 kips per pile, as well as at higher loads: 500, 1,000, and 2,000 kips. The horizontal axis is curvature in reciprocal inches, ranging form 0 to 0.006. The vertical axis is moment in kip-inches, ranging from 0 to 14,000. The lower curve is the same one shown in the previous figure. The three upper curves are similar in shape, but increase in strength and decrease in curvature capacity as the axial load increases. The 2,000 kip axial load results in a srrength exceeding 12,000 kip-inches and a curvature capacity of about 0.0015.
It is instructive to see how moment-curvature relationships vary with different values of applied axial load. The higher values of axial load result in significantly smaller values of ultimate curvature, validating the need to keep the axial load-to-capacity ratio low.

## Slide 90: Detailing for Ductility
ACI 318-14, Sections 18.7.5.2 through .4
Spiral spacing
  ¼ member dimension (7.5 in.)
  Six time bar diameter (6 in.)
  6 in.
Volumetric ratio (larger of the following):
Notes: Note that Section 1810.3.2.1.2 of the 2015 International Building Code indicates that the second of these formulas need not be applied to piles. However, this formula does indeed apply to these requirements for piles subject to lateral spreading. The improved confinement provided by the heavier spiral reinforcing is critical to develop the degree of ductility necessary for proper performance.

## Slide 91: Detailing for Ductility
Choose #5 spirals and compute required spacing
Use pitch of 2½ inches
Required from the top of the pile to 7 pile diameters (17’-6”) below the interface of the liquefiable soil and the competent soil below.
Notes: Where the variables are as defined in ACI 318 and is the out-to-out diameter of the confined core. Considering 3 inches of clear cover, this is 6 inches less than the pile diameter: 24 inches. This is considerably heavier spiral reinforcing than would be provided in a typical design without lateral spreading.
Where the variables are as defined in ACI 318 and 𝑑_𝑐ℎ is the out-to-out diameter of the confined core. Considering 3 inches of clear cover, this is 6 inches less than the pile diameter: 24 inches

## Slide 92: Shear Strength
Compute shear demand at probable moment
  Taken conservatively as 1.25 times nominal moment
Compute shear strength ignoring concrete within plastic hinge
Shear capacity is sufficient.
Notes: The pile must have shear strength at least sufficient to develop the double plastic hinge, in order to ensure ductile behavior in the pile. This shear demand is based on the probable moment occurring at the top of the pile and at the competent soil interface.

## Slide 93: Pile Section Detail
Notes: The figure shows a sectional view of the final design of the pile section: 30-in diameter, eight #8 longitudinal bars, and #5 spirals at 2-1/2” pitch. The 135-degree hook at the spiral end is required for all cast-in-place concrete piles, regardless of liquefaction. The spirals are 3 inches clear from the pile surface.

## Slide 94: Questions
Instructional Material Complementing FEMA 1051, Design Examples
Notes: Slide to initiate questions from the participants.

## Slide 95: DISCLAIMER
NOTICE: Any opinions, findings, conclusions, or recommendations expressed in this publication do not necessarily reflect the views of the Federal Emergency Management Agency. Additionally, neither FEMA nor any of its employees make any warranty, expressed or implied, nor assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, product or process included in this publication.
The opinions expressed herein regarding the requirements of the NEHRP Recommended Seismic Provisions, the referenced standards, and the building codes are not to be used for design purposes. Rather the user should consult the jurisdiction’s building official who has the authority to render interpretation of the code.
Any modifications made to the file represent the presenters' opinion only.