## Instructions
Interim Design Submittal
UFC 4-010-06 CHAPTER 5 Section 5-4.3
At the Interim Design (50-65% design) submittal, or the equivalent submittal step for projects not incorporating an Interim Design submittal, provide the following items:
CCI List: The recommended format for this list is to use the format of the tables in APPENDIX G with the addition of a column to document the required information. In addition to any other required formats, provide the CCI list in a format compatible with Microsoft Excel. The list must include the following items.
  The final classification (Designer, etc.) of each CCI (Step 2C).
  For each CCI categorized as designer and addressed in the design, include:
    Identification where and why the standard CCI requirements cannot be incorporated into the design (identified in Step 3), description of what requirements will be incorporated instead, and an explanation of the changes.
    Documentation of how the CCI has been incorporated into the control system design (Step 3), including specification or drawing references. If there are specific changes from standard requirements, or multiple options available, document these changes or options.
  For each CCI categorized as designer due to requiring information be provided (Step 3), provide the relevant information for use by others.
Redlined Specifications and Drawings: Draft specifications based on UFGS 25 05 11 with appropriate tailoring for system type and impact rating and edited for project requirements, and any relevant drawings or other attachments when requirements have been incorporated into drawings or other attachments.
Riser Diagrams: One-line/riser diagram showing concept architecture and major components.
System Connections: A document either indicating no network connections to other systems will exist or describing the network connections to other systems. For system connections include a description of the other system, the nature and purpose of the connection, and all protocols used by the communication interface.
The "System Connections" sheet provides a table for the System Connections information. The first line in italics provides an example of a table entry. This SHOULD BE REMOVED before submission. Additional rows can be added to the table as need. Provided entries are for example only.
The "CCI List" sheet provides space for the CCI list described above and other pertinent information. Five example table entries are provided, covering all columns of the table, in italics. These SHOULD BE REMOVED before submission. Additional rows can be added to the table as need. Provided entries are for example only.
Redline Specifications and Drawings and Riser Diagrams should be attached seperately.
CCI Definition, Implementation Guidance, and Assessment Procedures by CCI can be found here:
***The Final Design (Unreviewed 100%) Submittal is the finalized version of the submitted Interim Design. All items outlined in this template should be finalized and submitted for the Final Design (Unreviewed 100%) Submittal.

## System Connections
System Connections Table
| System Description | Nature/Purpose of Connection | Protocols Used by the Communication Interface
| Example | Example | Example

## CCI List
CCI List
Control Number | CCI | CCI Definition | Implementation Guidance | Assessment Procedures | Enclave | Designer | Non -Designer | Impractical | DoD Defined | Not Applicable to FRCS | Justification for N/A to FRCS UFC Table H-2 | Removed from Low baseline | Rationale for removal from Low baseline UFC Table H-3 | UFGS 25 05 11 - Reference | Implementation Status
AC-1 | 000001 | The organization develops and documents an access control policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance. | The organization being inspected/assessed develops and documents an access control policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance. Recommended Compelling Evidence: 1.) Signed and dated copy of access control policy that defines the purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance. | The organization conducting the inspection/assessment obtains and examines the access control policy to ensure the organization being inspected/assessed develops and documents an access control policy that addresses purpose, scope, roles, responsibilities, management commitment, coordination among organizational entities, and compliance. |  |  | X | [6 empty] | ---
AC-8 | 001384 | The information system, for publicly accessible systems, displays system use information organization-defined conditions before granting further access. | The organization being inspected/assessed configures the information system to display the content of DTM 08-060, "Policy on Use of Department of Defense (DoD) Information Systems - Standard Consent Banner and User Agreement," March 2013 before granting further access for publicly accessible systems For information system components that have applicable STIGs or SRGs, the organization being inspected/assessed must comply with the STIG/SRG guidance that pertains to CCI 1384. DoD has defined the conditions as the content of DTM 08-060, "Policy on Use of Department of Defense (DoD) Information Systems - Standard Consent Banner and User Agreement," March 2013. Recommended Compelling Evidence: 1.) Applicable STIG/SRG checks | The organization conducting the inspection/assessment examines the information system to ensure the organization being inspected/assessed configures the information system to display the content of DTM 08-060, "Policy on Use of Department of Defense (DoD) Information Systems - Standard Consent Banner and User Agreement," March 2013 before granting further access for publicly accessible systems For information system components that have applicable STIGs or SRGs, the organization conducting the inspection/assessment evaluates the components to ensure that the organization being inspected/assessed has configured the information system in compliance with the applicable STIGs and SRGs pertaining to CCI 1384. DoD has defined the conditions as the content of DTM 08-060, "Policy on Use of Department of Defense (DoD) Information Systems - Standard Consent Banner and User Agreement," March 2013. | [5 empty] | X | CS is not publically accessible |  |  | --- | Not Applicable to FRCS; Control Systems are not publicly accessible (Source: UFC 4-010-06)
CP-2 | 000443 | The organization develops a contingency plan for the information system that identifies essential missions. | The organization being inspected/assessed must clearly and accurately document essential missions for its information system(s). Impact of loss of essential mission functions must be defined using CNSSI 1253. Recommended Compelling Evidence: 1.) Signed and dated contingency plan, referencing essential missions section | The organization conducting the inspection/assessment obtains and examines the contingency plan to ensure it clearly and accurately documents essential missions for its information system(s). |  |  | X |  |  |  |  | X | A LOW CS doesn't have any "essential" mission | --- | Applicable only to Control Systems with essential mission function (Source: UFC 4-010-06)
CP-7(1) | 000516 | The organization identifies an alternate processing site that is separated from the primary processing site to reduce susceptibility to the same threats. | The organization being inspected/assessed identifies and documents within the contingency plan an alternate processing site not susceptible to the same threats that exist at the primary processing site. The organization must document threats in the risk management strategy IAW PM-9, CCI 000227. Recommended Compelling Evidence: 1.) Risk management strategy 2.) Contingency plan that identifies an alternate processing site that is separated from the processing site | The organization conducting the inspection/assessment obtains and examines the risk management strategy and the contingency plan to ensure the organization identifies an alternate processing site that is separated from the primary processing site so as not to be susceptible to the same threats identified at the primary site. | X |  |  | X | [5 empty] | ---
CP-8 | 000522 | The organization defines the time period to permit the resumption of organization-defined information system operations for essential missions when the primary telecommunications capabilities are unavailable at either the primary or alternate processing or storage sites. | DoD has defined the time period as 1 hour (Availability High ) 12 hours (Availability Moderate) as defined in the contingency plan. Recommended Compelling Evidence: Automatically Compliant | The organization being inspected/assessed is automatically compliant with this CCI because they are covered at the DoD level. DoD has defined the time period as 1 hour (Availability High ) 12 hours (Availability Moderate) as defined in the contingency plan. | X |  |  |  | X |  |  |  |  | ---