**SCHEDULE OF SPECIAL INSPECTIONS**

Reference UFGS 01 45 35 for all requirements not noted as part of this schedule.

**INSPECTION DEFINITIONS:**

**PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and noted verification.

**OBSERVE:** Observe these items randomly during the course of each work day to insure that applicable requirements are being met. Operations need not be delayed pending these inspections at contractor’s risk.

**DOCUMENT**: Document, with a report, that the work has been performed in accordance with the contract documents. This is in addition to any other reports required in the Special Inspections guide specification.

**CONTINUOUS:** Constant monitoring of identified tasks by a special inspector over the duration of performance of said tasks.

The Seismic Design Category for this project is:  A,  B,  C,  D,  E,  F (check appropriate box)

**STRUCTURAL - STEEL – WELDING SECTION**

**DESIGNER NOTES (delete this box after reviewing):**

1. This schedule contains minimum requirements. Do not delete applicable inspection tasks unless notes in blue indicate it is acceptable to do so.
2. Blue text = designers notes. The designer must review and edit all blue text in this schedule prior to inserting this schedule into the special inspections spec (UFGS 01 45 35).
3. Check section boxes with ANY inspection tasks applicable to your project. You may choose to delete unchecked sections or leave them in the schedule unchecked.
4. Individual rows/tasks that that are not applicable to the project may be left in the section, as the inspector can determine whether they occur/apply (e.g. metal trusses in the light gauge framing section for example).
5. Design discipline sections are color coded for easier reference by designers. This schedule does NOT need to be printed in color.
6. When finished editing, delete this note box and save this schedule as a PDF and insert into the project specifications (special inspections section).

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| STEEL INSPECTION PRIOR TO WELDING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 360-16: Table C-N5.4-1 | | |
| TASK | INSPECTION TYPE[[1]](#footnote-1) | DESCRIPTION |
| 1. Verify that the welding procedures specification (WPS) is available | **PERFORM** |  |
| 1. Verify manufacturer certifications for welding consumables are available | **PERFORM** |  |
| 1. Verify material identification | **PERFORM** | Type and grade. |
| 1. Welder Identification System | **PERFORM** | The fabricator or erector, as applicable, shall maintain a system by which a welder who has welded a joint or member can be identified. Stamps, if used, shall be the low-stress type. |
| 1. Fit-up of groove welds (including joint geometry) | OBSERVE | * Joint preparation * Dimensions (alignment, root opening, root face, bevel) * Cleanliness (condition of steel surfaces) * Tacking (tack weld quality and location) * Backing type and fit (if applicable) |
| 1. Configuration and finish of access holes | OBSERVE |  |
| 1. Fit-up of fillet welds | OBSERVE | * Dimensions (alignment, gaps at root) * Cleanliness (condition of steel surfaces) * Tacking (tack weld quality and location) |
| STEEL INSPECTION DURING WELDING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 360-16: Table C-N5.4-2 | | |
| TASK | INSPECTION TYPE | DESCRIPTION |
| 1. Use of qualified welders | **PERFORM** | Welding by welders, welding operators, and tack welders who are qualified in conformance with requirements. |
| 1. Control and handling of welding consumables | OBSERVE | * Packaging * Electrode atmospheric exposure control |
| 1. No welding over cracked tack welds | OBSERVE |  |
| 1. Environmental conditions | OBSERVE | * Wind speed within limits * Precipitation and temperature |
| 1. Welding Procedures Specification followed | OBSERVE | * Settings on welding equipment * Travel speed * Selected welding materials * Shielding gas type/flow rate * Preheat applied * Interpass temperature maintained (min./max.) * Proper position (F, V, H, OH) * Intermix of filler metals avoided |
| 1. Welding techniques | OBSERVE | * Interpass and final cleaning * Each pass within profile limitations * Each pass meets quality requirements |

**STRUCTURAL - STEEL – WELDING SECTION (CONTINUED)**

|  |  |  |
| --- | --- | --- |
| STEEL INSPECTION AFTER WELDING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 360-16: Table C-N5.4-3 | | |
| TASK | INSPECTION TYPE [[2]](#footnote-2) | DESCRIPTION |
| 1. Welds cleaned | OBSERVE |  |
| 1. Size, length, and location of all welds | **PERFORM** | Size, length, and location of all welds conform to the requirements of the detail drawings. |
| 1. Welds meet visual acceptance criteria | **PERFORM AND**  **DOCUMENT** | * Crack prohibition * Weld/base-metal fusion * Crater cross section * Weld profiles * Weld size * Undercut * Porosity |
| 1. Arc strikes | **PERFORM** |  |
| 1. k-area | **PERFORM** | When welding of doubler plates, continuity plates or stiffeners has been performed in the k-area, visually inspect the web k-area for cracks. (AISC 360 – Table N5.4-3) |
| 1. Backing removed, weld tabs removed and finished, and fillet welds added where required | **PERFORM** |  |
| 1. Repair activities | **PERFORM AND DOCUMENT** |  |
| 1. Document acceptance or rejection of welded joint or member | **PERFORM** |  |

**END SECTION**

**STRUCTURAL - STEEL – BOLTING SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| STEEL INSPECTION TASKS PRIOR TO BOLTING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 360-16: Table C-N5.6-1 | | |
| TASK | INSPECTION TYPE [[3]](#footnote-3) | DESCRIPTION |
| 1. Manufacture’s certifications available for fastener materials | **PERFORM** |  |
| 1. Fasteners marked in accordance with ASTM requirements | OBSERVE |  |
| 1. Proper fasteners selected for joint detail (grade, type, bolt length if threads are to be excluded from shear plane) | OBSERVE |  |
| 1. Proper bolting procedure selected for joint detail | OBSERVE |  |
| 1. Connecting elements, including appropriate faying surface condition and hole preparation, if specified, meet applicable requirements | OBSERVE |  |
| 1. Proper storage provided for bolts, nuts, washers, and other fastener components | OBSERVE |  |
| STEEL INSPECTION TASKS DURING BOLTING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 360-16: Table C-N5.6-2 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Fastener assemblies of suitable condition, placed in all holes and washers (if required) are positioned as required | OBSERVE |  |
| 1. Joint brought to the snug-tight condition prior to pretensioning operation | OBSERVE |  |
| 1. Fastener component not turned by the wrench prevented from rotating | OBSERVE |  |
| 1. Bolts are pretensioned in accordance with RCSC Specification, progressing systematically from the most rigid point toward the free edges | OBSERVE |  |
| STEEL INSPECTION TASKS AFTER BOLTING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC 1705.2.1, AISC 360-10: Table C-N5.6-3 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Document acceptance or rejection of all bolted connections | **DOCUMENT** |  |

**END SECTION**

**STRUCTURAL - STEEL - NON DESTRUCTIVE TESTING SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| NONDESTRUCTIVE TESTING OF WELDED JOINTS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 360-16: Section N5.5 | | |
| TASK | INSPECTION TYPE [[4]](#footnote-4) | DESCRIPTION |
| 1. Use of qualified nondestructive testing personnel | **PERFORM** | Visual weld inspection and nondestructive testing (NDT) shall be conducted by personnel qualified in accordance with AWS D1.8 clause 7.2 |
| 1. CJP groove welds | OBSERVE | **[NOTE: DOR must delete this row if section D (SEISMIC PROVISIONS SECTION) is checked]**  Dye penetrant testing (DT) and ultrasonic testing (UT) shall be performed on 20% of CJP groove welds for materials greater than 5/16” (8mm) thick. Testing rate must be increased to 100% if greater than 5% of welds tested have unacceptable defects. |
| 1. Welded joints subject to fatigue | OBSERVE | Dye penetrant testing (DT) and Ultrasonic testing (UT) shall be performed on 100% of welded joints identified on contract drawings as being subject to fatigue. |
| 1. Weld tab removal sites | OBSERVE | At the end of welds where weld tabs have been removed, magnetic particle testing shall be performed on the same beam-to-column joints receiving UT |

**END SECTION**

**STRUCTURAL - STEEL – AISC 341 REQUIREMENTS (SEISMIC PROVISIONS) SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| NONDESTRUCTIVE TESTING OF WELDED JOINTS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 341-16: Section J6.2 | | |
| TASK | INSPECTION TYPE [[5]](#footnote-5) | DESCRIPTION |
| **[NOTE: DOR may uncheck this section for projects NOT designed in accordance with AISC 341 (Seismic Provisions) or for projects designed according to AISC 341, but using an R value equal to 3]** | | |
| 1. CJP groove welds | OBSERVE | Dye penetrant testing (DT) and ultrasonic testing (UT) shall be performed on 100% of CJP groove welds for materials greater than 5/16” thick (8mm). |
| 1. Beam cope and access hole. | OBSERVE | At welded splices and connections, thermally cut surfaces of beam copes and access holes shall be tested using magnetic particle testing (MT) or dye penetrant testing (DT), when the flange thickness exceeds 1 1/2 in. for rolled shapes, or when the web thickness exceeds 1 1/2 in. for built-up shapes. |
| 1. K-area NDT (AISC 341) | **PERFORM** | Where welding of doubler plates, continuity plates or stiffeners has been performed in the k-area, the web shall be tested for cracks using magnetic particle testing (MT). The MT inspection area shall include the k-area base metal within 3-inches of the weld. The MT shall be performed no sooner than 48 hours following completion of the welding. |
| 1. Placement of reinforcing or contouring fillet welds | **DOCUMENT** |  |

**END SECTION**

**STRUCTURAL - STEEL - COMPOSITE CONSTRUCTION [[6]](#footnote-6)**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| COMPOSITE CONSTRUCTION PRIOR TO PLACING CONCRETE – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 360-16: Table N6.1, AISC 341-16: Table J9.1 | | |
| TASK | INSPECTION TYPE 2 | DESCRIPTION |
| 1. Placement and installation of steel headed stud anchors | **PERFORM** |  |
| 1. Material identification of reinforcing steel (Type/Grade) | OBSERVE |  |
| 1. Determination of carbon equivalent for reinforcing steel other than ASTM A706 | OBSERVE |  |
| 1. Proper reinforcing steel size, spacing, clearances, support, and orientation | OBSERVE |  |
| 1. Reinforcing steel has not been re-bent in the field | OBSERVE |  |
| 1. Reinforcing clearances have been provided | OBSERVE |  |
| 1. Reinforcing steel has been tied and supported as required | OBSERVE |  |
| 1. Composite member has required size | OBSERVE |  |

**END SECTION**

**STRUCTURAL - STEEL - OTHER INSPECTIONS**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| OTHER STEEL INSPECTIONS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.2.1, AISC 341-16: Tables J8.1 & J10.1 | | |
| TASK | INSPECTION TYPE [[7]](#footnote-7) | DESCRIPTION |
| 1. Anchor rods and other embedments supporting structural steel | **PERFORM** | Verify the diameter, grade, type, and length of the anchor rod or embedded item, and the extent or depth of embedment prior to placement of concrete. |
| 1. Fabricated steel or erected steel frame | OBSERVE | Verify compliance with the details shown on the construction documents, such as braces, stiffeners, member locations and proper application of joint details at each connection. |
| 1. Reduced beam sections (RBS) where/if occurs | **DOCUMENT** | * Contour and finish * Dimensional tolerances |
| 1. Protected zones | **DOCUMENT** | No holes or unapproved attachments made by fabricator or erector |
| 1. H-piles where/if occurs | **DOCUMENT** | No holes or unapproved attachments made by the responsible contractor |

**END SECTION**

**STRUCTURAL - COLD-FORMED METAL DECK - PLACEMENT SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| METAL DECK INSPECTION PRIOR TO DECK PLACEMENT – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.1 | | |
| TASK | INSPECTION TYPE [[8]](#footnote-8) | DESCRIPTION |
| 1. Verify compliance of materials (deck and all deck accessories) with construction documents, including profiles, material properties, and base metal thickness | **PERFORM** |  |
| 1. Document acceptance or rejection of deck and deck accessories | **DOCUMENT** |  |
| METAL DECK INSPECTION DURING DECK PLACEMENT – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.2 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Verify compliance of deck and all deck accessories installation with construction documents | **PERFORM** |  |
| 1. Verify deck materials are represented by the mill certifications that comply with the construction documents | **PERFORM** |  |
| 1. Document acceptance or rejection of installation of deck and deck accessories | **DOCUMENT** |  |
| METAL DECK INSPECTION AFTER DECK PLACEMENT – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.3 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Welding procedure specification (WPS) available | **PERFORM** |  |
| 1. Manufactures certifications for welding consumables available | OBSERVE |  |
| 1. Material identification (type/grade) | OBSERVE |  |
| 1. Check welding equipment | OBSERVE |  |

**END SECTION**

**STRUCTURAL - COLD-FORMED METAL DECK – WELDING SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| METAL DECK INSPECTION DURING WELDING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.4 | | |
| TASK | INSPECTION TYPE [[9]](#footnote-9) | DESCRIPTION |
| 1. Use of qualified welders | OBSERVE |  |
| 1. Control and handling of welding consumables | OBSERVE |  |
| 1. Environmental conditions (wind speed, moisture, temperature) | OBSERVE |  |
| 1. WPS followed | OBSERVE |  |
| METAL DECK INSPECTION AFTER WELDING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.5 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Verify size and location of welds, including support, sidelap, and perimeter welds. | **PERFORM** |  |
| 1. Welds meet visual acceptance criteria | **PERFORM** |  |
| 1. Verify repair activities | **PERFORM** |  |
| 1. Document acceptance or rejection of welds | **DOCUMENT** |  |

**END SECTION**

**STRUCTURAL - COLD-FORMED METAL DECK – FASTENING SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| METAL DECK INSPECTION BEFORE MECHANICAL FASTENING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.6 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Manufacturer installation instructions available for mechanical fasteners | OBSERVE |  |
| 1. Proper tools available for fastener installation | OBSERVE |  |
| METAL DECK INSPECTION DURING MECHANICAL FASTENING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.7 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Fasteners are positioned as required | OBSERVE |  |
| 1. Fasteners are installed in accordance with manufacturer's instructions | OBSERVE |  |
| METAL DECK INSPECTION AFTER MECHANICAL FASTENING – VERIFY THE FOLLOWING ARE IN COMPLIANCE  SDI QA/QC-2011, Appendix 1, Table 1.8 | | |
| TASK | INSPECTION TYPE [[10]](#footnote-10) | DESCRIPTION |
| 1. Check spacing, type, and installation of support fasteners | **PERFORM** |  |
| 1. Check spacing, type, and installation of sidelap fasteners | **PERFORM** |  |
| 1. Check spacing, type, and installation of perimeter fasteners | **PERFORM** |  |
| 1. Verify repair activities | **PERFORM** |  |
| 1. Document acceptance or rejection of mechanical fasteners | **DOCUMENT** |  |

**END SECTION**

**STRUCTURAL - LIGHT GAUGE STEEL FRAMING AND/OR LIGHT GAUGE TRUSSES SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| LIGHT GAUGE STEEL CONSTRUCTION AND CONNECTIONS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC 1705.2.2, 1705.11.2, 1705.11.3, UFC 4 023 03 | | |
| TASK | INSPECTION TYPE[[11]](#footnote-11) | DESCRIPTION |
| 1. Trusses spanning 60-feet or greater where/if applies | **PERFORM** | Verify that temporary and permanent truss restraint/bracing is installed in accordance with approved truss submittal package. |
| 1. Welded connections (seismic and/or wind resisting system) | OBSERVE | Visually inspect all welds composing part of the main wind or seismic force resisting system, including shearwalls, braces, collectors (drag struts), and hold-downs.  **[NOTE: DOR must identify critical wind and/or seismic force resisting welds in the contract drawings so that the special inspector can confirm compliance.]** |
| 1. Connections (seismic and/or wind resisting system) | OBSERVE | Visually inspect all screw attachment, bolting, anchoring and other fastening of components within the main wind or seismic force resisting system, including roof deck, roof framing, exterior wall covering, wall to roof/floor connections, braces, collectors (drag struts) and hold-downs.  **[NOTE: DOR must identify critical wind and/or seismic force resisting connection/fastener components in the contract drawings so that the special inspector can confirm compliance.]** |
| 1. Cold-formed steel (progressive collapse resisting system where/if applies) | OBSERVE | Verify proper welding operations, screw attachment, bolting, anchoring and other fastening of components within the progressive collapse resisting system, including horizontal tie force elements, vertical tie force elements and bridging elements (UFC 4 023 03).  **[NOTE: DOR must identify critical progressive collapse resisting connection/fastener components in the contract drawings so that the special inspector can confirm compliance.]** |

**END SECTION**

**STRUCTURAL - OPEN-WEB STEEL JOISTS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| OPEN-WEB STEEL JOISTS AND JOIST GIRDERS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC TABLE 1705.2.3 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Installation of open-web steel joists and joist girders | OBSERVE | * End connections – welded or bolted * Bridging – horizontal and diagonal |

**END SECTION**

**STRUCTURAL - CONCRETE CONSTRUCTION SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| CONCRETE CONSTRUCTION, INCLUDING COMPOSITE DECK – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC TABLE 1705.3 (ACI 318 REFERENCES NOTED IN IBC TABLE) | | |
| TASK | INSPECTION TYPE [[12]](#footnote-12) | DESCRIPTION |
| 1. Inspect reinforcement, including prestressing tendons, and verify placement. | OBSERVE | Verify prior to placing concrete that reinforcing is of specified type, grade and size; that it is free of oil, dirt and unacceptable rust; that it is located and spaced properly; that hooks, bends, ties, stirrups and supplemental reinforcement are placed correctly; that lap lengths, stagger and offsets are provided; and that all mechanical connections are installed per the manufacturer’s instructions and/or evaluation report. |
| 1. Reinforcing bar welding | OBSERVE | * Verify weldability of reinforcing bars other than ASTM A 706 * Inspect single-pass fillet welds, maximum 5/16” in accordance with AWS D1.4 |
| 1. All other welding | **CONTINUOUS** | Visually inspect all welds in accordance with AWS D1.4 |
| 1. Cast in place anchors and post installed drilled anchors (downward inclined) | OBSERVE | Verify prior to placing concrete that cast in place anchors and post installed drilled anchors have proper embedment, spacing and edge distance. |
| 1. Post-installed adhesive anchors in horizontal or upward inclined orientations | **CONTINUOUS AND DOCUMENT** | * Inspect as required per approved ICC-ES report * Verify that installer is certified for installation of horizontal and overhead installation applications * Inspect proof loading as required by the contract documents (IBC Table 1705.3, 4) |
| 1. Verify use of required mix design | OBSERVE | Verify that all mixes used comply with the approved construction documents(IBC Table 1705.3, 5) |
| 1. Prior to concrete placement, fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of the concrete | **CONTINUOUS** | At the time fresh concrete is sampled to fabricate specimens for strength test verify these tests are performed by qualified technicians. |
| 1. Inspect concrete and/or shotcrete placement for proper application techniques | **CONTINUOUS** | Verify proper application techniques are used during concrete conveyance and depositing avoids segregation or contamination. Verify that concrete is properly consolidated. |
| 1. Verify maintenance of specified curing temperature and technique | OBSERVE | Inspect curing, cold weather protection, and hot weather protection procedures. |
| 1. Pre-stressed concrete | **CONTINUOUS** | Verify application of prestressing forces and grouting of bonded prestressing tendons. |

**CONTINUED ON FOLLOWING PAGE**

**STRUCTURAL - CONCRETE CONSTRUCTION (CONTINUED)**

|  |  |  |
| --- | --- | --- |
| CONCRETE CONSTRUCTION, INCLUDING COMPOSITE DECK – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC TABLE 1705.3 (ACI 318 REFERENCES NOTED IN IBC TABLE) | | |
| TASK | INSPECTION TYPE [[13]](#footnote-13) | DESCRIPTION |
| 1. Inspect erection of precast concrete members | OBSERVE |  |
| 1. Verify in-situ concrete strength, prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | OBSERVE |  |
| 1. Inspect formwork for shape, location and dimensions of the concrete member being formed. | OBSERVE |  |

**END SECTION**

**STRUCTURAL - MASONRY CONSTRUCTION SECTION (ALL RISK CATEGORIES)**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| MASONRY CONSTRUCTION – VERIFY THE FOLLOWING ARE IN COMPLIANCE AT START OF CONSTRUCTION  IBC 1705.4 (ACI 530-13 TABLE 3.1.2 & 3.1.3) | | |
| TASK | INSPECTION TYPE [[14]](#footnote-14) | DESCRIPTION |
| 1. Compliance with approved submittals prior to start | OBSERVE |  |
| 1. Proportions of site-mixed mortar. | OBSERVE |  |
| 1. Grade and type of reinforcement, anchor bolts, and prestressing tendons and anchorages | OBSERVE |  |
| 1. Prestressing technique | OBSERVE |  |
| 1. Properties of thin bed mortar for AAC masonry | OBSERVE |  |
| MASONRY CONSTRUCTION – VERIFY THE FOLLOWING ARE IN COMPLIANCE PRIOR TO GROUTING  IBC 1705.4 (ACI 530-13 TABLE 3.1.2 & 3.1.3) | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Grout space | OBSERVE  **CONTINUOUS** | **[NOTE: DOR must either delete ‘OBSERVE’ for Risk Category IV/V, or delete ‘CONTINUOUS’ for Risk Categories I/II/ III]** |
| 1. Proportions of site-prepared grout and prestressing grout for bonded tendons | OBSERVE |  |
| 1. Proportions of site-mixed grout and prestressing grout for bonded tendons | OBSERVE |  |
| 1. Placement of masonry units and mortar joints | OBSERVE |  |
| 1. Welding of reinforcement | **CONTINUOUS** |  |
| MASONRY CONSTRUCTION – VERIFY THE FOLLOWING ARE IN COMPLIANCE DURING CONSTRUCTION  IBC 1705.4 (ACI 530-13 TABLE 3.1.2 & 3.1.3) | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Size and location of structural elements is in compliance | OBSERVE |  |
| 1. Preparation, construction, and protection of masonry during cold weather (temperature below 40oF (4.4oc) or hot weather (temp above 90oF (32.2oC)) | OBSERVE |  |
| 1. Application and measurement of prestressing force | **CONTINUOUS** |  |
| 1. Placement of grout and prestressing grout for bonded tendons | **CONTINUOUS** |  |
| 1. Placement of AAC masonry units and construction of thin bed mortar joints | **CONTINUOUS** | Continuous for first 5000 square feet only (465 square meters). |
| 1. Observe preparation of grout specimens, mortar specimens, and/or prisms | OBSERVE |  |
| 1. Type, size and placement of reinforcement, connectors, anchor bolts and prestressing tendons and anchorages, including details of anchorage of masonry to structural members, frames, or other construction | OBSERVE  **CONTINUOUS** | **[NOTE: DOR must either delete ‘OBSERVE’ for Risk Category IV/V, or delete ‘CONTINUOUS’ for Risk Categories I/II/III]** |

**END SECTION**

**STRUCTURAL - WOOD CONSTRUCTION – SPECIALTY ITEMS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| WOOD CONSTRUCTION – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC 1705.5 | | |
| TASK | INSPECTION TYPE [[15]](#footnote-15) | DESCRIPTION |
| 1. High-load diaphragms where applicable | OBSERVE | Verify thickness and grade of sheathing, size of framing members at panel edges, nail diameters and length, and the number of fastener lines and that fastener spacing is per approved contract documents. |
| 1. Metal-plate connected wood trusses spanning 60 feet or greater | OBSERVE | Verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package |

**END SECTION**

**STRUCTURAL - WOOD CONSTRUCTION - SEISMIC & WIND SECTION**

**THIS SECTION IS APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| WOOD CONSTRUCTION SEISMIC AND WIND – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.11 & 1705.12.2 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| **[NOTE: DOR may uncheck this section where sheathing nailing/fasteners (both shearwall and roof) are consistently greater than 4” on center, or if the design wind speed (ASD) is less than 110 mph (49 meters/sec) AND the seismic design category is A or B]** | | |
| 1. Nailing, bolting, anchoring and other fastening of elements of the main wind/seismic force-resisting system | OBSERVE (CONTINUOUS FOR GLUING) | Includes connectors for: shearwall sheathing, roof/floor sheathing, drag struts/collectors (double top plates), braces, hold downs, roof connections to exterior walls. |

**END SECTION**

**STRUCTURAL – ISOLATION AND ENERGY DISSIPATION SYSTEMS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| ISOLATION AND ENERGY DISSIPATION SYSTEMS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC TABLE 1705.12.8 | | |
| **[NOTE: This section is not applicable to Seismic Design Category A. Uncheck this section if this category applies]** | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Fabrication and installation | OBSERVE | Verify that fabrication and installation of isolator units and energy dissipation devices conform to manufacturer’s recommendations and approved construction documents |
| 1. Testing of seismic isolation Systems in seismically isolated structures |  | Seismic Isolation Systems in seismically isolated structures shall be tested accordance with ASCE 7, Section 17.8 |

**END SECTION**

**GEOTECHNICAL - SOILS INSPECTION SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| SOILS INSPECTION – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC 1705.6 | | |
| TASK | INSPECTION TYPE [[16]](#footnote-16) | DESCRIPTION |
| 1. Materials below shallow foundations are adequate to achieve the design bearing capacity. | OBSERVE |  |
| 1. Excavations are extended to proper depth and have reached proper material | OBSERVE |  |
| 1. Perform classification and testing of compacted fill materials | **OBSERVE** |  |
| 1. Verify use of proper materials, densities and lift thicknesses during placement and compaction of compacted fill | **CONTINUOUS** |  |
| 1. Prior to placement of compacted fill, inspect subgrade and verify that site has been prepared properly. | OBSERVE | During fill placement, the special inspector shall verify that proper materials and procedures are used in accordance with the provisions of the approved geotechnical report |

**END SECTION**

**GEOTECHNICAL - DRIVEN DEEP FOUNDATION ELEMENTS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| DEEP DRIVEN FOUNDATION CONSTRUCTION – VERIFY THE FOLLOWING ARE IN COMPLIANCE  IBC 1705.7 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Verify element materials, sizes and lengths comply with requirements | **CONTINUOUS** |  |
| 1. Inspect driving operations and maintain complete and accurate records for each element | **CONTINUOUS** |  |
| 1. Verify placement locations and plumbness, confirm type and size of hammer, record number of blows per foot of penetration, determine required penetrations to achiever design capacity, record tip and butt elevations and document any damage to foundation element | **CONTINUOUS** |  |
| 1. Determine capacities of test elements and conduct additional load tests if required. | **CONTINUOUS** |  |
| 1. For steel or concrete elements, perform additional special inspections in accordance with the Steel and Concrete sections in this schedule |  |  |

**END SECTION**

**GEOTECHNICAL - HELICAL PILE FOUNDATIONS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| HELICAL PILE FOUNDATIONS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.9 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Record installation equipment used, pile dimensions, tip elevations, final depth, final installation torque and other pertinent installation data as required. The approved geotechnical report and the contract documents shall be used to determine compliance | **CONTINUOUS** |  |

**END SECTION**

**GEOTECHNICAL - CAST IN PLACE DEEP FOUNDATION ELEMENTS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| CAST IN PLACE DEEP FOUNDATION ELEMENTS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.8 | | |
| TASK | INSPECTION TYPE [[17]](#footnote-17) | DESCRIPTION |
| 1. Inspect drilling operations and maintain complete and accurate records for each element. | **CONTINUOUS** |  |
| 1. Verify placement locations and plumbness, confirm element diameters, bell diameters (if applicable), lengths, embedment into bedrock (if applicable) and adequate end-bearing strata capacity. Record concrete or grout volumes | **CONTINUOUS** | For concrete elements, perform additional special inspections in accordance with the Concrete section in this schedule |

**END SECTION**

**FIRE PROTECTION - SPRAYED FIRE-RESISTANT MATERIALS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| SPRAYED FIRE RESISTANT MATERIALS (SFRM) – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.14 | | |
| TASK | INSPECTION TYPE [[18]](#footnote-18) | DESCRIPTION |
| 1. Substrate condition | OBSERVE | Prior to application, confirm that surfaces have been prepared according to the approved fire-resistance design and manufacturer’s instructions. |
| 1. Material thickness | OBSERVE | Verify SFRM thickness according to 2018 IBC 1705.14.4 |
| 1. Material density | OBSERVE | Verify SFRM density according to 2018 IBC 1705.14.5 |
| 1. Bond strength | OBSERVE | Verify bond strength of cured SFRM according to IBC 1705.14.6 |

**END SECTION**

**FIRE PROTECTION - MASTIC AND INTUMESCENT COATINGS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| MASTIC AND INTUMESCENT FIRE-RESISTANT COATINGS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.15 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Inspect according to AWCI 12-B and the contract documents | OBSERVE | Inspections shall be performed in accordance with AWCI 12-B, Standard Practice for the Testing and Inspection of Field Applied Thin Film Intumescent Fire-Resistive Materials. |

**END SECTION**

**FIRE PROTECTION – FIRE RESISTANT PENETRATIONS AND JOINTS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| FIRE RESISTANT PENETRATIONS AND JOINTS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.17 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| 1. Inspections of penetration firestop systems conducted in accordance with ASTM E 2174. | OBSERVE | **[NOTE: This section applies to Risk Category III, IV, & V only. DOR may choose to uncheck this section where project is assigned to Risk Category I or II. Confirm Risk Category with Structural Engineer]** |
| 1. Inspections of fire-resistant joint systems conducted in accordance with ASTM E 2393 | OBSERVE |

**END SECTION**

**FIRE PROTECTION – SMOKE CONTROL SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| SMOKE CONTROL – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.18 | | |
| TASK | INSPECTION TYPE [[19]](#footnote-19) | DESCRIPTION |
| 1. Verify device locations and perform leakage testing | OBSERVE | Perform during erection of ductwork and prior to concealment |
| 1. Pressure difference testing, flow measurements and detection and control verification | OBSERVE | Perform prior to occupancy and after sufficient completion |

**END SECTION**

**ARCHITECTURAL - EXTERIOR INSULATION AND FINISH SYSTEMS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| EXTERIOR INSULATION AND FINISH SYSTEMS (EIFS) – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.16 | | |
| TASK | INSPECTION TYPE [[20]](#footnote-20) | DESCRIPTION |
| 1. Water resistive barrier coating applied over a sheathing substrate. | OBSERVE | Verify that water resistive barrier coating complies with ASTM E 2570.  **[NOTE: not applicable to masonry or concrete wall applications. Uncheck this section in those cases]** |

**END SECTION**

**ARCHITECTURAL – ARCHITECTURAL COMPONENTS**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| ARCHITECTURAL COMPONENTS – VERIFY THE FOLLOWING ARE IN COMPLIANCE  2018 IBC 1705.12.5, 1705.12.7 | | |
| TASK | INSPECTION TYPE 1 | DESCRIPTION |
| **[NOTE: This section is not applicable to Seismic Design Categories A, B, & C. Uncheck this section if one of those categories applies. Confirm Seismic Design Category with the structural engineer]** | | |
| 1. Erection and fastening of exterior cladding and interior and exterior veneer. | OBSERVE | Verify appropriate materials, fasteners and attachment at commencement of work and at completion. **Inspector** **Note: Inspection not required if height is less than 30 feet or weight is less than 5psf** |
| 1. Interior and exterior non-load bearing walls | OBSERVE | Verify appropriate materials, fasteners and attachment at commencement of work and at completion. **Inspector** **Note: Inspection not required if interior non-load bearing walls weigh less than 15psf** |
| 1. Access floors | OBSERVE | Verify that anchorage complies with approved construction documents. |
| 1. Storage racks | OBSERVE | Verify that anchorage complies with approved construction documents. Inspection of post-installed anchors shall comply with approved ICC-ES report. **Inspector** **Note: Not required for racks less than 8 feet in height** |

**END SECTION**

**PLUMBING/MECHANICAL/ELECTRICAL DESIGNATED SEISMIC SYSTEMS SECTION**

**ALL OR PORTIONS OF THIS SECTION ARE APPLICABLE IF BOX IS CHECKED:**

|  |  |  |
| --- | --- | --- |
| PLUMBING, MECHANICAL AND ELECTRICAL  IBC 1705.12.6 | | |
| TASK | INSPECTION TYPE [[21]](#footnote-21) | DESCRIPTION |
| **[NOTE: This section is not applicable to Seismic Design Categories A or B. Uncheck this section if one of those categories applies. Confirm Seismic Design Category with structural engineer]** | | |
| 1. Anchorage of electrical equipment for emergency and standby power systems | OBSERVE | * Check for general conformance |
| 1. Anchorage of all other electrical equipment in Seismic Design Categories E and F only (See first page of this schedule for Seismic Design Category) | OBSERVE | * Check for general conformance |
| 1. Installation and anchorage of piping designed to carry hazardous materials and their associated mechanical units. | OBSERVE | * Check for general conformance |
| 1. Installation and anchorage of vibration isolation systems where the construction documents require a nominal clearance of ¼” or less between support framing and restraint. | OBSERVE | * Check for general conformance |
| 1. Verification of clearance between fire sprinkler piping and surrounding mechanical and electrical equipment, including ductwork, piping and their structural supports. | OBSERVE | * Check for minimum clearances noted in ASCE7 13.2.3 or a nominal clearance of not less than 3 inches |

**END SECTION**

1. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-1)
2. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports. [↑](#footnote-ref-2)
3. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

   **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports. [↑](#footnote-ref-3)
4. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-4)
5. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

   **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports. [↑](#footnote-ref-5)
6. See Concrete Construction Section for all concrete related inspection of composite steel construction. [↑](#footnote-ref-6)
7. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

   **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports. [↑](#footnote-ref-7)
8. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

   **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports. [↑](#footnote-ref-8)
9. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

   **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

   **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports. [↑](#footnote-ref-9)
10. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

    **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

    **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports. [↑](#footnote-ref-10)
11. **PERFORM**: Perform these tasks for each weld, fastener or bolted connection, and required verification.

    **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-11)
12. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

    **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports.

    **CONTINUOUS:** Constant monitoring of identified tasks by a special inspector over the duration of performance of said tasks. [↑](#footnote-ref-12)
13. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

    **DOCUMENT**: Document in a report that the work has been performed as required. This is in addition to all other required reports.

    **CONTINUOUS:** Constant monitoring of identified tasks by a special inspector over the duration of performance of said tasks. [↑](#footnote-ref-13)
14. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

    **CONTINUOUS:** Constant monitoring of identified tasks by a special inspector over the duration of performance of said tasks. [↑](#footnote-ref-14)
15. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-15)
16. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk.

    **CONTINUOUS:** Constant monitoring of identified tasks by a special inspector over the duration of performance of said tasks. [↑](#footnote-ref-16)
17. **CONTINUOUS:** Constant monitoring of identified tasks by a special inspector over the duration of performance of said tasks. [↑](#footnote-ref-17)
18. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-18)
19. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-19)
20. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-20)
21. **OBSERVE**: Observe these items on a random sampling basis daily to insure that applicable requirements are met. Operations need not be delayed pending these inspections at contractor’s risk. [↑](#footnote-ref-21)