## Read Me
Not all columns of the Points Schedule will be used. Which are used depends on the protocol selection. Rows 4-7 of the Points Schedule in this file indicate which columns apply to which protocols. Once unused columns are deleted or hidden, rows 4-7 may also be deleted or hidden
Similarly, some notes will not apply depending on protocol selection. The column next to the notes indicate when a note is or not applicable. Remove non-applicable notes and replace the colored cells indicating applicability with blank cells.

## Points Schedule-Blank
<TITLE>
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | POINT NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <_____>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <_____>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <_____>

## Points Schedule-Sample Entries
VAV [WITH][WITHOUT] RETURN FAN
EXAMPLE ONLY. This example Points Schedule is intended to demonstrate the overall format for a Points Schedule and illustrate the type and scope of entries. Points Schedules for actual systems/sequences are being updated and created under a separate effort to update HVAC Sequences of Operation. The points shown is this Points Schedule are not represetnative of a properly designed system.
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | POINT NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
| PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS |  |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [info] [crit] | [___] |  | <___> | <___> | [7 empty] | <INTRINSIC><REMOTE ALGORITHMIC><LOCAL ALGORITHMIC><NIAGARA FRAMEWORK>
|  | RF-S | RETURN FAN STATUS |  |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | RETURN FAN PROOF FAILED | [info] [crit] | [___] |  | <___> | <___>
|  | SA-SMK | SUPPLY AIR SMOKE |  |  | ALM/NORMAL | BI | [5 empty] | ALM | [info] [crit] | [___] |  | <___> | <___>
|  | RA-SMK | RETURN AIR SMOKE |  |  | ALM/NORMAL | BI | [5 empty] | ALM | [info] [crit] | [___] |  | <___> | <___>
|  | CLG-DA-T-LL | COOLING COIL DISCHARGE AIR TEMP LOW LIMIT |  | 39 DEG F | ALM/NORMAL | BI |  | H | V | [~] |  | ALM | [info] [crit] | [___] |  | <___> | <___>
|  | SA-P-HL | SUPPLY AIR PRESSURE HIGH LIMIT |  | [___ IWC] | ALM/NORMAL | BI |  | H |  |  |  | ALM | [info] [crit] | [___] |  | <___> | <___>
|  | RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) |  |  |  | [NET-IN][BI] | [9 empty] | [<___>][~] | [<___>][~]
| SCHEDULING | SYS-OCC-SCHED | SYSTEM OCCUPANCY SCHEDULE |  | SEE OCCUPANCY SCHEDULE DRAWING |  | <NET-OUT> |  | OC | V | [~] |  |  |  |  | SCHEDULE OBJECT <___> | [12 empty] | <___>
| START/STOP | UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTES) |  |  |  | NET-OUT |  |  | [V] | [ ~ ] | [ ~ ] | ~ | ~ | ~ |  | <___> | <___>
|  | SYS-OCC-C | OCCUPANCY COMMAND |  |  | OCCUPIED(1)/WUCD(2)/UNOCCUPIED(3) | <NET-IN> |  |  | VO | [~] | [ ~ ] |  |  |  | MSV <___> | <___> | <SNVT_OCCUPANCY> <SNVT_TOD_EVENT>
|  | SYS-OCC | SYSTEM OCCUPANCY (ACTUAL) |  |  | OCCUPIED(1)/WUCD(2)/UNOCCUPIED(3) | <~><NET-OUT> |  |  | V | [V] | X |  |  |  | MSV <___> | <___> | SNVT_OCCUPANCY
|  | SF-SS | SUPPLY FAN START/STOP |  |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] |  |  |  |  | <___> | <___>
|  | RF-SS | RETURN FAN START/STOP |  |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] |  |  |  |  | <___> | <___>
|  | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) |  |  | <___> | <AI><NET-IN> |  |  | V | [ ~ ] | [ ~ ] | BLDG-T LESS THAN BLDG-T-LL | [info] [crit] | [___] |  | <___> | <___>
|  | BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] | [17 empty] | <___>
| SUPPLY FAN CAPACITY CONTROL | SF-C | SUPPLY FAN COMMAND |  |  | 0-100% | AO | [~] |  | VO | [ ~ ] | [ ~ ] |  |  |  |  | <___> | <___>
|  | SA-P | SUPPLY AIR PRESSURE |  |  | <___> | AI, NET-OUT |  |  | V | [ V ] | X | SYSTEM HAS BEEN IN OCCUPIED MODE FOR MORE THAN 5 MINUTES AND SA-P IS MORE THAN 20% ABOVE OR BELOW SA-P-SP | [info] [crit] | <___> |  | <___> | <___> |  |  | DDC #17, DDC #18, DDC #19
|  | SA-P-SP | SUPPLY AIR PRESSURE SETPOINT |  | <___> |  |  |  | C | VO | [ ~ ] | [5 empty] | <___> | <___>
|  | SUPPLY FAN CONTROL LOOP CONFIGURATION SETTINGS | PROPORTIONAL CONSTANT
INTEGRAL CONSTANT
BIAS
MAXIMUM OUTPUT
MINIMUM OUTPUT
<____>
| RETURN FAN CAPACITY CONTROL | SA-F | SUPPLY AIR FLOW |  |  | [0 - ___ CFM] | NET-IN |  |  | V | [ V ] | [ ~ ] | [ ~ ] | ~ | [___] |  | <___> | <___> |  | DDC#12
|  | RA-F | RETURN AIR FLOW |  |  | [0 - ___ CFM] | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | ~ | [___] |  | <___> | <___>
|  | RF-C | RETURN FAN COMMAND |  |  | 0-100% | AO | [~] |  | VO | [ ~ ] | [ ~ ] |  |  |  |  | <___> | <___>
|  | F-DIFF-SP | FLOW DIFFERENCE SETPOINT |  | [___ CFM] |  |  |  | OC | VO | [ ~ ] | [5 empty] | <___> | <___> | [10 empty] | <___>
|  | RETURN FAN CONTROL LOOP CONFIGURATION SETTINGS | PROPORTIONAL CONSTANT | [5 empty] | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT | [5 empty] | C | [19 empty] | <___>
|  |  | BIAS | [5 empty] | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT | [5 empty] | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT | [5 empty] | C | [19 empty] | <___>
|  |  | <____> | [5 empty] | C | [19 empty] | <___>
| MINIMUM OUTSIDE AIR | MINOA-F | MINIMUM OUTSIDE AIR FLOW |  |  | [0 - ___ CFM] | AI |  |  | V | [ V ] | X | MINOA-F LESS THAN 80% OF MINOA-F-SP | [info] [crit] | [___] |  | <___> | <___>
|  | MINOA-D-C | MINIMUM OUTSIDE AIR DAMPER COMMAND |  |  | <0-100% OPEN> | AO | [~] |  | VO | [ V ] | [ ~ ] |  |  |  |  | <___> | <___>
|  | MINOA RESET SCHEDULE FOR DCV | CO2 MAXIMUM VALUE |  | [___ PPM] |  |  |  | C
|  |  | CO2 MINIMUM VALUE |  | [___ PPM] |  |  |  | C
|  |  | MINOA FLOW MINIMIM VALUE (AT CO2 MINIMUM VALUE) |  | [___ CFM] |  |  |  | C
|  |  | MINOA FLOW MAXIMUM VALUE (AT CO2 MAXIMUM VALUE) |  | [___ CFM] |  |  |  | C
|  | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT (SETTING) |  | [___ CFM] |  |  |  | C | VO | [~] | [5 empty] | <___> | <___> | [10 empty] | <___>
|  | MINIMIM OUTSIDE AIR DAMPER CONTROL LOOP CONFIGURATION SETTINGS | PROPORTIONAL CONSTANT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <____> |  | <___> |  |  |  | C | [19 empty] | <___>
| MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE |  |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | ~ | [ ~ ] |  | <___> | <___>
|  | MA-T | MIXED AIR TEMPERATURE |  |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | ~ | [ ~ ] |  | <___> | <___>
|  | MA-D-C | MIXED AIR DAMPER COMMAND |  |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] |  |  |  |  | <___> | <___>
|  | ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | [~] | [ V ] | [5 empty] | <___> | <___> | [10 empty] | <___>
|  | ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [5 empty] | <___> | <___> | [10 empty] | <___>
|  | MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] |  |  |  | C | VO | [~] | [5 empty] | <___> | <___> | [10 empty] | <___>
|  | MIXED AIR DAMPER CONTROL LOOP CONFIGURATION SETTINGS | <THROTTLING RANGE><PROPORTIONAL GAIN> |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <ALL OTHER CONFIG SETTINGS - ADD ROWS AS NEEDED> |  | <___> |  |  |  | C | [19 empty] | <___>
| SUPPLY AIR TEMPERATURE | SA-T | SUPPLY AIR TEMPERATURE |  |  | <___> | AI |  |  | V | [ V ] | X | SYSTEM HAS BEEN IN OCCUPIED MODE FOR MORE THAN 5 MINUTES AND SA-T MORE THAN 10 DEG F ABOVE OR BELOW SETPOINT | [info] [crit] | [___] |  | <___> | <___>
|  | CLG-V-C | COOLING VALVE COMMAND |  |  | <0-100% OPEN> | AO | [~] |  | VO | [ V ] | [ ~ ] |  |  |  |  | <___> | <___>
|  | SA-T-SP | SUPPLY AIR TEMPERATURE SETPOINT |  | [55 DEG F] |  |  |  | OC | VO | [ V ] | [5 empty] | <___> | <___> | [10 empty] | <___>
|  | COOLING VALVE CONTROL LOOP CONFIGURATION SETTINGS | <THROTTLING RANGE><PROPORTIONAL GAIN> |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT |  | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <____> |  | <___> |  |  |  | C | [19 empty] | <___>
| OTHER POINTS | RA-T | RETURN AIR TEMPERATURE |  |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | ~ | [___] |  | <___> | <___>
|  | MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH |  | <___> | ALM/NORMAL | BI |  | H | ~ | [ ~ ] |  | ALM | [info] [crit] | [___] |  | <___> | <___>
|  | OA-FLT-P | OUTSIDE AIR FILTER PRESSURE |  |  | <___> | AI |  |  | V | [ ~ ] |  | OA-FLT-P LESS THAN OA-FLT-P-LL | [info] [crit] | [___] |  | <___> | <___>
|  | OA-FLT-P-LL | OUTSIDE AIR FILTER PRESSURE LOW LIMIT |  | <___> |  |  |  | C | ~ | [ ~ ]
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <_____>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <_____>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <_____>