| UPS SYSTEM PERFORMANCE DATA SHEET |
| --- |
|  | ITEM | SPECIFIED | SUBMITTED |
|  | SYSTEM OPERATION | [SINGLE MODULE] [PARALLEL REDUNDANT] [PARALLEL NON REDUNDANT] |  |
|  | NUMBER OF SYSTEMS |  |  |
| GENERAL MODULE | NUMBER OF MODULES IN EACH SYSTEM | PRESENT [_____] |  |
|  |  | FUTURE [_____] |  |
|  | PRESENT SYSTEM CAPACITY | [_____] kW/[_____] kVA |  |
|  | FUTURE SYSTEM CAPACITY | [_____] kW/[_____] kVA |  |
|  | BATTERY | ONE PER MODULE |  |
|  | MTBF (SYSTEM) |  |  |
|  | MTTR |  |  |
|  | MODULE RATING | [_____] kW/[_____] kVA |  |
|  | DC VOLTAGE WINDOW | [_____] Vdc |  |
|  | INPUT/OUTPUT PROTECTIVE DEVICE INTERRUPT RATING | [_____] A SYM. |  |
| BATTERY | MANUFACTURER |  |  |
|  | TYPE | [LEAD-CALCIUM] [LEAD-ANTIMONY] [NICKEL-CADMIUM] |  |
|  | DISCHARGE TIME TO END VOLTAGE AT FULL LOAD | [_____] MINUTES |  |
|  | END VOLTAGE | [_____] V/CELL |  |
|  | SPECIFIC GRAVITY |  |  |
|  | FLOAT VOLTAGE | [_____] V/CELL |  |
|  | NUMBER OF CELLS | [_____] CELLS |  |
|  | HYDROGEN GENERATION |  |  |
|  | RECHARGE TIME TO 95 percent CAPACITY | 10 X DISCHARGE |  |
| SYS CABINET | PROTECTIVE DEVICE | [AIR POWER, DRAW-OUT] [_____] |  |
|  | MANUFACTURER |  |  |
|  | INTERRUPTING RATE | [_____] A SYM. |  |
|  | STATIC SWITCH | [_____] A |  |
| AC INPUT | VOLTS, LINE/LINE | [_____] V |  |
|  | PHASES | [3-PHASE, 3-WIRE] [_____] |  |
|  | VOLTAGE RANGE | + 10 percent, - 15 percent |  |
|  | FREQUENCY | [50] [60] Hz |  |
|  | FREQUENCY RANGE | + or – 5 percent |  |
|  | POWER WALK-IN 20 TO 100 percent LOAD | 15 - 24 SECONDS |  |
|  | TOTAL HARMONIC DISTORTION REFLECTED-PRIMARY | [5 percent MAX (CURRENT)] [_____] |  |
|  | ORDER OF HARMONIC (fill in as required) |  | PERCENTAGE OF TOTAL |
|  | 2nd |  |  |
|  | 3rd |  |  |
|  | 4th |  |  |
|  | 5th |  |  |
|  | 6th |  |  |
|  | 7th |  |  |
|  | 8th |  |  |
|  | 9th |  |  |
|  | TRANSFORMER SUB-CYCLE INRUSH | [_____] x FULL LOAD |  |
|  | POWER FACTOR | [0.8] [0.9] |  |
| AC OUTPUT | VOLTAGE, LINE-LINE | [_____] V |  |
|  | PHASES | 3-PHASE, 4-WIRE |  |
|  | POWER FACTOR | 0.8 LAGGING, 1.0 |  |
|  | VOLTAGE REGULATION |
|  | BALANCED LOAD | +/- 1.0 percent |  |
|  | 50 percent IMBALANCE BETWEEN PHASES | +/- 2.0 percent |  |
|  | NO-LOAD MODULATION | +/- 1.0 percent |  |
|  | DRIFT (30 DAYS) | +/- 1.0 percent |  |
|  | VOLTAGE ADJUST. | +/- 5.0 percent MANUALLY |  |
|  | FREQUENCY - 60 Hz |
|  | REGULATION | +/- 0.1 percent |  |
|  | DRIFT (24 HRS.) | +/- 0.1 percent |  |
|  | HARMONIC CONTENT |
|  | TOTAL (50% NON-LINEAR LOAD | 7.0 percent MAX. |  |
|  | TOTAL (LINEAR LOAD) | 5.0 percent MAX. |  |
|  | SINGLE HARMONIC (LINEAR LOAD) | 3.0 percent MAX. |  |
|  | PHASE DISPLACEMENT |
|  | BALANCED LOAD | +/- 1.0 DEG. OF BYPASS |  |
|  | 50 percent IMBALANCE | +/- 3.0 DEG. OF BYPASS |  |
|  | WAVE FORM DEVIATION FACTOR | 5.0 percent (NO LOAD) |  |
|  | OVERLOAD CAPACITY |
|  | 125 percent | 10 MINUTES |  |
|  | 150 percent | 30 SECONDS |  |
|  | 300 percent | MOMENTARY |  |
|  | LOAD SHARING AMONG MODULES | +/- 5.0 percent OF AVERAGE LOAD |  |
|  | VOLT. TRANSIENT RESPONSE |
|  | 50% STEP LOAD 0 to 50 percent | +/- 8.0 percent |  |
|  | 50% STEP LOAD 50 to 100% | +/- 8.0 percent |  |
|  | LOSS OR RETURN OF INPUT | +/- 1.0 percent |  |
|  | LOSS OR RETURN OF A REDUNDANT MODULE - AUTOMATICALLY | +/- 8.0 percent |  |
|  | LOSS OR RETURN OF A REDUNDANT MODULE - MANUALLY | +/- 8.0 percent |  |
|  | AUTO TRANSFER, AT FULL LOAD, FROM UPS TO BYPASS | +/- 4.0 percent |  |
|  | MANUAL TRANSFER, AT FULL LOAD, FROM BYPASS TO UPS | +/- 4.0 percent |  |
|  | RECOVERY TIME TO 99% STEADY-STATE CONDITION | 50 MILLISECONDS |  |
|  | FREQUENCY TRANSIENT RESPONSE | +/- 0.5 Hz |  |
|  | SLEW RATE | 1.0 Hz/SECOND |  |
|  | EFFICIENCY AT FULL LOAD |
|  | MODULE | [_____]percent |  |
|  | SYSTEM | [_____]percent |  |
| ENVIRONMENTAL | SYSTEM NOISE GEN. LEVEL @ 1.8 M (6 FT.) FROM EQUIPMENT | [_____] DBA |  |
|  | OPERATING AMBIENT TEMPERATURE | 0 to [40] [50] DEG. C (32 to [104] [122] DEG. F) |  |
|  | STORAGE AMBIENT TEMPERATURE | -20 to +60 DEG. C (-4 to +140 DEG. F.) |  |
|  | BATTERY ROOM AMBIENT TEMPERATURE | 25 DEG. C (77 DEG. F) NOMINAL |  |
|  | RELATIVE HUMIDITY (NON-CONDENSING) | 0 - 95 percent |  |
|  | BAROMETRIC PRESSURE (ALTITUDE) |
|  | OPERATING | 0 - [_____] FT. |  |
|  | NON-OPERATING | 0 – 12,200 m (40,000 FT.) |  |
|  | HEAT REJECTION |
|  | MODULE |  |  |
|  | SYSTEM |  |  |
| PHYSICAL DATA | MODULE SIZE |  |  |
|  | MODULE WEIGHT |  |  |
|  | SYSTEM CABINET SIZE |  |  |
|  | SYSTEM CABINET WEIGHT |  |  |
|  | BATTERY |
|  | SEISMIC PARAMETERS |  |  |
|  | RACKS SIZE |  |  |
|  | RACKS WEIGHT |  |  |
|  | CELLS SIZE |  |  |
|  | CELLS WEIGHT |  |  |
|  | DISCONNECT SIZE |  |  |
|  | DISCONNECT WEIGHT |  |  |