SECTION 01013 - SUMMARY OF THE WORK - ASBESTOS ABATEMENT

PART 1 - GENERAL

BASED ON SECTION 01010 "SUMMARY OF WORK" FROM MASTERSPEC TEXT COPYRIGHTED IN 1993 BY AIA, THE AMERICAN INSTITUTE OF ARCHITECTS.

THIS SECTION HAS BEEN COMPLETELY REVISED FROM THE 2ND EDITION TO REFLECT THE CHANGES OF THE REVISED CORRESPONDING MASTERSPEC SECTION.

THIS SECTION USES THE TERM DESIGNER. CHANGE THIS TERM AS NECESSARY TO MATCH THE ACTUAL TERM USED TO IDENTIFY THE DESIGN PROFESSIONAL AS DEFINED IN THE GENERAL AND SUPPLEMENTARY CONDITIONS.

THIS SECTION, MORE THAN ANY OTHER, IS PROJECT SPECIFIC. SAMPLE TEXT IS CONTAINED IN THE EVALUATIONS TO ILLUSTRATE POSSIBLE SECTION CONTENT. REVISE SAMPLE PARAGRAPHS CAREFULLY TO REFLECT SPECIFIC PROJECT REQUIREMENTS, OR DELETE THEM IF THEY DO NOT APPLY. SEE EVALUATIONS FOR SAMPLE TEXT AND FURTHER DISCUSSION

THIS SECTION IS BASED ON THE PRESUMPTION THAT THE ABATEMENT CONTRACTOR WILL HAVE A CONTRACT DIRECTLY WITH THE OWNER THAT IS INDEPENDENT FROM ALL OTHER CONTRACTORS PERFORMING WORK. IT ALSO ASSUMES THAT THE CONTRACT DOCUMENTS FOR THE ABATEMENT WORK ARE COMPLETELY INDEPENDENT OF DOCUMENTS FOR OTHER PORTIONS OF THE WORK. IF A MORE COMPLICATED RELATIONSHIP EXISTS THEN THIS SECTION SHOULD BE SUBSTANTIALLY REVISED.

1.1	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections, apply to this Section.

1.2	WORK COVERED BY CONTRACT DOCUMENTS

THIS ARTICLE ILLUSTRATES ONE METHOD OF SUMMARIZING THE WORK. REVISE AS NECESSARY TO DESCRIBE THE PROJECT ACCURATELY.

IN THE FOLLOWING PARAGRAPHS, REMOVE TEXT ENCLOSED IN ANGLE BRACKETS <> AND INSERT TEXT APPROPRIATE FOR THE PROJECT.

PARAGRAPH BELOW IDENTIFIES NAME AND LOCATION OF THE PROJECT AND NAME OF THE OWNER AND THE DESIGNER.

A.	The Project consists of <INSERT BRIEF PROJECT DESCRIPTION>

1.	Project Location:  <INSERT PROJECT LOCATION (STREET ADDRESS, CITY, AND STATE).>

2.	Owner:  <INSERT NAME AND ADDRESS OF THE OWNER.>

B.	Contract Documents, dated <INSERT DATE INDICATED IN THE CONTRACT DOCUMENTS> were prepared for the Project by <INSERT NAME AND ADDRESS OF THE DESIGNER>.

INSERT PARAGRAPH IDENTIFYING THE CONSTRUCTION MANAGER FOR PROJECTS CONDUCTED USING CONSTRUCTION-MANAGEMENT TECHNIQUES.

INCLUDE AN ABBREVIATED SUMMARY OF WORK FOR THE PROJECT DESCRIBED ABOVE IN PARAGRAPHS BELOW. USE LANGUAGE IDENTICAL TO THAT IN THE AGREEMENT.

C.	The Work consists of <INSERT AN ABBREVIATED SUMMARY OF THE PROJECT>

THE FOLLOWING SUBPARAGRAPH IS USUALLY NOT NECESSARY UNLESS THE ABATEMENT INVOLVES INSTALLATION OF UNIQUE SYSTEMS, SUCH AS MAJOR HVAC MODIFICATIONS, INSTALLATION OF TEMPORARY WORK PLATFORMS WITH FINISHED WALLS AND CEILINGS, AND ISOLATION OF COMPUTER SYSTEMS.

1.	The Work includes <INSERT A BRIEF LISTING OF MAJOR PRODUCTS AND SYSTEMS INCLUDED IN THE PROJECT>

INSERT ADDITIONAL PARAGRAPHS FOR OTHER MAJOR ITEMS OF WORK.

RETAIN THE FOLLOWING IF THE ABATEMENT WORK IS TO BE CARRIED OUT AS A SINGLE PRIME CONTRACT. SEE EVALUATIONS

D.	The Work will be constructed under a single prime contract.

1.3	WORK UNDER OTHER CONTRACTS

RETAIN THIS ARTICLE IF WORK UNDER THIS CONTRACT DEPENDS ON SUCCESSFUL COMPLETION OF WORK PERFORMED UNDER OTHER CONTRACTS AND VICE VERSA. SEE EVALUATIONS FOR FURTHER DISCUSSION

RETAIN PARAGRAPH BELOW WHEN WORK UNDER OTHER CONTRACTS IS EXPECTED TO BE COMPLETE BEFORE WORK ON THIS CONTRACT BEGINS. REVISE TO SUIT ACTUAL PROJECT CONDITIONS.

A.	Separate Contract:  The Owner has awarded a separate contract for performance of certain construction operations at the site.  Those operations are scheduled to be substantially complete before work under this Contract begins.  The separate contract includes the following:

RETAIN SUBPARAGRAPH BELOW FOR EACH SEPARATE CONTRACT. REMOVE TEXT ENCLOSED IN ANGLE BRACKETS <> AND INSERT TEXT APPROPRIATE FOR THE PROJECT. REPEAT SUBPARAGRAPH BELOW AS NECESSARY TO LIST ALL SEPARATE CONTRACTS.

1.	Contract:  A separate contract has been awarded to <INSERT NAME OF SEPARATE CONTRACTOR> for <INSERT A BRIEF DESCRIPTION OF WORK  PERFORMED UNDER THE SEPARATE CONTRACT>.

RETAIN PARAGRAPH BELOW WHEN WORK UNDER OTHER CONTRACTS WILL BE CONDUCTED CONCURRENTLY WITH WORK UNDER THIS CONTRACT. REVISE TO SUIT ACTUAL PROJECT CONDITIONS.

B.	Separate Contract:  The Owner has awarded a separate contract for performance of certain construction operations at the site.  Those operations will be conducted simultaneously with work under this Contract.  That Contract includes the following:

RETAIN SUBPARAGRAPH BELOW FOR EACH SEPARATE CONTRACT. REMOVE TEXT ENCLOSED IN ANGLE BRACKETS <> AND INSERT TEXT APPROPRIATE FOR THE PROJECT. REPEAT SUBPARAGRAPH BELOW AS NECESSARY TO LIST ALL SEPARATE CONTRACTS.

1.	Contract:  A separate contract has been awarded to <INSERT NAME OF SEPARATE CONTRACTOR> to <INSERT A BRIEF DESCRIPTION OF WORK PERFORMED UNDER THE SEPARATE CONTRACT>.

C.	Cooperate fully with separate contractors so that work under those contracts may be carried out smoothly, without interfering with or delaying work under this Contract.

1.4	FUTURE WORK

RETAIN THIS ARTICLE IF WORK UNDER A FUTURE CONTRACT DEPENDS ON SUCCESSFUL COMPLETION OF WORK PERFORMED UNDER THIS CONTRACT. SEE EVALUATIONS FOR FURTHER DISCUSSION

REVISE PARAGRAPH BELOW TO SUIT ACTUAL PROJECT CONDITIONS. .

A.	Future Contract:  The Owner has awarded a separate contract for additional work to be performed at the site following Substantial Completion.  Completion of that work depends on successful completion of preparatory work under this Contract.  The Contract for future work includes the following:

RETAIN SUBPARAGRAPH BELOW FOR EACH SEPARATE CONTRACT. REMOVE TEXT ENCLOSED IN ANGLE BRACKETS <> AND INSERT TEXT APPROPRIATE FOR THE PROJECT. REPEAT SUBPARAGRAPH BELOW AS NECESSARY TO LIST ALL SEPARATE CONTRACTS.

1.	Contract:  A separate contract has been awarded to <INSERT NAME OF SEPARATE CONTRACTOR> to <INSERT A BRIEF DESCRIPTION OF WORK PERFORMED UNDER THE SEPARATE CONTRACT>.

1.5	WORK SEQUENCE

RETAIN THIS ARTICLE IF THE PROJECT IS CONDUCTED IN SEPARATE PHASES. DELETE IF PHASED CONSTRUCTION IS NOT REQUIRED. SEE EVALUATIONS FOR DISCUSSION ON PHASED CONSTRUCTION.

AMPLIFY PARAGRAPH BELOW IF NECESSARY. REVISE TO SUIT ACTUAL PROJECT CONDITIONS.

A.	The Work will be conducted in <INSERT NUMBER OF PHASES> phases.

RETAIN SUBPARAGRAPH BELOW FOR EACH PHASE REQUIRED. REMOVE TEXT ENCLOSED IN ANGLE BRACKETS <> AND INSERT TEXT APPROPRIATE FOR THAT PHASE. REPEAT SUBPARAGRAPH, REVISED AS APPROPRIATE, FOR EACH SEPARATE PHASE.

1.	Phase <INSERT PHASE NUMBER>:  <BRIEFLY DESCRIBE WORK OF THIS PHASE.> Work of this phase shall be substantially complete, ready for reconstruction within <INSERT TIME> of commencement of construction.

1.6	ASBESTOS-CONTAINING MATERIALS:

OSHA REQUIRES THAT THE OWNER NOTIFY THE CONTRACTOR ABOUT THE LOCATION OF ASBESTOS IN THE BUILDING. INFORMATION ON ASBESTOS TYPE AND CONTENT IS IMPORTANT FOR THE CONTRACTOR TO KNOW. THIS HELPS THE CONTRACTOR ESTIMATE HOW WELL THE MATERIAL WILL WET AND HENCE HOW DUSTY THE WORK IS LIKELY TO BE. THIS AFFECTS THE TYPE OF RESPIRATORY PROTECTION REQUIRED AND MAN-HOURS OF EFFORT NEEDED FOR REMOVAL. REFER TO THE EVALUATIONS FOR ADDITIONAL DISCUSSION.

A.	The Work of this contract involves activities that will disturb asbestos-containing materials (ACM) or presumed asbestos-containing materials (PACM).  The location and type of ACM known to be present at the worksite is set forth in the drawings.  If any other ACM or PACM is  found, notify the owner, other employers and employees the about  the location and quantity of the ACM or PACM within 24 hours of the discovery.

DELETE EITHER PARAGRAPH ABOVE OR BELOW. RETAIN PARAGRAPH ABOVE AND DELETE BELOW IF DRAWINGS SHOWING THE LOCATION AND TYPE OF ACM ARE USED TO INDICATE THE SCOPE OF WORK. DELETE PARAGRAPH ABOVE AND RETAIN BELOW IF THERE ARE NO DRAWINGS AND A SCHEDULE IS USED TO DELINEATE THE SCOPE OF THE WORK. THE SCHEDULE SHOWN AT THE END OF THIS SECTION IS ADEQUATE AS A NOTIFICATION, BUT WOULD NEED TO BE MUCH MORE SPECIFIC TO ADEQUATELY SET FORTH THE SCOPE OF WORK FOR THE PROJECT.

B.	The Work of this contract involves activities that will disturb asbestos-containing materials (ACM).  The location and type of ACM known to be present at the worksite is set forth in the Schedule of Asbestos-Containing Materials at the end of this section.  If any other ACM or PACM is  found, notify the owner, other employers and employees about  the location and quantity of the ACM or PACM within 24 hours of the discovery.

1.7	ASBESTOS HEALTH RISK:

A.	The disturbance or dislocation of ACM may cause asbestos fibers to be released into the building`s atmosphere, thereby creating a potential health risk to workers and building occupants.  Apprise all workers, supervisory personnel, subcontractors and consultants who will be at the job site of the seriousness of the  risk and of proper work procedures which must be followed.

B.	Where in the performance of the work, workers, supervisory personnel, subcontractors, or consultants may encounter, disturb, or otherwise function in the immediate vicinity of any identified ACM, take appropriate continuous measures as necessary to protect all building occupants from the risk of exposure to airborne asbestos.  Such measures shall include the procedures and methods described herein, and compliance with regulations of applicable federal, state and local agencies.

1.8	CONTRACTOR USE OF PREMISES

THIS ARTICLE SPECIFIES REQUIREMENTS THAT GOVERN THE CONTRACTOR'S USE OF THE PREMISES.

RETAIN PARAGRAPH BELOW WHEN THE PROJECT IS ON A VACANT SITE OR IN AN UNOCCUPIED BUILDING BEING RENOVATED. REVISE IF NECESSARY. IF PARAGRAPH IS RETAINED, DELETE THE REMAINDER OF THE ARTICLE UNLESS UNUSUAL PROJECT REQUIREMENTS EXIST.

A.	General:  During the construction period the Contractor shall have full use of the premises for construction operations, including use of the site.  The Contractor's use of the premises is limited only by the Owner's right to perform work or to retain other contractors on portions of the Project.

DELETE ABOVE AND RETAIN BELOW IF THE SITE WILL BE ACCESSIBLE TO OTHER PARTIES, OR IF SOME PARTS OF A BUILDING BEING RENOVATED WILL BE OCCUPIED DURING CONSTRUCTION. REVISE TO SUIT SPECIFIC PROJECT REQUIREMENTS.

B.	Use of the Site:  Limit use of the premises to work in areas indicated.  Confine operations to areas within contract limits indicated.  Do not disturb portions of the site beyond the areas in which the Work is indicated.

1.	Owner Occupancy:  Allow for Owner occupancy and use by the public.

SUBPARAGRAPH BELOW CONTAINS AN EXAMPLE OF A SPECIAL REQUIREMENT APPROPRIATE TO MANY PROJECTS. CHANGE THE REQUIREMENT AS NECESSARY TO SUIT PROJECT CONDITIONS OR DELETE IF INAPPROPRIATE.

2.	Driveways and Entrances:  Keep driveways and entrances serving the premises clear and available to the Owner, the Owner's employees, and emergency vehicles at all times.  Do not use these areas for parking or storage of materials.  Schedule deliveries to minimize space and time requirements for storage of materials and equipment on-site.

INSERT ADDITIONAL PARAGRAPHS AS APPROPRIATE, DESCRIBING ADDITIONAL LIMITATIONS ON USE OF THE SITE BY CONSTRUCTION PERSONNEL.

RETAIN REQUIREMENTS BELOW WHEN THE WORK INVOLVES AN EXISTING OCCUPIED BUILDING. DELETE OTHERWISE.

C.	Use of the Existing Building:  Maintain the existing building in a weather tight condition throughout the construction period.  Repair damage caused by construction operations.  Take all precautions necessary to protect the building and its occupants during the construction period.

INSERT ADDITIONAL PARAGRAPHS SPECIFYING SPECIFIC LIMITATIONS ON A CONTRACTOR'S USE OF AN EXISTING BUILDING. SUBPARAGRAPH BELOW CONTAINS AN EXAMPLE OF A SPECIAL REQUIREMENT APPROPRIATE TO MANY PROJECTS. CHANGE THE REQUIREMENT AS NECESSARY TO SUIT PROJECT CONDITIONS OR DELETE IF INAPPROPRIATE.

COORDINATE THE FOLLOWING PARAGRAPH WITH DIVISION-1 SECTION ON TEMPORARY ENCLOSURES AND DIVISION-14 SECTION ON ELEVATORS. MODIFY THE PARAGRAPH AS APPROPRIATE TO SUIT PROJECT. DELETE IF PROVISIONS ARE INCLUDED ELSEWHERE, OR IF THE PROJECT DOES NOT INVOLVE THE USE OF ELEVATORS. THE FOLLOWING IS WORKABLE FOR SMALL PROJECTS IN BUILDINGS WHERE THE OWNER MAKES INFREQUENT USE OF ELEVATORS. ON HIGH RISE PROJECTS THESE RESTRICTIONS ON THE CONTRACTOR MAY BE UNWORKABLE. USE OF ELEVATORS SHOULD BE CAREFULLY WORKED OUT WITH THE OWNER AND CONTRACTOR. OVER TIGHT RESTRICTIONS ON THE CONTRACTORS USE OF ELEVATORS CAN RESULT IN SCHEDULING OR COST PROBLEMS.

1.	Use of Existing Elevators:  Except for the Freight Elevator, use of elevators by the Contractor will not be permitted.  The Contractor will be permitted to use the freight elevator for temporary freight service and the transportation of construction personnel during the construction period.  This elevator must also be available to the Owner at all times; coordinate freight elevator usage with the Designer.  Provide protective pads for the elevator car and other appropriate protective measures for the car and entrance doors and frames.  During asbestos abatement activities the car is to be protected as set forth in the Division 1 Section on Temporary Enclosures.

2.	Smoking: Smoking or open fires will not be permitted within the building enclosure or on the premises.

COORDINATE THE FOLLOWING PARAGRAPH WITH OTHER DIVISION-1 SECTIONS ON TEMPORARY FACILITIES. MODIFY AS REQUIRED TO SUIT PROJECT.

3.	Toilet Rooms:  Except for toilet rooms designated for use by the Contractor's personnel, use of existing toilets within the building, by the Contractors  personnel, will not be permitted.

1.9	OCCUPANCY REQUIREMENTS

THE ARTICLE BELOW CONTAINS SAMPLE PARAGRAPHS DESCRIBING OCCUPANCY OF THE PROJECT DURING CONSTRUCTION. IT ALSO DESCRIBES PARTIAL OCCUPANCY BEFORE SUBSTANTIAL COMPLETION.

RETAIN PARAGRAPH BELOW WHEN THE OWNER WILL OCCUPY THE PREMISES DURING CONSTRUCTION. MODIFY AS NECESSARY.

A.	Full Owner Occupancy:  The Owner will occupy the site and existing building during the entire construction period.  Cooperate with the Owner during construction operations to minimize conflicts and facilitate owner usage.  Perform the Work so as not to interfere with the Owner's operations.

RETAIN PARAGRAPH BELOW WHEN THE OWNER MIGHT OCCUPY COMPLETED PORTIONS OF THE BUILDING PRIOR TO SUBSTANTIAL COMPLETION. MODIFY TO SUIT PROJECT REQUIREMENTS.

B.	Partial Owner Occupancy:  The Owner reserves the right to occupy and to place and install equipment in completed areas of the building prior to Substantial Completion, provided such occupancy does not interfere with completion of the Work.  Such placing of equipment and partial occupancy shall not constitute acceptance of the total Work.

SUBPARAGRAPHS BELOW DESCRIBE PROCEDURES AND REQUIREMENTS NECESSARY BEFORE PARTIAL OCCUPANCY OF PORTIONS OF THE PROJECT.

1.	The Designer will prepare a Certificate of Substantial Completion for each specific portion of the Work to be occupied prior to Owner occupancy.

1.10	AIR MONITORING BY THE OWNER:

A.	The Owner has contracted for air monitoring.  Air monitoring may be conducted both outside and inside of the work area during the work, and for clearance sampling at the end of the project

1.	Outside of the Work Area: The Owner's air monitoring firm may sample air outside of the work area to detect faults in the work area isolation such as:

a.	Contamination of the building outside of the work area with airborne asbestos fibers,

b.	Failure of filtration or rupture in the differential pressure system,

c.	Contamination of air outside the building envelop with airborne asbestos fibers.

2.	Inside the Work Area:  The Owners air monitoring firm may monitor airborne fiber counts in the Work Area.  The purpose of this air monitoring is to detect airborne asbestos concentrations which may challenge the ability of the Work Area isolation procedures to protect the balance of the building or outside of the building from contamination by airborne fibers.

B0	Work area clearance: Clearance air sampling by the Owners air monitor at the completion of asbestos abatement work is described in Section 01711 Project Decontamination.

C0	Air monitoring required by OSHA is work of the Contractor and is not covered in this section

1.11	SCHEDULE OF AIR SAMPLES BY OWNER:

EDIT THIS SECTION WITH THE ASSISTANCE OF THE FIRM THAT WILL BE PROVIDING AIR MONITORING. REFER TO EVALUATION FOR MORE INFORMATION.

A0	Sample cassettes:  Samples will be collected on 25 mm. cassettes as follows:

1	PCM:  0.8 micrometer mixed cellulose ester.

2	TEM:  0.45 micrometer mixed cellulose ester or 0.40 micrometer polycarbonate, with 5.0 micron mixed cellulose ester backing filter.

B0	Number and Volume of Samples:  The number and volume of air samples given in the schedules is approximate.  The exact number and volume of samples collected by the Owner may vary depending upon job conditions and the analytical method used.

C0	Sample Volume and Sensitivity:

1	PCM: The sample volumes collected by the Owners air monitor will be determined by the following formula:

Where:

Number of fibers	=	5 fibers/100 fields, based on a limit of detection (LOD) of 7 fibers/mm2 on the filter

Area of 100 fields	= 	0.785mm2

Total Filter Area 	= 	385mm2

Limit Value 	=	as specified in the schedules of samples below

a0	For purposes of this specification, the sample volume calculated above will be considered to be of sufficient size so that there is a 95% level of confidence that the value measured by each individual sample at the limit of detection (LOD) is less than or equal to the limit values specified below.

b0	For purposes of this specification, the Limit of Detection (LOD) is defined as 7 fibers/mm2 on the filter or  5 fibers/100 fields.

c0	For purposes of this specification overloaded samples will be considered as exceeding the applicable limit value.

2	TEM:  Analytical Sensitivity of 0.05 structures/cc as set forth in the AHERA regulation.

D0	Base Line:

1	Before Start of Work: The Owner will secure air samples to establish a base line.

2	PCM Samples

Location 	   		Number  		Limit		Approx.  	Rate

Sampled     			of 			Value 		Volume   	(Liters/

Samples        	(Fibers/cc)  	(Liters)	Minute)

Each Work Area  		5  			0.01    	 	<1,000>   	1-10

Outside Each   		5   			0.01    	 	 <1,000>	1-10

Work Area

Outside Building 		5   			0.01    	  	<1,000>	1-10

3	TEM Samples:

Location 	   		Number  		Analytical 	Approx.	Rate

Sampled     			of 			Sensitivity  	Volume   	(Liters/

Samples        	(Struct./cc.)  	(Liters)	Minute)

Each Work Area  		1   			0.005    		1,300   		1-10

Outside Each   		1   			0.005    		1,300 		1-10

Work Area

Outside Building 		1   			0.005    		1,300   		1-10

4	Base Line:   a level expressed in fibers per cubic centimeter which is twenty-five percent greater than the largest of the following:

a0	Average of the PCM samples collected outside each Work Area

b0	Average of the PCM samples collected outside the building

c0	0.01 fibers per cubic centimeter

5	Samples collected for TEM analysis will be held without analysis.  These samples will be analyzed under the conditions and terms set forth in "Fibers Counted" and "Affect On Contract Sum".

E0	Daily:

1	From start of work of Section 01526 Temporary Enclosures through the work of Section 01711 Project Decontamination, the Owner may take samples.

2	Sample volume and sensitivity: inside the work area may vary depending upon conditions in the work area.  If samples are overloaded at the sample volume required for a limit value equal to the Stop Action Levels or Immediate Stop Action Levels given later in this section, the level is considered to have been exceeded.

FOLLOWING IS AN EXAMPLE AND SHOULD BE EDITED TO SUIT PROJECT SPECIFICS. THE LIMIT VALUE AND VOLUME OF SAMPLES INSIDE THE WORK AREA SHOULD TIE IN WITH THE STOP ACTION LEVELS SELECTED LATER IN THIS SECTION. SAMPLING REQUIREMENTS DEPEND ON SIZE AND GEOMETRY OF WORK AREA. NUMBER AND LOCATION OF SAMPLES SHOULD BE REVIEWED WITH THE ENTITY PROVIDING AIR MONITORING. IF THIN FIBERS ARE SUSPECTED OR NON-ASBESTOS FIBER ARE SUSPECTED THE FOLLOWING MAY HAVE TO BE AUGMENTED BY TEM OR SEM ANALYSIS.

3	PCM Samples:

Location 	   		Number  		Limit 		Approx.  	Rate

Sampled     			of 			Value 		Volume   	(LPM)

Samples        	(Fibers/cc)  	(Liters)

Each Work Area  		2  			<0.1>    		<100>		1-10

Outside Each   		1   			0.01    		 <1,000>	1-10

Work Area at

Critical Barrier

Clean Room   		1   			0.01    		  <1,000>	1-10

Equipment Decon		1   			0.01    		  <1,000>	1-10

Outside Building 		1   			0.01    		  <1,000>	1-10

Output of Pressure		1  			0.01 		  <1,000>	1-10

Differential System

F0	Additional samples may be taken at Owner's or  Designers discretion.  If airborne fiber counts exceed allowed limits additional samples may be taken as necessary to monitor fiber levels.

1.12	ANALYTICAL METHODS USED BY THE OWNER:

THIS ARTICLE SETS OUT THE "RULES" IN TERMS OF THE ANALYSIS THAT IS GOING TO BE PERFORMED BY THE OWNER. BASED ON THIS ANALYSIS, THE OWNER MAY, FOR CAUSE, STOP WORK OR OTHERWISE DELAY THE CONTRACTOR. IT IS NECESSARY TO CLEARLY SET OUT THE RULES TO AVOID DISPUTES.

A0	The following methods will be used by The Owner in analyzing filters used to collect air samples.  Sampling rates may be varied from printed standards to allow for high volume sampling.

CHOOSE ONE OF THE FOLLOWING PCM METHODOLOGIES AND DELETE THE OTHER ONE. SOME STATE AND LOCAL JURISDICTIONS REQUIRE ANALYSIS TO BE PERFORMED AT FIXED LABORATORY LOCATIONS ONLY. EDIT THE FOLLOWING ACCORDINGLY

1	Phase Contrast Microscopy (PCM)  will be performed using the NIOSH 7400 method.

2	Phase Contrast Microscopy (PCM)  will be performed using the OSHA Reference Method (ORM).

CHOOSE ONE OF THE FOLLOWING TEM METHODOLOGIES AND DELETE THE OTHER.

3	Transmission Electron Microscopy(TEM) will be performed using the analysis method set forth in the AHERA regulation 40 CFR Part 763 Appendix A.

4	Transmission Electron Microscopy (TEM) will be performed using the Level II analysis per EPA Provisional Method and Update (USEPA 1977, Yamate 1984), with either polycarbonate or mixed cellulose ester filters.

1.13	LABORATORY TESTING BY OWNER:

CHOOSE THE APPROPRIATE PARAGRAPH FROM THE THREE BELOW AND DELETE THE OTHER TWO. IT IS IMPORTANT TO THE CONTRACTOR TO KNOW HOW IMMEDIATELY AIR SAMPLE RESULTS WILL BE AVAILABLE.

THE FOLLOWING PARAGRAPH REPRESENTS THE IDEAL SITUATION FOR BOTH THE CONTRACTOR AND THE OWNER. IF THERE IS A PROBLEM WITH MAINTAINING LOW FIBER COUNTS THE ABILITY TO READ AN AIR SAMPLE IMMEDIATELY WILL BE AN IMPORTANT DIAGNOSTIC TOOL.

A0	The services of a testing laboratory may be employed by the Owner to perform laboratory analyses of the air samples.  A microscope and technician will be setup at the job site, so that verbal reports on air samples can be obtained immediately.

THE FOLLOWING PARAGRAPH SHOULD BE USED IF THERE WILL BE NO MICROSCOPE AT THE JOB SITE.

EDIT THE FOLLOWING TO INDICATE HOW SAMPLES WILL BE TRANSMITTED AND HANDLED.

B0	The services of a testing laboratory may be employed by the Owner to perform laboratory analyses of the air samples.  A technician will be at the job site, and samples will be sent daily by carrier for next day delivery, so that verbal reports on air samples can be obtained within 24 hours.

THE FOLLOWING PARAGRAPH IS A CATCH-ALL AND DOES NOT PROVIDE THE CONTRACTOR WITH DETAILED INFORMATION ON HOW THE OWNER INTENDS TO ANALYZE AIR SAMPLES.

C0	The services of a testing laboratory may be employed by the Owner to perform laboratory analyses of the air samples.  A microscope and technician will be set up at the job site, or samples will be sent overnight on a daily basis, so that verbal reports on air samples can be obtained within 24 hours.  The Contractor will have access to  all air monitoring tests and results.

CHOOSE ONE OF THE TWO PARAGRAPHS BELOW AND DELETE THE OTHER.

THE FOLLOWING PARAGRAPH ASSURES A HIGH LEVEL OF COMMUNICATION BETWEEN THE CONTRACTOR AND THE OWNER'S AIR MONITORING FIRM. THIS FREE FLOW OF INFORMATION INSURES THAT THE CONTRACTOR WILL HAVE THE INFORMATION HE NEEDS TO DETERMINE THE SUCCESS OF CONTROL MEASURES BEING IMPLEMENTED. HOWEVER, THIS DOES BIND THE OWNER TO PROVIDING THIS INFORMATION.

D0	A complete record of all air monitoring and results will be furnished to the  Designer, the Owner, and the Contractor.

THE FOLLOWING LANGUAGE PROTECTS THE OWNER FROM ABROGATION OF CONTRACT IF FOR SOME REASON HE FAILS TO PROVIDE TEST DATA.

E0	The Contractor will have access to  all air monitoring tests and results upon request.

FOLLOWING IS AN EXAMPLE. REVISE AFTER CONSULTATION WITH THE FIRM WHO WILL BE PROVIDING AIR MONITORING. POSTING OF RESULTS IS IDEAL FROM THE BOTH THE OWNER'S AND CONTRACTOR'S POINT OF VIEW. HOWEVER, THIS DOES BIND THE OWNER TO PROVIDE THIS INFORMATION.

F0	Written Reports:  of all air monitoring tests will be posted at the job site on a daily basis.

1.14	FIBERS AND STRUCTURES

THE FOLLOWING ESTABLISHES THE GROUND RULES WHICH WILL BE USED TO DETERMINE WHICH ANALYTICAL METHODS WILL BE USED AND WHAT DEFINITION OF "FIBER" WILL BE USED IN ENFORCING THE SPECIFICATION. THE FOLLOWING MAKES THE PCM MICROSCOPE, WHICH MAY BE AT THE JOB SITE, THE FIRST METHOD TO BE USED TO DETERMINE AIRBORNE FIBER COUNTS. IF THERE IS A CONSISTENT PROBLEM WITH HIGH FIBER COUNTS OR IF EXTREMELY SMALL FIBERS ARE ANTICIPATED THEN ELECTRON MICROSCOPY (PREFERABLY TEM) IS USED TO DETERMINE AIRBORNE FIBER COUNTS. THE FOLLOWING SHOULD BE REVIEWED WITH THE CONSULTANT PROVIDING ON-SITE AIR MONITORING FOR THE OWNER AND REVISED AS APPROPRIATE.

A0	Fibers Counted:  The following procedure will be used to resolve any disputes regarding fiber types when a project has been stopped  due to excessive airborne fiber counts.

THE FOLLOWING LANGUAGE SETS OUT THE METHOD OF RESOLVING SITUATIONS WHERE THERE ARE NON-ASBESTOS FIBERS IN THE AIR CAUSING HIGH PCM FIBER COUNTS. IN SITUATIONS WHERE THIS IS EXPECTED TO BE A PROBLEM, THE BACKGROUND SAMPLING SHOULD INCLUDE ELECTRON MICROSCOPY. THE INFORMATION ON THIS ANALYSIS SHOULD BE INCLUDED IN THE CONTRACT DOCUMENTS.

1	Large Fibers:  "Airborne Fibers" referred to above include all fibers regardless of composition as counted by phase contrast microscopy (PCM), unless additional analysis by transmission or scanning electron microscopy demonstrates to the satisfaction of the  Designer that non-asbestos fibers are being counted.  "Airborne Fibers" counted in samples analyzed by  transmission electron microscopy shall be  asbestos fibers, greater than 5 microns in length.  For purposes of stop action levels, subsequent to analysis by electron microscopy, the number of "Airborne Fibers" shall be determined by multiplying the number of fibers, regardless of composition, counted by PCM by the proportion of fibers that are asbestos as determined by TEM (a number equal to, asbestos fibers counted, divided by all fibers counted in the electron microscopy analysis).

THE FOLLOWING INCLUDES ASBESTOS STRUCTURES TOO SMALL TO BE SEEN WITH AN OPTICAL MICROSCOPE, IN THE DEFINITION OF FIBERS THAT CAN TRIGGER A STOP WORK. SEE EVALUATION

2	Small Structures:  "Airborne Fibers" referred to above include asbestos structures (fibers, bundles, clusters or matrices) of any diameter and any length greater than 0.5 microns.

1.15	ADDITIONAL TESTING:

IT IS NOT GOOD PRACTICE TO HAVE THE CONTRACTOR PROVIDE ANY OF THE TESTING DESCRIBED IN THIS SPECIFICATION SECTION. THESE ANALYSES ARE USED TO DETERMINE PERFORMANCE. THE FOLLOWING ADDRESSES THE TOPIC OF TESTING WHICH THE CONTRACTOR MAY WISH TO PERFORM . GENERALLY THIS WILL BE AIR SAMPLING PERFORMED FOR OSHA COMPLIANCE.

IT IS GOOD PRACTICE TO REQUIRE THE CONTRACTOR TO ENGAGE THE SERVICES OF AN INDEPENDENT LABORATORY RATHER THAN USING THE ENTITY PROVIDING SERVICES FOR THE OWNER.

A0	The Contractor may conduct  air monitoring and laboratory testing.  If he elects to do this the cost of such air monitoring and laboratory testing shall be at no additional cost to the Owner.

1.16	PERSONAL MONITORING:

A0	Owner will not perform air monitoring for the Contractor to meet Contractor's OSHA requirements for personal sampling or any other purpose.

1.17	MISCELLANEOUS PROVISIONS

RETAIN THIS ARTICLE ONLY WHEN THE PROJECT IS SUBJECT TO UNUSUAL GENERAL REQUIREMENTS THAT DO NOT BELONG ELSEWHERE BUT AFFECT THE ENTIRE PROJECT. DELETE THE ENTIRE ARTICLE IF NO UNUSUAL REQUIREMENTS ARE REQUIRED.

INSERT PARAGRAPHS HERE AS APPROPRIATE, DETAILING FULLY MISCELLANEOUS PROVISIONS. DEVELOP PARAGRAPHS TO SATISFY SPECIFIC PROJECT REQUIREMENTS.

PART 2 - PRODUCTS (Not Applicable)

PART 3  - EXECUTION

3.1	STOP ACTION LEVELS:

CHOOSE ONE OF THE TWO ARTICLES ON "INSIDE WORK AREA" BELOW AND DELETE THE OTHER. THE FIRST IS BASED ON A SINGLE STOP ACTION LEVEL. THE SECOND IS BASED ON THE RESPIRATORY PROTECTION BEING PROVIDED. BACKGROUND LEVELS SHOULD BE CONSIDERED IN SETTING STOP ACTION LEVELS. IN SOME INDUSTRIAL SETTINGS THE FOLLOWING COULD BE REQUIRING A CLEANER ENVIRONMENT THAN IS GENERALLY AVAILABLE OUTSIDE THE WORK AREA.

BELOW IS AN EXAMPLE. EDIT TO SUIT SPECIFIC PROJECT REQUIREMENTS. A SIMPLE STOP ACTION LEVEL OF 0.5 F/CC IS NOT REQUIRED BY ANY STANDARD OR CODE, BUT IS PRACTICAL TO MAINTAIN DURING THE COURSE OF A NORMAL REMOVAL, OR ENCAPSULATION, OR ENCLOSURE PROJECT. IF THIS LEVEL IS EXCEEDED IT MAY INDICATE THAT SOMETHING IS GOING WRONG. 0.5 IS A PRACTICAL LIMIT FOR A CHRYSOTILE REMOVAL PROJECT. THIS MAY NEED TO BE HIGHER FOR AN AMOSITE OR CROCIDOLITE PROJECT.

COORDINATE THIS SECTION WITH THE PEL AND RESPIRATOR PROTECTION FACTORS SPECIFIED IN SECTION 01562 RESPIRATORY PROTECTION. THE RESPIRATORY PROTECTION REQUIRED SHOULD PREVENT AN EXPOSURE GREATER THAN THE SPECIFIED PEL AT THE AIRBORNE LIMITS SET BELOW. FOR A TWA OF 0.01 F/CC A RESPIRATOR WITH A MINIMUM PROTECTION FACTOR OF 50 IS REQUIRED AT THE 0.5 F/CC SET FORTH BELOW. IF THE LIMIT BELOW WERE RAISED TO 1.0 F/CC (SUCH AS IT MIGHT FOR AN AMOSITE JOB), THEN RESPIRATORY PROTECTION WITH A PROTECTION FACTOR OF 100 WOULD NEED TO BE SPECIFIED IN 01562 TO MAINTAIN THE SAME PEL.

A0	Inside Work Area:  Maintain an average airborne count in the Work Area of less than 0.5 fibers per cubic centimeter.  If the fiber counts rise above this figure for any sample taken, revise work procedures to lower fiber counts.  If the Time Weighted Average (TWA) fiber count for any work shift or 8 hour period exceeds 0.5 fibers per cubic centimeter, stop all work, leave Pressure Differential System in operation and notify  Designer.  After correcting cause of high fiber levels, do not recommence work for 24 hours unless otherwise authorized, in writing, by  Designer.

1	If airborne fiber counts exceed 2.5  fibers per cubic centimeter for any period of time cease all work except corrective action until fiber counts fall below 0.5 fibers per cubic centimeter and notify  Designer.  After correcting cause of high fiber levels, do not recommence work for 24 hours unless otherwise authorized, in writing, by  Designer.

MAINTAINING THESE WORK PLACE FIBER COUNTS FOR AMOSITE REMOVALS MAY REQUIRE STRINGENT WORK PRACTICE CONTROL AND ADDITIONAL HEPA FILTERED PRESSURE DIFFERENTIAL AND VENTILATION SYSTEMS RE-CYCLED IN THE SPACE.

IF THE RESPIRATORY PROTECTION IS BASED ON A PARTICULAR TYPE OF RESPIRATOR RATHER THAN A STIPULATED PERMISSIBLE EXPOSURE LIMIT (PEL) THE STOP ACTION LEVELS BELOW SHOULD BE RELATED TO THE RESPIRATORY PROTECTION. THE STOP ACTION LEVELS GIVEN BELOW ARE BASED ON A TWA OF 0.01 F/CC AND AN IMMEDIATE STOP LEVEL 5 TIMES THIS AMOUNT.

B0	Inside Work Area:  Maintain an average airborne count in the work area of less than the Stop Action Level given below for the type of respiratory protection in use.  If the fiber counts rise above this figure for any sample taken, revise work procedures to lower fiber counts.  If the Time Weighted Average (TWA) fiber count for any work shift or 8 hour period exceeds the Stop Action Level, stop all work except corrective action, leave pressure differential and air circulation system in operation and notify  Designer.  After correcting cause of high fiber levels, do not recommence work for 24 hours unless otherwise authorized, in writing, by  Designer.

STOP 		IMMEDIATELY		MINIMUM

ACTION		STOP			RESPIRATOR 		PROTECTION

LEVEL		LEVEL			REQUIRED 			FACTOR

(f/cc)			(f/cc)

0.1			0.5				Half face			10

0.5			2.5				PAPR			50

1.0			5.0				Supplied Air			100

Pressure Demand

1	If airborne fiber counts exceed Immediate Stop Level given above for type of respiratory protection in use for any period of time cease all work except corrective action.  Notify  Designer.  Do not recommence work until fiber counts fall below Stop Action Level given above for the type of respiratory protection in use.  After correcting cause of high fiber levels, do not recommence work for 24 hours unless otherwise authorized, in writing, by  Designer.

MAINTAINING THESE WORK PLACE FIBER COUNTS FOR AMOSITE REMOVALS MAY REQUIRE STRINGENT WORK PRACTICE CONTROL AND ADDITIONAL PRESSURE DIFFERENTIAL AND HEPA FILTERED VENTILATION SYSTEMS RECYCLED IN THE SPACE.

EDIT THE FOLLOWING FOR PROJECT SPECIFICS. IN GENERAL, A PCM LIMIT SHOULD BE AT OR BELOW THE 0.01 F/CC AHERA CLEARANCE CRITERIA. AT AN ABSOLUTE MINIMUM REQUIREMENT, THE LEVEL REQUIRING REMEDIAL ACTION MUST BE LOWER THAN THE O.1 FIBERS PER CUBIC CENTIMETER OSHA PEL. IF THIS LEVEL IS EXCEEDED IT MAY BE NECESSARY TO INITIATE OSHA COMPLIANCE ACTIVITIES FOR BUILDING OCCUPANTS.

C0	Outside Work Area:  If any air sample taken outside of the Work Area exceeds the base line established in Part 1 of this section, immediately and automatically stop all work except corrective action.  The  Designer will determine the source of the high reading and so notify the Contractor in writing.

1	If the high reading was the result of a failure of Work Area isolation measures initiate the following actions:

a0	Immediately erect new critical barriers as set forth in Section 01526 Temporary Enclosures to isolate the affected area from the balance of the building.  Erect Critical Barriers at the next existing structural isolation of the involved space (e.g. wall, ceiling, floor).

b0	Decontaminate the affected area in accordance with Section 01712 Cleaning & Decontamination Procedures.

c0	Require that respiratory protection as set forth in Section 01562 Respiratory Protection be worn in affected area until area is cleared for re-occupancy in accordance with Section 01711 Project Decontamination.

d0	Leave Critical Barriers in place until completion of work and insure that the operation of the pressure differential system in the Work Area results in a flow of air from the balance of the building into the affected area.

e0	If the exit from the clean room of the personnel decontamination unit enters the affected area, establish a  decontamination facility consisting of a Shower Room and Changing Room as set forth in Section 01563 Decontamination Units at entry point to affected area.

f0	After Certification of Visual Inspection in the Work Area remove critical barriers separating the work area from the affected area.  Final air samples will be taken within the entire area as set forth in Section 01711 Project Decontamination.

2	If the high reading was the result of other causes initiate corrective action as determined by the  Designer.

FOLLOWING RESTATES IN MORE SPECIFIC FORM PROVISIONS OF THE GENERAL CONDITIONS.

D0	Effect on Contract Sum:  Complete corrective work with no change in the Contract Sum if high airborne fiber counts were caused by Contractor's activities.  The Contract Sum and schedule will be adjusted for additional work caused by high airborne fiber counts beyond the Contractor's control.

3.2	STOP WORK:

THIS SECTION CHANGES SOME OF THE NORMAL RELATIONSHIPS IN THE CONTRACTS FOR CONSTRUCTION. IT IS STRONGLY RECOMMENDED THAT ADVICE OF COUNSEL BE SOUGHT WHEN EDITING THIS SECTION.

PROBLEMS SUCH AS A CONTAINMENT FAILURE OR SUPPLIED AIR SYSTEM PROBLEMS CAN CREATE HEALTH AND SAFETY ISSUES THAT REQUIRE IMMEDIATE CORRECTION. ON ASBESTOS ABATEMENT PROJECTS, THE ON-SITE PROJECT ADMINISTRATOR IS FREQUENTLY GIVEN THE AUTHORITY TO STOP WORK. HOWEVER, THE RESPONSIBILITIES AND ASSOCIATED LIABILITIES FOR THE PARTIES IN THE CONSTRUCTION CONTRACT CHANGE FROM NORMAL PRACTICE WHEN THE PROJECT ADMINISTRATOR AND DESIGNER ARE GIVEN THE AUTHORITY TO STOP WORK. REFER TO THE EVALUATIONS FOR MORE DISCUSSION ON THIS MATTER.

IF THE FOLLOWING PARAGRAPH IS USED THE AGREEMENT BETWEEN THE OWNER AND PROJECT ADMINISTRATOR NEEDS TO BE CHANGED FROM NORMAL PRACTICE AND GIVE THE PROJECT ADMINISTRATOR THE AUTHORITY TO STOP WORK FOR THE OWNER. THE AIA AND EJCDC STANDARD GENERAL CONDITIONS WILL ALSO NEED TO BE ALTERED.

A0	If the Owner or the Project Administrator presents a written stop work order, immediately and automatically conform to that stop work order, while maintaining temporary enclosures and pressure differential.  Do not recommence abatement work until authorized in writing by Owner or Project Administrator.

DELETE EITHER PARAGRAPH ABOVE OR BELOW. RETAIN THE PARAGRAPH ABOVE AND DELETE THE PARAGRAPH BELOW IF THE AUTHORITY TO STOP WORK IS TO BE RETAINED BY THE OWNER, DELETE ABOVE AND RETAIN BELOW IF THE DESIGNER HAS AGREED TO ACCEPT RESPONSIBILITY FOR STOPPING WORK.

B.	If the Owner, Designer, or Project Administrator  presents a written stop work order, immediately and automatically conform to that stop work order, while maintaining temporary enclosures and pressure differential.  Do not recommence abatement work until authorized in writing by Owner, Designer or Project Administrator.

IN GENERAL ALWAYS RETAIN THE FOLLOWING. REVISE AS NECESSARY FOR PROJECT SPECIFICS.

C.	Immediately initiate the following actions: After being presented with a stop work order immediately:

1.	Cease all asbestos removal activities, or any other activities that disturbs ACM.

2.	Repair any fallen, ripped or otherwise failed work area isolation measures.

3.	Maintain in operation all work area isolation measures including those required by Sections 01526 Temporary Enclosures, 01513 Temporary Pressure Differential & Air Circulation System, 01563 Decontamination Units.

4.	Maintain all worker protections including those required by Sections 01560 Worker Protection - Asbestos Abatement, and 01562 Respiratory Protection.

5.	Fog the air in the work area with a mist of amended water to reduce airborne fiber levels.

D.	Do not recommence work until authorized in writing by the Owner or Designer.

SCHEDULE OF ASBESTOS-CONTAINING MATERIALS:

IF A SCHEDULE OF ASBESTOS-CONTAINING MATERIALS (ACM) IS USED INSTEAD OF DRAWINGS TO SHOW THE LOCATION AND TYPE OF ACM, THE SCHEDULE MUST BE COMPLETE AND ACCURATE SINCE OMISSION OF ANY ITEM, LOCATION OF ANY ITEM OR ERROR IN QUANTITY GIVES THE CONTRACTOR GROUNDS FOR A CLAIM FOR AN EXTRA.

IF A SCHEDULE OF ASBESTOS-CONTAINING MATERIALS (ACM) IS REQUIRED, INSERT A LISTING OF ALL ACM EXPECTED TO BE ENCOUNTERED AT EACH WORK LOCATION. NOTIFICATION OF THE LOCATION, AND QUANTITY OF ACM IS REQUIRED BY OSHA. INCLUDE THE TYPE AND PERCENT OF ASBESTOS-CONTENT FOR EACH SPECIFIC BUILDING MATERIAL TO BE ABATED. THE "OTHER" COMPONENTS" MAY BECOME IMPORTANT IN BUILDING CLEARANCE. THIS INFORMATION CAN HELP A LABORATORY IN ITS ANALYSIS OF AIR SAMPLES.

THE FOLLOWING IS AN EXAMPLE OF THE PRESENTATION OF INFORMATION NEEDED. REVISE AS REQUIRED TO SUIT PROJECT.

Quantities are estimations only and need to be field verified by Contractor.

Item/Location			Estimated		Asbestos				Other

Quantity		Content				Components

BOILER INSULATION

Boiler:

Surface Coat		100SqFt		95% to 100% Chrysotile		Rock Wool

Base Coat			100SqFt		60% to 65% Amosite			Refractory Binders

Boiler Breeching:

Surface Coat		100SqFt		75% to 80% Chrysotile		Gypsum plaster

Base Coat			100SqFt		45% to 50% Amosite			Refractory Binders

PIPE INSULATION:

Air Cell on domestic		115 Ft		45% to 50% Chrysotile		Cellulose

cold water piping

Plaster Fittings,			35Units		30% to 35% Chrysotile		Rockwool, Gypsum,

on cold water piping 										Plaster

Bodies, etc.

ARCHITECTURAL SURFACES

Troweled-on			1750SqFt		9% to 10% Chrysotile			Sand, Gypsum,

acoustical plaster										Plaster

in Library

FIREPROOFING

Sprayed-on			1450 SqFt		25% to 30% Chrysotile		Vermiculite, fireproofing,											Gypsum

on beams in rooms

16, 35 and 36

END OF SECTION - 01013