SECTION 01712 - CLEANING AND DECONTAMINATION PROCEDURES

PART 1 - GENERAL

1.1	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and other Division-1 Specification Sections, apply to work of this section.

1.2	DESCRIPTION OF THE WORK:

THIS SECTION CAN BE USED TO SPECIFY CLEANUP OF SMALL AREAS OF MATERIAL WHICH HAVE FALLEN FROM ARCHITECTURAL FINISHES OR THERMAL INSULATION SYSTEMS. OR IT CAN BE USED TO SPECIFY THE CLEANUP AND DECONTAMINATION OF AN AREA WHICH HAS BEEN SYSTEMATICALLY CONTAMINATED.

A.	The extent of cleaning and decontamination work is shown on the drawings.

USE THE ABOVE IF THERE ARE DRAWINGS DESCRIBING THE WORK. IF THERE ARE NO DRAWINGS PROVIDE A VERBAL DESCRIPTION OF THE WORK, SUCH AS IN THE EXAMPLE BELOW.

FOLLOWING IS AN EXAMPLE. REVISE TO SUIT PROJECT REQUIREMENTS.

B.	The work includes the removal of asbestos-containing debris that has fallen from the ceiling in Room no. 115 "Main Reading Room" in the Anthophyllite City Library, 239 Whitedust Drive, Anthophyllite, Anystate.  The work includes:

1.	Removal and disposal of visible debris.

2.	Decontamination of carpeting in the area of the debris and for 10 feet (3.05 m) beyond any visible debris.

3.	Removal, cleaning and reshelving of books within the above area.

AS AN ALTERNATIVE TO THE ABOVE, A SCHEDULE COULD BE ATTACHED AND THE FOLLOWING LANGUAGE USED.

C.	The work includes decontamination of the areas indicated in the "Schedule of Decontamination Work," found at the end of this section.

1.3	RELATED WORK SPECIFIED ELSEWHERE:

DELETE THE FOLLOWING IF THIS SECTION IS BEING USED AS PART OF A REPAIR AND MAINTENANCE SPECIFICATION. SECTION 01714 WORK AREA CLEARANCE AS WRITTEN IS APPLICABLE ONLY TO LARGE SCALE ABATEMENT PROJECTS.

A.	Work Area Clearance:  Specified in Section 01714 Work Area Clearance

PART 2 PRODUCTS (NOT APPLICABLE)

PART 3 EXECUTION

3.1	GENERAL:

A.	Complete the following before start of work of this section:

1.	01527 Regulated Areas

2.	01562 Respiratory Protection

3.	01561 Worker Protection - Repair and Maintenance

3.2	WET CLEANING:

DELETE FOLLOWING IF NO WET CLEANING IS REQUIRED. WHEREVER WET CLEANING IS REQUIRED, USE THE FOLLOWING PROCEDURES.

A.	Accomplish wet cleaning during decontamination with paper towels or disposable rags:

B.	Immerse paper towel or rag in container of amended water or dilute removal encapsulant.

IF A REMOVAL ENCAPSULANT IS USED, TEST FIRST TO INSURE THAT IT WILL NOT EITHER LEAVE A RESIDUE THAT WILL IMPEDE VISUAL INSPECTION OR BECOME GUMMY DURING CLEANING.

C.	Wring out,

D.	Fold into quarters,

E.	Wipe surface once and refold to a fresh face of cloth.  Proceed in this manner until all available faces of paper towel or rag have been used.

F.	Dispose of paper towel or rag,

G.	Do not place rag back in container to rinse out or for any other purpose.  If a used towel or rag comes in contact with water, empty container and refill.

H.	Material adhered to a surface with removal encapsulant may require the application of additional removal encapsulant to facilitate cleaning.

3.3	REMOVAL OF ASBESTOS-CONTAINING DEBRIS

FOLLOWING IS AN EXAMPLE OF A PROCEDURE USED TO CLEAN A SPACE AFTER FALLOUT OF A SMALL AMOUNT OF MATERIAL FROM A CEILING, PIPE INSULATION OR OTHER SOURCE. IF A LARGE QUANTITY OF MATERIAL IS INVOLVED, THEN THIS SECTION SHOULD BE COMBINED WITH THE FOLLOWING SECTION ON ROOM DECONTAMINATION.

A.	Work of this Section is limited to the cleanup of a small quantity of amassed debris which has fallen from an architectural finish, fire-proofing, or thermal insulation on pipes, boilers and other  equipment.

B.	Remove asbestos-containing debris and decontaminate the area involved using the following sequence:

1.	Shut down all ventilation into room.

DELETE THE FOLLOWING IF A SMALL AMOUNT OF RELATIVELY INTACT MATERIAL IS INVOLVED.

2.	Seal entry to work area with 6 mil (0.15 mm)  polyethylene.  Slit polyethylene for entry.  Install a flap to cover the slit automatically; tape slit closed after entry.

DELETE THE FOLLOWING TWO PARAGRAPHS IF THE AREA IS GOING TO BE SEALED OFF AND A DIFFERENTIAL PRESSURE SYSTEM INSTALLED.

3.	Start HEPA vacuum before entering the area.

4.	Use the HEPA vacuum to clean a path at least 6 feet (1.83 m) wide from the entry point of the work area to the site of the fallen material.

5.	Remove all small debris with the HEPA vacuum.

6.	HEPA vacuum surfaces of all pieces too large to be removed by the suction of the HEPA vacuum.

7.	Pick up such pieces and place in the bottom of a 6 mil (0.15 mm) polyethylene disposal bag conforming to the requirements of Section 02084 Disposal of Regulated Asbestos-Containing Material.  Place pieces in the bag without dropping and avoiding unnecessary disturbance and release of material.

8.	Remove all remaining visible debris with HEPA vacuum.

9.	HEPA vacuum an area 3 feet (0.91 m) beyond the location in which any visible debris was found in two directions each at right angles to the other.

10.	Place a 6 mil (0.15 mm) polyethylene drop cloth in accordance with Section 01527, Local Area Protection, immediately on top of the HEPA vacuumed area before performing any repair work on site from which fall-out occurred.

11.	HEPA vacuum the site from which material fell removing all loose material which can be removed by the vacuums suction.

12.	Repair or remove remaining material.

13.	HEPA vacuum ladder and/or any tools used and pass out of the work area.

DELETE FOLLOWING TWO PARAGRAPHS IF A VERY SMALL AMOUNT OF RELATIVELY INTACT MATERIAL IS INVOLVED. SOME STATES SET FORTH MINIMUM LEVELS OF MATERIAL CLEAN UP BELOW WHICH REOCCUPANCY AIR-MONITORING IS NOT REQUIRED. CONSULT STATE AND LOCAL REGULATIONS.

C.	HEPA vacuum all surfaces in the room starting at the top of wall and working downward to the floor. Then start at corner of floor farthest from Work Area entrance and work towards entrance.

1.	HEPA vacuum the floor using a floor attachment with rubber floor seals and adjustable floor to attachment height.  Adjust the height so that the rubber seals just touch the floor if carpeted and are within 1/16 inch (1.6 mm) of hard surface floors.  Vacuum the floor in parallel passes  with each pass overlapping the previous by one-half the width of the floor attachment. At the completion of one cleaning vacuum the floor a second time at right angles to the first.

DELETE THE FOLLOWING IF THE SEAL ON DOOR IS DELETED.

D.	Secure area from occupancy until air monitoring results per Section 01714 Project Decontamination indicate that area is safe for reoccupancy.

3.4	CLEANING AND DECONTAMINATING OBJECTS

FOLLOWING IS A PROCEDURE FOR CLEANING CONTAMINATED OBJECTS. EDIT FOR PROJECT SPECIFICS.

A.	Perform all work of decontaminating objects wherever possible on a plastic drop sheet installed in conformance with Section 01527.

B.	HEPA vacuum all surfaces of object and immediate area before moving the object.

C.	Pick-up object, if possible, and HEPA vacuum all surfaces.

D.	Hand to off-sheet worker who will wet-clean object, if possible, and place in storage location.

E.	Decontaminate area where object was located by HEPA vacuuming twice, in two perpendicular directions.  Wet clean if necessary to remove any debris.

F.	Return object to its original location.

3.5	DECONTAMINATION OF ROOMS:

FOLLOWING IS AN EXAMPLE OF PROCEDURES FOR CLEANING SPACES ADJACENT TO A WORK AREA WHICH HAVE BEEN CONTAMINATED BY FIBER MIGRATION, OR WHICH HAVE BEEN CONTAMINATED BY GROSS DEBRIS. AS WRITTEN THIS SECTION REQUIRES WORKER DECONTAMINATION BY SHOWERING. EDIT FOR PROJECT SPECIFICS.

A.	Shut down all ventilation into space.

USE THE FOLLOWING THREE PARAGRAPHS REFERRING TO SEALING THE ROOM AND INSTALLING A HEPA FILTERED FAN UNIT ONLY IF THE AIR IN THE ROOM MAY BE CONTAMINATED WITH AIRBORNE FIBERS WHICH MUST BE REMOVED AS A PART OF THE DECONTAMINATION. IN THIS CASE WORKERS SHOULD UNDERGO A WET DECONTAMINATION PROCEDURE AT THE END OF THE WORK DAY.

IF THE ROOM IS CONTAMINATED WITH VISIBLE DEBRIS (SUCH AS TRACKED MATERIAL), BUT IS NOT CONTAMINATED WITH AIRBORNE FIBERS DELETE THE NEXT THREE PARAGRAPHS. IN THIS CASE THE DRY DECONTAMINATION PROCEDURES OF SECTION 01561 SHOULD BE USED.

B.	Seal entry to Work Area with 6 mil (0.15 mm)  polyethylene.  Slit polyethylene for entry.  Install a flap to cover the slit automatically; tape slit closed after entry.

C.	Install Differential Pressure System in accordance with Section 01513.

IF IT IS NOT FEASIBLE TO EXHAUST THE HEPA FILTERED FAN UNITS FROM THE WORK AREA, DELETE THE ABOVE AND USE THE FOLLOWING PARAGRAPH.

D.	Recirculate HEPA filtered fan units in space by operating them so that discharge from machine is back into room.  Use one HEPA filtered fan unit for each 2,500 cubic feet  (70.8 cubic meters) of room volume.

E.	HEPA vacuum all surfaces in the room starting at the ceiling, then top of wall and working downward to the floor.

F.	HEPA vacuum the floor using a floor attachment with rubber floor seals and adjustable floor to attachment height.  Adjust the height so that the rubber seals just touch the floor if carpeted and are within 1/16 inch (1.6 mm) of hard surface floors.  Vacuum the floor in parallel passes with each pass overlapping the previous by one half the width of the floor attachment.  At the completion of one cleaning, vacuum the floor a second time at right angles to the first.

G.	Operate HEPA filtered fan unit in space for 96 air changes minimum.

H.	At completion of Decontamination Work workers decontaminate in accordance with Section 01561 Worker Protection - Repair and Maintenance.

I.	Secure area from occupancy until air monitoring results per Section 01714 Work Area Clearance indicate area is safe for reoccupancy.

END OF SECTION - 01712