SECTION 01527 - REGULATED AREAS

A REGULATED AREA AS DESCRIBED IN THIS SECTIONS IS INTENDED TO DEMARCATE AREAS WHERE CLASS II, AND III ASBESTOS WORK IS CONDUCTED FOR OPERATIONS AND MAINTENANCE (O&M) WORK, AND ANY ADJOINING AREA WHERE DEBRIS AND WASTE FROM SUCH ASBESTOS WORK ACCUMULATE. A REGULATED AREA AS DESCRIBED IN THIS SECTION WILL ONLY BE USED FOR WORK PRACTICES WHERE A NEGATIVE EXPOSURE ASSESSMENT HAS BEEN MADE. REFER TO THE NIBS PUBLICATION GUIDANCE MANUAL - ASBESTOS OPERATIONS & MAINTENANCE WORK PRACTICES, FOR FURTHER GUIDANCE ON THIS TOPIC.

THIS SECTION IS NOT INTENDED FOR USE WITH SECTION 02085 RESILIENT FLOORING REMOVAL - RESILIENT FLOOR COVERING MANUFACTURERS RECOMMENDED WORK PRACTICES. SECTION O2O85 IS SELF CONTAINED. THIS SECTION CONTAINS REQUIREMENTS THAT MAY BE IN CONFLICT WITH O2O85

PART 1 - GENERAL

1.1	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and other Division-1 Specification Sections, apply to work of this section.

1.2	RELATED WORK SPECIFIED ELSEWHERE:

SELECT EITHER THE REFERENCE ABOVE OR BELOW AND DELETE THE OTHER.

A.	Worker Protection:  is specified in Section 01561 Worker Protection - Repair and Maintenance.

B.	Respiratory Protection:  is specified in Section 01562 Respiratory Protection

INCLUDE THE FOLLOWING IF A REMOTE SHOWER IS REQUIRED BY THE WORK. 01563 WILL REQUIRE SUBSTANTIAL REVISION TO BE APPROPRIATE FOR USE WITH THIS SECTION. REFER TO THE NIBS PUBLICATION GUIDANCE MANUAL - ASBESTOS OPERATIONS & MAINTENANCE WORK PRACTICES, FOR FURTHER GUIDANCE ON THIS TOPIC.

C.	Wet Decontamination Facilities: are described in Section 01563 Decontamination Units.

1.3	DESCRIPTION OF WORK:

PROCEDURES SET OUT IN THIS AND ACCOMPANYING SECTIONS, 01528, 01561, 01712, 02083 AND 15254 SHOULD BE USED TO SPECIFY PROCEDURES NEEDED TO SUPPORT REPAIR OR MAINTENANCE OF EXISTING BUILDING COMPONENTS. UNDER NO CIRCUMSTANCES SHOULD THESE SECTIONS BE USED TO SPECIFY DEDICATED PURPOSE REMOVAL OF ASBESTOS-CONTAINING MATERIALS.

SECTION 01529 MINI -ENCLOSURES AND GLOVEBAGS DESCRIBES THE REGULATED AREA REQUIRED FOR WORK FOR WHICH THERE IS NO NEGATIVE EXPOSURE ASSESSMENT OR THAT INVOLVES DRILLING, CUTTING, ABRADING, SANDING, CHIPPING, BREAKING, OR SAWING OF THERMAL SYSTEM INSULATION OR SURFACING MATERIAL .

A.	Work of this section consists of preparing a Regulated Area for work of the following specification sections only.  Do not use procedures set forth in this section in connection with any other work.

1.	Section 01046 Cutting & Patching Asbestos Containing Materials

2.	Section 01528 Entry Into Controlled Areas

3.	Section 01529  Mini Enclosures and Glovebags

4.	Section 01712 Cleaning and Decontamination Procedures

5.	Section 02083 Disturbance of ACM During O&M Work

INCLUDE THE FOLLOWING REFERENCE TO SECTION 09251 ONLY IF THIS SECTION IS EDITED TO ALLOW ONLY OPERATIONS THAT DO NOT DIRECTLY DISTURB ACM.

6.	Section 09251 Gypsum Drywall - Asbestos Enclosures

7.	Section 15254 Repair of Insulation and Lagging

1.4	SUBMITTALS

A.	Before the Start of Work:  Submit the following to the Designer for review.  Begin no work until these submittals are returned with Designer's action stamp indicating that the submittal is returned for unrestricted use or final-but-restricted use.

1.	HEPA Filtered Vacuum Cleaners:  Submit product data.

2.	Signs:  Submit samples of each type of sign to be used.

3.	Warning Tape:  Submit samples.

PART 2 - EQUIPMENT

2.1	PRODUCTS

A.	HEPA Filter Vacuum Cleaners:

1.	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products which may be incorporated in the Work include, but are not limited to, the following:

RETAIN ABOVE FOR NONPROPRIETARY OR BELOW FOR SEMI-PROPRIETARY SPECIFICATION. REFER TO DIVISION-1 SECTION "PRODUCTS AND SUBSTITUTIONS." ABOVE IS THE CURRENT LANGUAGE REPLACING FORMER "OR EQUAL" CLAUSES.

2.	Manufacturer:  Subject to compliance with requirements, provide products of one of the Following:

THE FOLLOWING IS A LIST OF FIRMS BELIEVED TO MANUFACTURE THIS PRODUCT. NO MANUFACTURERS HAVE BEEN KNOWINGLY EXCLUDED AND NO ATTEMPT HAS BEEN MADE TO EVALUATE THESE PRODUCTS. ADDITIONAL SUPPLIERS MAY EXIST. PRODUCT LITERATURE SHOULD BE USED TO EVALUATE THESE PRODUCTS AND TO VERIFY THAT LISTED PRODUCTS COMPLY WITH THE SPECIFICATIONS AND MEET PROJECT REQUIREMENTS. VERIFY THAT PRODUCTS INDICATED ARE STILL BEING MANUFACTURED. EDIT OR ADD TO THE LIST AS APPROPRIATE TO THE PROJECT REQUIREMENTS. THIS LIST IS BEING REVISED.

Nilfisk of America, Inc.			HEPA filtered

225 Great Valley Parkway		Vacuums

Malvern, PA  19355

(800) 645-3475

Minuteman International			Minuteman

111 South Route 53			HEPA Vacuums

Addison, IL  60101

(708) 627-6900

Pullman-Holt (White) Corp.		HEPA Filtered

PO Box 16647				Vacuums

Tampa, FL  33617

(813) 645-3475

B.	Plastic Sheet:

1.	Plastic Sheet: A single polyethylene film in the largest sheet size possible to minimize seams,  6.0  mil  (0.15 mm) thick , clear, frosted, or black as indicated.

PART 3 - EXECUTION

3.1	SECURING WORK AREA:

A.	Secure work area from access by occupants, staff or users of the building.  Accomplish this where possible, by locking doors, windows, or other means of access to the area, by scheduling work for periods of time that the building in unoccupied, or by constructing temporary wood stud and plywood barriers.

3.2	DEMARCATION OF REGULATED AREA:

THIS ARTICLE DOES NOT APPLY TO THE REMOVAL OF RESILIENT FLOORING MATERIALS. REFER TO SECTION 02085 RESILIENT FLOORING REMOVAL - RESILIENT FLOOR COVERING MANUFACTURERS RECOMMENDED WORK PRACTICES. SECTION O2O85 IS SELF CONTAINED.

A.	Demarcation.  Demarcate the Regulated Area with a sheet plastic drop cloth, signs and barrier tape.  Configure the regulated area in a manner that minimizes the number of persons within the area and protects persons outside the area from exposure to airborne concentrations of asbestos.

1.	Drop Cloth:  Cover floor in vicinity of Work Area and six (6) feet (1.82 meters) beyond, with 6 mil  (0.15 mm) polyethylene drop sheet.  Where work is adjacent to wall, extend drop sheet up wall and secure at ceiling with duct tape.  This drop sheet demarcates the boundary of the Regulated Area.

REVISE BELOW AS REQUIRED BY LOCAL REQUIREMENTS

2.	Signs:  Post warning signs that carry the following legends in both English and Spanish:

a.	First Sign: Provide warning signs at each locked door leading to the controlled area reading as follows:

Legend				Notation

KEEP OUT				3 inch (76.2 mm )Block

b.	Second Sign: Immediately inside the locked door and outside the controlled area post an approximately 20 inch by 14 inch (508 mm x 356 mm)  manufactured caution sign displaying the following legend with letter sizes and styles of a visibility required by 29 CFR 1926:

THE FOLLOWING IS THE STANDARD COMMERCIALLY AVAILABLE ASBESTOS WARNING SIGN. OSHA REQUIRES WARNING SIGNS TO BE COMPREHENSIBLE TO NON-ENGLISH SPEAKING WORKERS. RESPIRATORS ARE REQUIRED FOR WORK THAT DISTURBS THERMAL SYSTEM INSULATION OR SURFACING MATERIAL EVEN IF THERE IS A NEGATIVE EXPOSURE ASSESSMENT.

Legend:

DANGER

ASBESTOS

CANCER AND LUNG DISEASE HAZARD

AUTHORIZED PERSONNEL ONLY

RESPIRATORS AND PROTECTIVE CLOTHING

ARE REQUIRED IN THIS AREA

EDIT BELOW BASED UPON SPECIFIC WIDTH AND TEXT AVAILABLE.

3.	Barrier Tape:  Where the controlled area is in a large area such as on part of a boiler room or open office area, delineate area with 3 inch (76.2 mm) wide polyethylene ribbon with the printed warning, "CAUTION ASBESTOS REMOVAL". Install this ribbon at between 3 and 4 feet ( 0.91 and 1.22 meters ) above the floor.

3.3	SCHEDULING:

A.	Work may be carried out during normal working hours in those areas which can be completely secured by lockable doors from access by building occupants and staff, and which have HVAC equipment that can be shut down and locked off.  Otherwise, work is to be carried out after building occupants and cleaning staff have left.

3.4	GENERAL PROCEDURES:

THIS ARTICLE DOES NOT APPLY TO THE REMOVAL OF RESILIENT FLOORING MATERIALS. REFER TO SECTION 02085 RESILIENT FLOORING REMOVAL - RESILIENT FLOOR COVERING MANUFACTURERS RECOMMENDED WORK PRACTICES. SECTION O2O85 IS SELF CONTAINED.

A.	The following precautions and procedures have application to work of this section.  Workers must exercise caution to avoid release of asbestos fibers into the air:

1.	Setup and management of the controlled area is to be under the supervision of a OSHA Competent Person as described in Section 01043 Project Coordination - Asbestos Abatement

.

2.	Before start of work comply with requirement for worker protection in section 01561, and respiratory protection in section 01562.

3.	Do not allow eating, drinking, smoking, chewing tobacco or gum, or applying cosmetics in the Regulated Area.

4.	Shut down any air handling equipment bringing air into or out of the Regulated Area.

5.	Clean any existing dust or debris from the floor and walls, and other surface in the immediate location of the work prior to commencing work by damp-mopping or by use of a High Efficiency Particulate Air (HEPA) filtered vacuum.

6.	Cover floor in vicinity of Work Area and six (6) feet (1.82 meters) beyond, with 6 mil  (0.15 mm) polyethylene drop sheet.  Where work is adjacent to wall, extend drop sheet up wall and secure at ceiling with duct tape.  This drop sheet demarcates the boundary of the Regulated Area.

7.	Seal all openings, supply and exhaust vents, and convectors within ten (10) feet (3.05 meters ) of the Work Area with 6 mil  (0.15 mm) polyethylene sheeting secured and completely sealed with duct tape.

8.	Perform the work per the appropriate specification section while on plastic drop sheet.

9.	Immediately remove any asbestos-containing debris which collects on the drop sheet either by using a HEPA vacuum or by spraying with amended water or removal encapsulant, collecting with wet paper towels, placing in a disposal bag while still wet, and cleaning surface of plastic sheet with wet paper towels.

10.	Complete the following at completion of work in an area before stepping off drop sheet

a.	While standing on plastic sheet thoroughly HEPA vacuum ladder and any tools used and pass to worker standing off sheet.

b.	Worker standing off the sheet HEPA vacuum thoroughly the worker standing on the sheet.

c.	Worker on the sheet thoroughly HEPA vacuum all surfaces of the plastic sheet, bags, and any other items on the sheet including  the workers feet.

11.	If moving to the next Work Area in the same secured area:  Worker on the drop sheet is to don clean foot covers, placing each foot, in turn, off the sheet as the foot cover is put on.  Remove clean foot covers at the next Work Area while standing on the sheet.  Dispose of the used foot covers along with the plastic sheet at completion of work in that area.  Do not reuse foot covers to move off the sheet.

12.	If work day is complete or if next Work Area is in another secured area:  all workers remove paper suits turning them inside out while doing so.  The person on the sheet steps with each foot off the sheet as the foot covers are removed.

13.	Fold sheet and all its contents toward the center.

14.	Place the sheet in a properly labeled disposal bag.

15.	Neck down the bag and collapse it with the HEPA vacuum.

16.	Twist the bag shut, bend over and seal with duct tape by wrapping around bag neck at least 3 times.

17.	Clean all surfaces of the Work Area by use of a HEPA filter vacuum until no visible residue remains.

USE FOLLOWING TWO PARAGRAPHS IF WORK INVOLVED WILL NOT RESULT IN CONTAMINATION OF WORKERS CLOTHES OR AIRBORNE FIBER CONCENTRATIONS ABOVE BUILDING BACKGROUND LEVELS. IF A WORKER'S CLOTHING BECOMES CONTAMINATED OR AIRBORNE ASBESTOS CONCENTRATIONS ABOVE BUILDING BACKGROUND ARE EXPERIENCED DELETE THE FOLLOWING TWO PARAGRAPHS AND USE THE PARAGRAPH REQUIRING A WET DECONTAMINATION.

B.	At completion of work require all workers to complete decontamination procedures in accordance with Section 01561 Worker Protection - Repair & Maintenance.

C.	Remove respirators using the procedure in Section 01561 Worker Protection - Repair & Maintenance.

IF OPERATION MAY RESULT IN CONTAMINATION OF WORKER CLOTHING OR AIRBORNE ASBESTOS CONCENTRATIONS ABOVE BUILDING BACKGROUND RETAIN THE PARAGRAPH BELOW, REQUIRING A WET DECONTAMINATION, AND DELETE THE TWO ABOVE.

D.	At completion of work require all workers to complete wet decontamination procedures in accordance with Section 01560 Worker Protection - Asbestos-Abatement.

END OF SECTION - 01527

This Page Intentionally Blank