SECTION 15254 - REPAIR OF INSULATION AND LAGGING

PART 1 - GENERAL

1.1	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and Division-1 Specification Sections apply to work of this Section.

1.2	DESCRIPTION OF WORK:

A.	Repair of insulation on all piping upon which asbestos-containing insulation is to remain.

B.	Repair of lagging on boilers, breeching and equipment upon which asbestos-containing lagging and/or insulation is to remain.

C.	Extent of pipe insulation and lagging to be repaired is shown on the drawings.

D.	Labeling of repaired Asbestos-Containing Materials (ACM).

1.3	SUBMITTALS

A.	Before the Start of Work:  Submit the following to the Designer for review.  Do not begin work until these submittals are returned with Designer's action stamp indicating that the submittal is returned for unrestricted use or final-but-restricted use.

1.	Mineral Wool Insulating Cement:  Provide product data.

2.	Waterproof Cement:  Provide product data.

3.	Nonwoven Fibrous Glass Mat:  Provide product data.

4.	Open Weave Glass Fiber Mat:  Provide product data.

5.	Plastic Jackets:  Provide product data.

6.	Labels:  Submit samples.

PART 2 - PRODUCTS

2.1	MATERIALS

A.	Mineral Wool Insulating Cement:  Provide job-mixed insulating plaster manufactured for use on plumbing equipment.

B.	Waterproof Cement:  Provide premixed or job mixed cement manufactured for coating of thermal insulation lagging.

C.	Nonwoven Fibrous Glass Mat:  Provide felt approximately 3/32 inch (2.4 mm)  thick fabricated from glass fibers.

D.	Open Weave Glass Fiber Mat:  Provide cloth with approximately 1/4 inch (6 mm) openings in weave, fabricated from glass fibers twisted or braided into strands approximately 1/128 inch (0.198 mm) in diameter.

REVISE BELOW IF SECTION 09805 IS NOT GOING TO BE INCLUDED IN THE SPECIFICATION.

E.	Bridging Type Encapsulant:  as specified in section 09805.

F.	Plastic Jackets:

1.	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products which may be incorporated in the work include, but are not limited to, the following:

RETAIN ABOVE FOR NON-PROPRIETARY OR BELOW FOR SEMI-PROPRIETARY SPECIFICATION. REFER TO SECTION 01632 PRODUCT SUBSTITUTIONS - ASBESTOS ABATEMENT.

2.	Manufacturer:  Subject to compliance with requirements, provide products of one of the Following:

THE FOLLOWING IS A LIST OF FIRMS BELIEVED TO MANUFACTURE THIS PRODUCT. NO MANUFACTURERS HAVE BEEN EXCLUDED AND NO ATTEMPT HAS BEEN MADE TO EVALUATE THESE PRODUCTS. ADDITIONAL SUPPLIERS MAY EXIST. PRODUCT LITERATURE SHOULD BE USE TO EVALUATE THESE PRODUCTS AND TO VERIFY THAT LISTED PRODUCTS COMPLY WITH THE SPECIFICATIONS AND MEET PROJECT REQUIREMENTS. VERIFY THAT PRODUCTS INDICATED ARE STILL BEING MANUFACTURED. EDIT OR ADD TO THE LIST AS APPROPRIATE TO THE PROJECT REQUIREMENTS

a.	H. B. Fuller Company		Speedline 25/50

6107 Industrial Way		Smoke-Safe PVC

Houston, Texas  77011

(800)231-9541

PART 3 - EXECUTION

3.1	GENERAL:

A.	Before starting work of this section complete the following:

1.	Section 01513 - Temporary Pressure Differential & Air Circulation System

2.	Section 01563 - Decontamination Units

3.	Section 01526 - Temporary Enclosures

4.	Section 01560 - Worker Protection - Asbestos Abatement

5.	Section 01562 - Respiratory Protection

SELECT EITHER ABOVE OR BELOW. SELECT ABOVE FOR CLASS I AND II ASBESTOS WORK. SELECT BELOW FOR CLASS III AND CLASS IV ASBESTOS WORK.

6.	Section 01527 - Regulated Areas

ADD THE SECTIONS BELOW FOR CLASS III ASBESTOS WORK

7.	Section 01529 -Mini Enclosures and Glovebags

8.	Section 01561 - Worker Protection - Repair & Maintenance

9.	Section 01562 - Respiratory Protection

CHOOSE ONE OF THE TWO REPAIR METHODS BELOW

B.	Piping: Remove any loose material with HEPA vacuum.  No existing jacket material is to be removed.

C.	Reinforced Bridging Encapsulant:  Repair with reinforced bridging encapsulant:

1.	Fill holes with mineral wool insulating cement and cover damaged areas with nonwoven fibrous glass mat completely saturated with bridging type encapsulant.

2.	Wrap open joints with nonwoven fibrous glass mat embedded in bridging type encapsulant.

3.	Smooth mat to a wrinkle free condition.  Allow to dry and coat entire surface of mat with an additional coat of bridging type encapsulant and brush to a smooth uniform appearance.

BRIDGING TYPE ENCAPSULANT INSTALLED AS ABOVE PROVIDES A DURABLE FLEXIBLE COVERING THAT BONDS WELL TO BOTH METAL SURFACES AND INSULATING MATERIALS. NORMAL PIPE WRAPPING MATERIALS SUCH AS CANVAS AND WATERPROOF CEMENT DO NOT BOND WELL TO METAL SURFACES AND FREQUENTLY CRACK DUE TO EXPANSION AND CONTRACTION OF PIPING.

D.	Plastic Jackets:  Repair by covering with plastic jackets.

1.	Install in strict accordance with manufacturers instructions

E.	Fittings:  Remove any loose material with HEPA vacuum.  No existing jacket material is to be removed.

CHOOSE ONE OF THE TWO REPAIR METHODS BELOW

F.	Reinforced Bridging Encapsulant:  Repair with reinforced bridging encapsulant:

1.	Patch damaged fittings as required, using mineral wool insulating cement.  Smooth insulation to a uniform appearance, continuous with and not overlapping adjacent straight insulation runs.

2.	Cover entire surface of fitting with nonwoven fibrous glass mat embedded in bridging type encapsulant. Stretch to conform to shape of fitting and smooth to a uniform appearance without wrinkles.

3.	Overlap jackets of adjacent straight insulation sections by 3 inches (75 mm).

4.	Allow to dry and coat entire surface of mat with bridging type encapsulant and brush to a smooth finished appearance.

G.	Plastic Jackets:  Repair by covering with plastic jackets.

1.	Install in strict accordance with manufacturers instructions.

2.	Fill holes and gaps in insulation with fibrous glass insulation prior to installing jacket.

H.	Equipment Lagging: (hot water tanks, converters, etc.)  Fill damaged portion of lagging as required with mineral wool insulating cement and cover with nonwoven fibrous glass mat completely embedded in bridging type encapsulant.  Coat area of repair and six inches on all sides with bridging type encapsulant, brush out to a uniform appearance.  Completely coat lagging which do not possess a canvas jacket with two coats of bridging type encapsulant.

I.	Boiler and Smoke Hoods Breeching Lagging: Fill damaged portions of lagging, as required, with mineral wool insulating cement.   Coat entire surface of lagging with 1/4" (6 mm) minimum thickness of mineral wool insulating cement reinforced with open weave glass fiber mat.  Trowel surface smooth finish.

REFER TO 29 CFR 1926 OR SUBSEQUENT REVISIONS OR PROGRAM DIRECTIVES FOR INFORMATION ON OSHA REQUIREMENTS FOR LABELING.

J.	Labeling:  Label all asbestos-containing piping insulation, fitting insulation lagging, etc. in unoccupied areas with a 3 inch x 5 inch (75 mm x 125 mm) stickers containing the words

FOLLOWING IS THE LABEL REQUIRED BY OSHA

1.	DANGER

CONTAINS ASBESTOS FIBERS

AVOID BREATHING DUST

CANCER AND LUNG DISEASE HAZARD

AVOID BREATHING ASBESTOS

FOLLOWING IS THE LABEL REQUIRED BY THE AHERA REGULATION IN ROUTINE MAINTENANCE AREAS.

2.	CAUTION

ASBESTOS HAZARD

DO NOT DISTURB WITHOUT PROPER TRAINING AND EQUIPMENT

K.	Alternate labels.  Apply labels minimum 2 per side or maximum of five feet (5') (1500 mm) apart on boilers, breeching and equipment and a minimum of one per section and a maximum of eight feet (8') (2400 mm) apart on pipe runs.  Apply labels to both sides of pipe runs which are accessible from both sides.

1.	In occupied areas, provide labels shaped like stop signs approximately 3 inches (75 mm) across with text reading:

FOLLOWING LABEL DOES NOT MEET REQUIREMENTS OF AHERA AND OSHA REGULATIONS AND SHOULD NOT BE USED IN LOCATIONS WHERE THESE REGULATIONS REQUIRE A LABEL. THIS LABEL IS INAPPROPRIATE FOR USE IN MECHANICAL EQUIPMENT AND BOILER ROOMS.

a.	STOP

Before Doing Work In This Area

See Custodian

END OF SECTION  - 15254