SECTION 01504 - CONSTRUCTION FACILITIES AND TEMPORARY CONTROLS - LEAD-BASED PAINT

PART

1 - GENERAL

1.1		RELATED DOCUMENTS:

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division-1 Specification sections, apply to work of this section.

1.2		DESCRIPTION OF REQUIREMENTS:

A.	General:  Provide temporary connection to existing building utilities or provide temporary facilities as required herein or as necessary to carry out the work.

1.3	SUBMITTALS

A.	Before the Start of Work:  Submit the following to the Designer for review.  Begin no work until these submittals are returned with Designer's action stamp indicating that the submittal is returned for unrestricted use or final-but-restricted use.

B.	Scaffolding:  submit list of rolling and fixed scaffolding intended for use on the project.  Submit sufficient detail to indicate compliance with applicable worker safety regulations or other requirements.

C.	Hot water heater:  Submit manufacturers name, model number, size in gallons, heating capacity, power requirements.

D.	Decontamination Unit Sub-panel:  Submit product data.

E.	Ground Fault Circuit Interrupters (GFCI):  Submit product data.

F.	Lamps and Light Fixtures:  Submit product data.

G.	Temporary Heating Units:  Provide product data.

H.	Temporary Cooling Units:  Provide product data and installation instructions.

I.	Self Contained Toilet Units:  Provide product data and name of sub-contractor used for servicing self contained toilets.  Submit method to be used for servicing.

J.	First Aid Supplies:  Provide list of contents of first aid kit.  Submit in form of check list.

K.	Fire Extinguishers:  Provide product data.  Submit schedule indicating location at job site.

PART 2 - PRODUCTS

2.1		MATERIALS AND EQUIPMENT:

A.	General:  Provide new or used materials and equipment that are undamaged and in serviceable condition.  Provide only materials and equipment that are recognized as being suitable for the intended use, by compliance with appropriate standards.

2.2		SCAFFOLDING:

A.	Provide all scaffolding, ladders and/or staging, etc. as necessary to accomplish the work of this contract.  Scaffolding may be of suspension type; or standing type such as metal tube and coupler, tubular welded frame, pole or outrigger type or cantilever type.  The type, erection and use of all scaffolding shall comply with all applicable OSHA provisions.

B.	Equip rungs of all metal ladders, etc. with an abrasive non-slip surface.

C.	Provide a nonskid surface on all scaffold surfaces subject to foot traffic.

2.3		WATER SERVICE:

A.	Temporary Water Service Connection:  All connections to the Owner's water system shall include backflow protection.  Valves shall be temperature and pressure rated for operation of the temperatures and pressures encountered.  After completion of use, connections and fittings shall be removed without damage or alteration to existing water piping and equipment.  Leaking or dripping valves shall be piped to the nearest drain or located over an existing sink or grade where water will not damage existing finishes or equipment.

B.	Water Hoses:  Employ heavy-duty abrasion-resistant hoses with a pressure rating greater than the maximum pressure of the water distribution system to provide water into each work area and to each Decontamination Unit.  Provide fittings as required to allow for connection to existing wall hydrants or spouts, as well as temporary water heating equipment, branch piping, showers, shut-off nozzles and equipment.

C.	Water Heater:  Provide UL rated 40 gallon electric water heater to supply hot water for the Decontamination Unit shower.  Activate from 30 amp circuit breaker located within the Decontamination Unit subpanel.  Provide with relief valve compatible with water heater operation; pipe relief valve down to drip pan on floor with type L copper.  Drip pans shall consist of a 12" X 12" X 6" (30 cm x 30 cm x 15 cm) deep pan, made of 19 gauge galvanized steel, with handles.  A 3-quart (3 L) kitchen saucepan may be substituted for this purpose.  Drip pan shall be securely fastened to the water heater with bailing wire or similar material.  Wiring of the water heater shall be in compliance with NEMA, NECA, and UL standards.

DELETE FOLLOWING WHEN BUILDING HOT WATER SYSTEM WILL BE SHUT DOWN OR OTHERWISE UNAVAILABLE FOR USE.

D.	Hot Water: may be secured from the building hot water system, provided backflow protection is installed at point of connection as described in this section under Temporary Water Service connection, and if authorized in writing by the Designer.

2.4		ELECTRICAL SERVICE:

A.	General:  Comply with applicable NEMA, NECA and UL standards and governing regulations for materials and layout of temporary electric service.  Provide equipment which is compatible with existing electrical characteristics and available power.  If existing power is either incompatible or inadequate for performance of the Work, provide auxiliary generators(s) located outside of the building.

B.	Temporary Power:  Provide service to Decontamination Unit subpanel with minimum 60 amp, 2 pole circuit breaker or fused disconnect connected to the buildings main distribution panel.  Subpanel and disconnect shall be sized and equipped to accommodate all electrical equipment required for completion of the work.

C.	Voltage Differences:  Provide identification warning signs at power outlets which are other than 110-120 volt power.  Provide polarized outlets for plug-in type outlets, to prevent insertion of 110-120 volt plugs into higher voltage outlets.  Dry type transformers shall be provided where required to provide voltages necessary for work operations.

D.	Ground Fault Protection:  Equip all circuits for any purpose entering Work Area with ground fault circuit interrupters (GFCI).  Locate GFCI's exterior to Work Area so that all circuits are protected prior to entry to Work Area.  Provide circuit breaker type ground fault circuit interrupters (GFCI) equipped with test button and reset switch for all circuits to be used for any purpose in work area, decontamination units, exterior, or as otherwise required by national electrical code, OSHA or other authority.  Locate in panel exterior to Work Area.

2.5		ELECTRICAL EQUIPMENT:

A.	Electrical Power Cords:  Use only grounded extension cords; use "hard-service" cords where exposed to abrasion and traffic.  Use single lengths or use waterproof connectors to connect separate lengths of electric cords, if single lengths will not reach areas of work.

B.	Lamps and Light Fixtures:  Provide sealed quartz halogen construction lights, general service incandescent lamps or fluorescent lamps of wattage indicated or required for adequate illumination as required by the work or this section.  Protect lamps with guard cages where fixtures are exposed to breakage by construction operations.  Provide lighting with a secure base to insure that they will not be knocked over.  Keep lights away from combustible materials.

2.6		TEMPORARY HEAT:

A.	Heating Units:  Provide temporary heating units that have been tested and labeled by UL, FM or another recognized trade association related to the fuel being consumed.  Use steam or hot water radiant heat where available, and where not available use electric resistant fin radiation supplied from a branch circuit with ground fault circuit interrupter.

2.7		TEMPORARY COOLING:

A.	Cooling Units:  Provide temporary cooling units consisting of a fan coil unit inside the work area with a compressor and heat rejection coil outside.

2.8		SELF-CONTAINED TOILETS:

A.	Self-Contained Toilet Units:  Provide single-occupant self-contained toilet units of the chemical type, properly vented and fully enclosed with a glass fiber reinforced polyester shell or similar non-absorbent material.

2.9		FIRST AID:

A.	First Aid Supplies:  Comply with governing regulations and recognized recommendations within the construction industry.

2.10	FIRE EXTINGUISHERS:

A.	Fire Extinguishers:  Provide Type "A" fire extinguishers for temporary offices and similar spaces where there is minimal danger of electrical or grease-oil-flammable liquid fires.  In other locations provide type "ABC" dry chemical extinguishers, or a combination of several extinguishers of NFPA recommended types for the exposures in each case.

PART 3 - EXECUTION

3.1		SCAFFOLDING:

A.	Require that a Competent Person supervise the erection, movement, and dismantling of scaffolding in accordance with OSHA 29 CFR 1926.451.

B.	During the erection and/or moving of scaffolding, care must be exercised so that the polyethylene floor covering is not damaged.

C.	Clean as necessary debris from non slip surfaces.

D.	At the completion of abatement work clean all construction aids within the work area, wrap in one layer of 6 mil polyethylene sheet and seal before removal from the work area.

3.2		INSTALLATION, GENERAL:

A.	General:  Use qualified tradesmen for installation of temporary services and facilities.  Locate temporary services and facilities where they will serve the entire project adequately and result in minimum interference with the performance of the Work.

1.	Require that tradesmen accomplishing this work be licensed as required by local authority for the work performed.

B.	Relocate, modify and extend services and facilities as required during the course of work so as to accommodate the entire work of the project.

3.3		WATER SERVICE:

A.	General:  Water connection (without charge) to Owner's existing potable water system is limited to one 3/4" pipe-size connection, and a maximum flow of 10 gpm each to hot and cold water supply.  Install using vacuum breakers or other backflow preventer as required by local authority.

B.	Maintain hose connections and outlet valves in leak-proof condition.  Where finish work below an outlet might be damaged by spillage or leakage, provide a drip pan of suitable size to minimize the possibility of water damage.  Drain water promptly from pans as it accumulates.

3.4		TEMPORARY POWER - REGULATED AREAS:

A.	General:  Use existing power available in Work Area.

B.	Circuit Protection:  Protect each tool or extension cord with a ground fault circuit interrupter (GFCI) of proper size.  GFCI can be type that plugs into existing duplex outlets.  Insure that outlet is properly grounded before installation of GFCI.

3.5		ELECTRICAL SERVICE:

A.	General:  Provide a weatherproof, grounded temporary electric power service and distribution system of sufficient size, capacity, and power characteristics to accommodate performance of work during the construction period.  Install temporary lighting adequate to provide sufficient illumination for safe work and traffic conditions in every area of work.

B.	Lockout:  Lockout all existing power to or through the work area as described below.  Unless specifically noted otherwise existing power and lighting circuits to the work area are not to be used.  All power and lighting to the Work Area is to be provided from temporary electrical panel described below.

1.	Lockout power to work area by switching off all breakers serving power or lighting circuits in work area.  Label breakers with tape over breaker with notation "DANGER circuit being worked on".  Lock panel and have all keys under control of contractor's superintendent or owner's designated representative.

2.	Lockout power to circuits running through work area wherever possible by switching off all breakers serving these circuits.  Label breakers with tape over breaker with notation "DANGER circuit being worked on".  Sign and date danger tag.  Lock panel and supply keys to contractor, Owner and Designer.  If circuits cannot be shut down for any reason, label at 4'-0" on center with tags reading, "DANGER live electric circuit.  Electrocution hazard."

C.	Temporary Electrical Panel:  Provide temporary electrical panel sized and equipped to accommodate all electrical equipment and lighting required by the work.  Connect temporary panel to existing building electrical.  Protect with circuit breaker or fused disconnect.  Locate temporary panel as directed by Owner or Designer.  Power may be obtained from adjacent apartments if authorized in writing by the Owner.

D.	Power Distribution System:  Provide circuits of adequate size and proper characteristics for each use.  In general run wiring overhead, and rise vertically where wiring will be least exposed to damage from construction operations.

E.	Circuit Protection:  Protect each circuit with a ground fault circuit interrupter (GFCI) of proper size located in the temporary panel.  Do not use outlet type GFCI devices.

F.	Temporary Wiring: in the work area shall be type UF non-metallic sheathed cable located overhead and exposed for surveillance.  Do not wire temporary lighting with plain, exposed (insulated) electrical conductors.  Provide liquid tight enclosures or boxes for wiring devices.

G.	Number of Branch Circuits:  Provide sufficient branch circuits as required by the work.  All branch circuits are to originate at temporary electrical panel.  At minimum provide the following:

1.	For power tools and task lighting, provide one temporary 4-gang outlet in the following locations.  Provide a separate 110-120 Volt, 20 Amp circuit for each 4-gang outlet (4 outlets per circuit).

a.	One outlet in the work area for each 2500 square feet of work area

b.	One outlet at each decontamination unit, located in equipment room

2.	110-120 volt 20 amp branch circuits with 4-gang outlet for Owner's exclusive use while conducting air sampling during the work as follows:

a.	One in each work area

b.	One at clean side of each Decontamination Unit.

3.6		TEMPORARY LIGHTING - REGULATED AREAS:

A.	General:  Provide sufficient temporary lighting to ensure proper workmanship everywhere; by combined use of daylight, general lighting, and portable plug-in task lighting.

B.	Circuit Protection:  Protect each light with a ground fault circuit interrupter (GFCI) of proper size.  GFCI can be type that plugs into existing duplex outlets.  Insure that outlet is properly grounded before installation of GFCI.

3.7		TEMPORARY LIGHTING - CONTAINMENT:

A.	Lockout:  Lockout all existing power to lighting circuits in work area.  Unless specifically noted otherwise existing lighting circuits to the work area are not to be used.  All lighting to the Work Area is to be provided from temporary electrical panel described above.

B.	Lighting levels:  Provide the following or equivalent where natural lighting or existing building lighting does not meet the required light level:

1.	One 200-watt incandescent lamp per 1000 square feet of floor area, uniformly distributed, for general construction lighting, or equivalent illumination of a similar nature.  In corridors and similar traffic areas provide one 100-watt incandescent lamp every 50 feet.  In stair ways and at ladder runs, provide one lamp minimum per story, located to illuminate each landing and flight.  Provide sufficient temporary lighting to ensure proper workmanship everywhere; by combined use of daylight, general lighting, and portable plug-in task lighting.

2.	Provide lighting in areas where work is being performed as required to supply a 100 foot candle minimum light level.

3.	Provide lighting in any area being subjected to a visual inspection as required to supply a 100 foot candle minimum light level.

4.	Provide lighting in the Decontamination Unit as required to supply a 50 foot candle minimum light level.

C.	Number of Lighting Circuits:  Provide sufficient lighting circuits as required by the work.  All lighting circuits are to originate at temporary electrical panel.

D.	Circuit Protection:  Protect each circuit with a ground fault circuit interrupter (GFCI) of proper size located in the temporary panel.

3.8		TEMPORARY HEAT:

A.	General:  Provide temporary heat where indicated or needed for performance of the Work.

B.	Temperature:  Maintain a minimum temperature of 70 degrees F. where finished work has been installed.

C.	Temperature in shower:  Maintain a minimum temperature of 75 degrees F.in the shower of the decontamination unit.

D.	Temperature:  Maintain a minimum temperature of 70 degrees F. in the Work Area at all times that work is going on.  At all other times and at completion of removal work, but before start of reconstruction work, maintain a minimum temperature of 50 degrees F.

E.	Temperature:  Maintain a minimum temperature of 50 degrees F. in the Work Area at all times during and after removal work.

3.9		TEMPORARY COOLING:

A.	Required Cooling:  Provide units sufficient to supply 20,000 BTU's of cooling per 8,000 cubic feet of work area.

3.10	PROJECT MONITOR'S FIELD OFFICE:

A.	Project Monitor's Field Office:  Provide air conditioned, heated office space near the Work Area for professional person, suitably finished, furnished, equipped, locked, heated, naturally ventilated, lighted and wired with electrical power, not less than 250 sq. ft. floor area.  Equip office with 1 telephone line and 1 telephone, and not less than 2 duplex convenience power outlets.  In addition to 1 desk, 1 four drawer file cabinet and 3 chairs, furnish office with one 36" X 96" plan table, and one 24" X 48" work table near electrical power outlet.  Provide portable office or use a suitable room as designated by Owner and relocate or add equipment as required to meet the above requirements.

3.11	SANITARY FACILITIES:

A.	Toilets:  Use of the Owner's existing toilet facilities, as indicated, will be permitted, so long as these facilities are properly cleaned and maintained in a condition acceptable to the Owner.  At substantial completion, restore these facilities to the condition prevalent at the time of initial use.  Written permission from the owner must be obtained, and all provisions of these specifications regarding leaving the work area are met.

B.	Toilets: Provide one self-contained chemical toilet unit in the Work Area for each 30 workers.. Facilities shall be maintained throughout the Work.  At the end of the job, facilities shall be decontaminated in accordance with these specifications.

3.12	FIRE EXTINGUISHERS:

A.	Fire Extinguishers:  Comply with the applicable recommendations of NFPA Standard 10 "Standard for Portable Fire Extinguishers".  Locate the appropriate class of fire extinguishers where they are most convenient and effective for their intended purpose.

3.13	STORAGE FACILITIES:

A.	Storage:  The Contractor shall provide a temporary construction trailer as a storage area for tools, equipment and supplies.  Waste generated during abatement shall be stored in a construction trailer in addition to above.

END OF SECTION - 01504