## Introduction
PROJECT BOOK
AE SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTERS
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
2020-02-26
"
PROJECT NAME
| I. | PROJECT BOOK PHASE OVERVIEW
|  | A. | General
|  |  | 1. | The purpose of the PROJECT BOOK analysis phase is to provide a thorough technical evaluation to establish the requirements for the project, covering site and any existing building conditions, utilities, the final SEPS Program for Design (PFD) baseline and Preliminary Room Contents (PRC), which will establish the Design-to Budget for the AE of Record. The PROJECT BOOK analysis will be done under a separate contract from the AE-of-Record contract in coordination with the Project Stakeholders and VAMC Staff.
|  |  | 2. | Additional studies may be required to verify existing conditions to resolve proposed programming issues. Special studies shall be handled on a case-by-case basis with the approval of the VA PM. AE will verify and coordinate workload and staffing requirements.
The PROJECT BOOK includes only studies and analysis; it does not include any design work.
|  | B. | How to Use this Document
|  |  | 1. | This spreadsheet should be used to ensure all required content is compiled into a single source for use with the AE of Record.
|  |  | 2. | VA will use this document as Government Furnished Information (GFI) to assist the AE of Record in preliminary project design work.
|  |  | 3. | The PROJECT BOOK spreadsheet for the required project deliverables is completed by the VA and the AE during an assessment phase prior to the project kickoff meeting. VA should identify all work provided by VA, as well as all work required by PB Contractor in provided columns.
|  |  | 4. | A level of development is noted for each submittal element. The levels are:
P = Preliminary Information
U = Updated Information
F = Final Information
|  |  | 5. | The Project Book spreadsheet is locked with the exception of the Submittal Checklist, which can be edited.
|  |  | 6. | Additional work can be added by inserting rows in the spreadsheet.
|  |  | 7. | Work that is not needed can be eliminated by putting "NA" in the Submittal Checklist.
|  |  | 8. | The spreadsheet can be sorted using the Tabs located in the Header.
|  |  | 9. | At the top of the Heading in the PROJECT BOOK tab, enter the Project Name, Project Number, and Effective Date of the spreadsheet.
|  | C. | Tab Heading Legend
|  | D. | Type of Deliverable
Report
Calculations
Aggregate
Drawings
| II. | DISTRIBUTION OF A/E SUBMITTALS FOR REVIEW

## PROJECT BOOK
PROJECT BOOK
A/E SUBMISSION REQUIREMENTS FOR VA MEDICAL CENTER
MAJOR NEW FACILITIES, ADDITIONS & RENOVATIONS
PROJECT NAME | [6 empty] | PROJECT NUMBER | EFFECTIVE DATE OF SPREADSHEET
Submittal Checklist
Seq. No. |  | Type | Topic |  |  |  |  | Description | VA Work | Project Book Consultant | Submitted | Pending | NA | Comments
PROJECT BOOK
PB-1. | 0 |  |  | NEPA/Historic Preservation
PB-1. | 1 | Report |  | NEPA/Environmental Site Assessment |  |  |  | Conduct a NEPA and Environmental Site Assessment Study (if needed)
PB-1. | 2 | Report |  | Cultural/Historic Resources Studies |  |  |  | Complete Cultural and Historic Resource Studies
PB-1. | 3 | Report |  | Historic Preservation Requirements |  |  |  | Perform a physical condition assessment to identify historic preservation requirements if applicable and extent of preservation limits (i.e. exterior or interior or identified key areas).
PB-1. | 4 | Report |  | Analysis |  |  |  | Provide a summary of the impacts to the project of the Environmental Site Assessment, NEPA, and cultural and historic resources analysis surveys.
PB-2. | 0 |  |  | Existing Building Assessment
PB-2. | 1 | Report |  |  | Accessibility Assessment (Accessible Path) |  |  | For existing buildings being renovated, the Project Book A/E shall do site investigations for conformance with ABA accessibility requirements. The Project book A/E shall produce a report of the required accessibility upgrades. The report shall include a scope of work, and budget for the site upgrades. This includes the accessible path of travel and any associated spaces such as bathrooms, entries, etc…
PB-2. | 2 | Report |  |  | Transport & Logistic Systems |  |  | Provide Transport and Logistical Systems study for existing and the new project.
PB-2. | 3 | Report |  |  | Inventory of Existing Documentation |  |  | Provide an Inventory of existing available facility documentation (drawings, specifications, etc.) from the VAMC Engineering Department. When needed, provide description of recommended investigation.
PB-2. | 4 | Report |  |  | Shared Services |  |  | Shared services agreements with other facilities. This could include utilities, medical services, or other.
PB-2. | 5 | Report |  |  | FCA |  |  | Provide the most recent Facility Condition Assessments and Façade Inspection Report
PB-2. | 6 | Report |  |  | Code Violations |  |  | Determine if there are code violations, e.g. demand exceeds design capacity.
PB-2. | 7 | Report |  |  | Existing Facility Laser Scanning |  |  | If accurate architectural information is not available, conduct a laser scan as-built survey as basis of BIM
PB-2. | 8 | Report |  |  | Steam Distribution |  |  | Submit an initial assessment including the following:
PB-2. | 9 | Report | [5 empty] | Provide description and evaluation of existing steam distribution facilities that are involved in the project.
PB-2. | 10 | Report | [5 empty] | Estimate of the remaining service life for all steam and condensate systems.
PB-2. | 11 | Report | [5 empty] | Provide information on existing system steam pressures, types of condensate return systems (pumped gravity, vacuum).
PB-2. | 12 | Report | [5 empty] | Provide documentation of existing utility loads with supporting data.
PB-2. | 13 | Report | [5 empty] | Assess amount of demolition required.
PB-2. | 14 | Report | [5 empty] | Provide analysis of capabilities of existing systems to accommodate additional loads.
PB-2. | 15 | Report | [5 empty] | Describe existing systems and determine the remaining service life of the system.
PB-3. | 0 |  |  | Alternatives for Waste Disposal
PB-3. | 1 | Report | [5 empty] | Provide summary of documentation of existing types and quantities of waste.
PB-3. | 2 | Report | [5 empty] | Determine emissions regulations and types of emissions controls required.
PB-4. | 0 |  |  | Hazardous Materials Report
PB-4. | 1 | Report | [5 empty] | Submit the Medical Center Hazardous Materials Report for all known hazards (see VA guidelines for asbestos abatement).
PB-5. | 0 |  |  | General
PB-5. | 1 | Report |  |  | COGEN |  |  | Identify if COGEN option will be executed
PB-5. | 2 | Report |  |  | Fire Protection |  |  | Report on the fire protection meeting with fire marshal
PB-5. | 3 | Report |  |  | Project Risk Register |  |  | VA and Project Book AE shall collaborate to develop the Project Risk Register
PB-5. | 4 | Report |  |  | Sustainability Rating |  |  | Identify required level of Third Party Sustainability rating required.
PB-5. | 5 | Report |  |  | Sustainability, Energy Reduction, Renewable Energy Use |  |  | Identify the sustainability, energy reduction, and renewable energy strategies that show the most promise for this location, climate, and building type. Renewable energy to be included in the assessment must include solar thermal, solar PV, wind, solar hot-water, and geothermal.
PB-6. | 0 |  |  | Physical Security
PB-6. | 1 | Report | [5 empty] | Determine if facility requires Mission Critical or Life Safety designation.
PB-6. | 2 | Report | [5 empty] | Identify Major Site Security Issues/Risks
PB-6. | 3 | Report | [5 empty] | Provide preliminary calculations for required emergency storage capacity.
PB-6. | 4 | Report | [5 empty] | Provide information regarding existing security risks and security plans (collaborate with VAMC)
PB-6. | 5 | Report | [5 empty] | Confirm cyber security compliance of existing Telecommunications Systems and Medical Low Voltage systems.
PB-6. | 6 | Report |  |  | Continuity of Operations Plan |  |  | Provide Continuity of Operations Plan (COOP) requirements.
PB-7. | 0 |  |  | Site Analysis
PB-7. | 1 | Report |  |  | Seismic Analysis |  |  | If an existing facility: Define seismic zone, ranking on VA's seismic list, typical structural types and bay sizes, review VA's analysis for problems needing correction, provide preliminary suggestion for corrections. If a new facility: Define seismic zone; determine if testing for local non-structural seismic bracing is needed.
PB-7. | 2 | Report |  |  | Climate Analysis |  |  | Provide Graphic presentation of the results of the site climate analysis (wind, water, solar, temperature, humidity). Identify typical extreme weather events (hurricanes, tornados, hail, monsoons, etc.) and mitigating strategies (e.g., hurricane lateral wind-borne rain in Gulf coast areas = glazing/framing water drainage, roof drainage scupper capacities). Provide heating & cooling days, high and low temperatures, average rainfall and snowfall by month and by highest record events. Show sun arc and angles for summer and winter solstices. Note prevailing wind direction and speed.
PB-7. | 3 | Report |  |  | Preliminary Geotech & Soils Report |  |  | Provide a preliminary Geotech Analysis and soils report.
PB-7. | 4 | Report |  |  | Parking |  |  | Determine existing number of parking spaces (full and compact), accessible parking spaces, and handicapped van parking spaces for surface and structured parking allotment.
PB-7. | 5 | Report |  |  | Storm water Regulations |  |  | Review and define requirements of local, state, and federal storm water regulations, and third-party sustainability storm water design requirements, when required. Evaluate erosion control requirements
PB-7. | 6 | Report |  |  | Site Cost Impacts |  |  | Document On-site considerations that may impact design and cost of project development including but not limited to: Site access/circulation, ingress/egress by pedestrians (including persons with disabilities), passenger vehicles, delivery vehicles, emergency vehicles, and mass transit, if applicable as well as building access for fire apparatus, site security requirements, etc.
PB-7. | 7 | Report |  |  | Drainage |  |  | Perform a preliminary drainage analysis of existing site conditions to assess potential options for storm water management strategies. Generally locate areas where storm water storage facilities shall be, if needed.
PB-7. | 8 | Report |  |  | Flood Plain |  |  | Identify location of wetlands, 100, and 500-year flood plains.
PB-7. | 9 |  |  |  | Permanent USGS Survey Marker |  |  | Verify if a permanent, physical geographic USGS marker in the State Plane Coordinate system is available on the project campus or site. If not, the Civil Engineer, or licensed surveyor, will establish the Survey Marker and coordinates to be used for accurately locating buildings, site work, utilities, and infrastructure.
PB-7. | 10 | Drawings & Model(s) |  |  | Professional Land Survey and Site Utility Plans |  |  | Provide a topographic survey (2-foot contour lines, spot elevations at building entrances and corners, location of runs, rim, and invert elevations for all utilities), Boundary Survey (metes and bounds, legal description, easement description and locations) for the project site and extending five feet beyond the project boundaries. Model all topographic information, location of site boundary and easements, and existing underground utilities (location, rim and invert elevations) information in BIM. Provide the model and 2D plans as noted in the DDR. All work shall be under the direction and signed/sealed by a Professional Engineer.
PB-7. | 11 | Drawings |  |  | Seismic Information |  |  | Provide Seismic Vulnerability Study Summary, seismic site study, structural drawings, strengthening studies, and other documents (if existing).
PB-7. | 12 | Drawings |  |  | Site Context |  |  | Surrounding site considerations that may impact design and cost of project development, including but not limited to: surrounding land uses, mass transit routes, and utilities, zoning, easements, aircraft flight patterns, flood hazards, wetlands, topography, and biological and other environmental considerations, advantageous views or historic-heritage trees, local neighborhood or civic concerns.
PB-8. | 0 |  |  | Helicopter Operations
PB-8. | 1 | Report | [5 empty] | Ascertain if helicopter operations are required.
PB-8. | 2 | Report | [5 empty] | If helicopter operations are required, define design requirements, site constraints, FMS emergency voice and radio communications systems. Ensure compliance with FCC and FAA requirements.
PB-8. | 3 | Aggregate |  |  | Adjacent Utilities |  |  | Provide locations and types of adjacent overhead utilities.
PB-9. | 0 |  |  | Utility Surveys |  |  |  | Graphic Material provided as per the VA BIM STANDARD
PB-9. | 1 | Report |  |  | On Site Utilities |  |  | Provide on-site utility report. Investigate conditions and field-test points of connection for all on-site utilities and telecommunications. Provide information dynamic and static flow testing and indicate direction of flow, size, type, condition, and location, including test-pits and determinations of useful life potential, the need for improvements on and off site, identification of available redundancy and recommend tests (if any) need to determine remaining service life. Include makes, models, sizes, ages, performance capabilities, and remaining service life of all equipment and systems. Determine if existing utilities meet existing code or VA Standards. Recommend tests, as appropriate, to determine remaining service life and capacity of major equipment and piping. Utilities shall include (at a minimum):
PB-9. | 2 | Report |  |  |  | Central Energy Plant (CUP) |  | Conduct analysis of location, types of CUP equipment, existing capacity & condition, expansion capability. Perform a LCCA and capacity study, make a recommendation for upgrade, expansion, or replacement of the existing CUP.
PB-9. | 3 | Report |  |  |  | Steam Generation |  | Provide report discussing alternative types of steam generation and distribution systems to be evaluated.
PB-9. | 4 | Report |  |  |  | CHP |  | Provide report assessing the feasibility of a Combined Heat and Power (cogeneration) system.
PB-9. | 5 | Report |  |  |  | Waste Disposal |  | Provide report discussing alternatives for waste disposal, including incineration of all waste, incineration of portions of the waste (such as pathological) and off‑site disposal of the remainder, off‑site disposal of all waste, and alternative technologies for waste sanitation, processing, and disposal.
PB-9. | 6 | Aggregate |  |  |  | Gas |  | Survey existing propane and natural gas, fuel oil, medical gas systems, and gasoline and diesel fuel systems.
PB-9. | 7 | Aggregate |  |  |  | Steam, Hot & Chilled Water |  | Document sizes, locations, and pressure of all supply & return lines. Document location and sizes of all site-located valves, including capacity and spare capacity.
PB-9. | 8 | Drawing |  |  |  | Storm water |  | Existing drains, catch basins, manholes, drain lines sizes, rim and invert elevations, existing storm water retention features and capacities.
PB-9. | 9 | Drawing |  |  |  | Wastewater and Sewer |  | Sizes, types, condition (if known), and locations of all drain lines, manholes, lift stations, holding tanks, etc.
PB-9. | 10 | Aggregate |  |  |  | Domestic & Fire Protection Water Supply |  | Sizes, locations, types, direction of flow, pressures of all supply piping, valves, meters, backflow preventers, pumps, water quality or treatment systems. Provide pressure test for each fire hydrant and show pressures & flow rates. Show existing water storage tanks (potable, landscape irrigation).
PB-9. | 11 | Report |  |  |  | Water Analysis |  | Water analysis, including pH, total hardness as CaCO3, and total dissolved solids. Identify the need for a water softener or special waters systems such as reverse-osmosis. Identify the need for acid or chemical resistant piping.
PB-9. | 12 | Aggregate |  |  |  | Electrical Service and Distribution |  | Electrical services voltage, conduit, overhead and underground locations, manholes, and hand holds. Show substation and transformer locations and capacities; backup emergency power types, location, equipment condition, and capacity. Provide the capacity and demand load of the existing loop. Present demand load (medium voltage switchgear and primary feeder) and projected additional load of new construction. Determine requirements for emergency power.
PB-9. | 13 | Report |  |  |  | Medical Low-voltage |  | Identify and list existing systems, with all requirements, controls, existing and unused capacity, shielding, power requirements, grounding, heating and cooling requirements, security (types of firewalls, physical security of system), expansion capacity (trays/plenum spaces), etc., as needed to support existing medical equipment. Identify similar requirements for a new building, anticipating/recommending future-proof technology that will most likely be current at the anticipated "First Patient Day" plus 3 years.
PB-9. | 14 | Aggregate |  |  |  | Medical Gas |  | Medical Gas Systems
PB-9. | 15 | Aggregate |  |  |  | Emergency Power |  | Emergency Power System/ Equipment
PB-9. | 16 | Aggregate | [5 empty] | Fire Alarm Systems
PB-9. | 17 | Aggregate | [5 empty] | Security Systems
PB-9. | 18 | Aggregate |  |  |  | Building Automation System (BAS) |  | Identify existing building control system(s) and system control requirements/BAS integration for the new building. Include lighting controls. Define BAS electronic security requirements.
PB-9. | 19 | Report |  |  |  | Waste Disposal |  | Accurate determination of existing types and quantities of waste. Provide verification of the accuracy.
PB-9. | 20 | Report | [5 empty] | Evaluation of the capability of the existing incinerator facilities to accept additional quantities and types of waste material.
PB-9. | 21 | Report | [5 empty] | Provide analysis of viable alternatives for waste disposal and recommended solution. Give rationale for the selection or rejection of alternatives.
PB-9. | 22 | Report | [5 empty] | Determine emissions regulations and types of emissions controls required.
PB-9. | 23 | Report |  |  | Telecommunications
PB-9. | 24 | Aggregate | [5 empty] | Provide survey and analysis of existing Telecommunications Equipment Rooms (i.e. DEMARC Room, Telephone Room, Telephone Operator’s Room, Main Computer Room, Antenna Head end Room, Emergency Management and Preparedness and Police Control Rooms), HVAC, UPS and A/C Power Requirements. Provide identification and amount of available space for Telecommunications Infrastructure Plant (TIP) backbone and pathways; must be sized for sharing by FMS and OI&T. Sizes and locations of all conduits, manholes, and hand holes. Provide wire type, sizes, and number. Include Wi-Fi, telephone, satellite, and other communication systems. If Telecommunications Service Providers have existing inside building distribution systems installed contact Spectrum Management and CONSEC Service as per the Telecommunications Design Manual (TDM) Paragraph 1.3).
PB-9. | 25 | Report |  |  | FMS Emergency System |  |  | Evaluation of FMS Emergency system
PB-9. | 26 | Report |  |  | Assessment |  |  | Assessment of whether the existing telecommunications services are adequate for project needs.
PB-9. | 27 | Report | [5 empty] | Statement of the impact of the new construction to the existing telecommunications systems.
PB-9. | 28 | Report | [5 empty] | Describe location and need for redundant feeds.
PB-9. | 29 | Report | [5 empty] | Description of the extent of utility company work required.
PB-9. | 30 | Report |  |  |  | Service Providers |  | Description of Service Provider presence.
PB-9. | 31 | Report | [5 empty] | Verify if Telecommunications Service Providers have existing building distribution systems installed – if so, IMMEDIATELY contact Spectrum Management and COMSEC Service see Telecommunications Design Manual (TDM).
PB-10. | 0 |  |  |  | Off-Site Utilities |  |  | Graphic Material provided as per VA BIM Standards
PB-10. | 1 | Report |  |  |  | Utility Locations |  | Verify and show sizes, types, capacities, existing water pressure, and points of connection (including elevation and inverts) for all utilities needed for the project. Determine if any additional infrastructure improvements (lift stations, transfer stations, backflow preventers, pressure regulators, etc.) are required.
PB-10. | 2 | Report |  |  |  | Utility Providers |  | Identify all utility providers, office location, contact individual, and phone number. Verify with utility providers that capacity exists for the new project.
PB-10. | 3 | Report |  |  |  | Required Permits |  | Identify permits required and tap fees.
PB-10. | 4 | Report |  |  |  | Utility Redundancies |  | Identify potential off-site source(s) and location(s) for providing utility redundancies to comply with requirements in the Physical Security Design Manual for Mission Critical Facilities.
PB-11. | 0 |  |  | Transportation and Parking
PB-11. | 1 | Report |  |  | Traffic |  |  | Provide traffic analysis/study for existing on and off-site traffic, intersection and traffic/pedestrian/public transportation access.
PB-11. | 2 | Report |  |  | Public Transportation |  |  | Identify public transportation options available or planned to the site.
PB-11. | 3 | Report |  |  | Parking |  |  | Conduct a parking demand study for existing and proposed number of parking spaces, accessible and van spaces, for surface and structured parking.
PB-11. | 4 | Report |  |  | Site Access |  |  | Evaluate site access for passenger, delivery, emergency, and fire vehicles.
PB-12. | 0 |  |  | Existing Building Structural Analysis
PB-12. | 1 | Report | [5 empty] | Documentation and evaluation of existing structure, including review of original construction drawings and specifications.
PB-13. | 0 |  |  | Existing Building HVAC Analysis
PB-13. | 1 | Report | [5 empty] | Identify and analyze existing HVAC systems. Consider age, remaining useful life, condition, accessibility for maintenance, repair, and replacement, costs, deficiencies to managing healthcare, and other considerations as needed.
PB-13. | 2 | Calculations | [5 empty] | Identify unused system capacities
PB-13. | 3 | Report | [5 empty] | Identify impact and compatibility of existing control systems
PB-13. | 4 | Calculations | [5 empty] | Establish and provide the existing building annual energy-use intensity and annual site energy use in both tabular and graphical form by end use (where available).
PB-13. | 5 | Calculations | [5 empty] | Investigate capacity & life cycle of existing steam systems
PB-13. | 6 | Report | [5 empty] | Identify if steam can be purchased in lieu of generation onsite
PB-14. | 0 |  |  | Planning
PB-14. | 1 | Report |  |  | Reports from SEPS |  |  | Provide the Project BIM Export Excel file for the Baseline Space & Equipment Planning Systems Program for Design (PFD) and Project Room Contents (PRC) for use in the SEPS2BIM process (Data to BIM transfer)
PB-14. | 2 | Report | [5 empty] | Program for Design (Excel)
PB-14. | 3 | Report | [5 empty] | Program for Design Summary
B-14. | 4 | Report | [5 empty] | Program for Design Summary (Excel)
B-14. | 5 | Report | [5 empty] | Project Room Contents
B-14. | 6 | Report | [5 empty] | Project Contents List (Excel)
B-14. | 7 | Report | [5 empty] | Project Contents Cost Summary By Acquisition Code (VA)
B-14. | 8 | Report | [5 empty] | Project Contents Cost by Acquisition Code (VA)
B-14. | 9 | Report | [5 empty] | Establish final ConOps provided by the station
B-14. | 10 | Report | [5 empty] | Provide a Copy of the Integrated Master plan or Facility Master plan for the site (if available)
PB-15. | 0 |  |  | Project Management Plan (PMP)
PB-15. | 1 | Report | [5 empty] | Provide support, input, information, data, and detail to the VA Project Manager for development of the VA Project Management Plan (PMP) which will address Scope/Requirements, Schedule, Cost Management, Communications Management, Process Improvement, Staffing Management, Quality Management, Change Management, and Risk Management, and cover functionality, budgetary, aesthetic, sustainability, security, schedule, procurement method, and related requirements for the project. The VA PMP shall also outline participants roles and responsibilities, regularity of meetings, and define the process for information sharing and frequency. The AE shall assist the VA PM in updating the PMP at each design phase.
PB-15. | 2 | Report |  |  | Risk Register |  |  | Create Risk Register (assist VA PM)
PB-15. | 3 | Report |  |  | PDRI |  |  | Create PDRI
PB-15. | 4 | Report |  |  | Integrated Master Schedule (IMS) |  |  | Provide the Integrated Management Schedule (IMS--a subset of the VA PMP) which outlines the design schedule, construction schedule, and activation schedule
PB-15. | 5 | Report |  |  | Acquisition Method |  |  | Define the Acquisition process/method (derived from collaboration with acquisitions). CPM is a subset of Master VA PMP.
PB-15. | 6 | Report |  |  | Major Milestone Schedule |  |  | Working with CFM, provide a preliminary "First Patient Day," do a Lean "Pull Schedule," and integrate the IMS major design/construction milestones.
PB-16. | 0 |  |  | Requirements Definition for New Facility
PB-16. | 1 |  |  |  | Building
PB-16. | 2 | Report |  |  |  | Basis of Design |  | Create a Basis of Design (BOD) Report for the project, providing the descriptive information necessary to evaluate the proposed project from a technical perspective. Include the Concept of Operations for medical delivery and for facility management/maintenance, etc. Include workload and staffing requirements.
PB-16. | 3 | Drawings |  |  |  | Functional Adjacencies |  | Identify optimal functional adjacencies based on the program requirements
PB-16. | 4 | Report |  |  |  | ASE |  | Identify and quantify all Architectural Significant Equipment (ASE) required.
PB-16. | 5 | Report |  |  |  | Codes & VA Standards |  | Provide preliminary list by document name and effective date of applicable national codes and VA Standards that will apply to project. Provide summary of the code analysis for each applicable code or standard needed for the project.
PB-16. | 6 | Report | [5 empty] | Evaluation of percentage of new and existing construction to ascertain if code compliance, security upgrades, etc., will apply to all parts of the building.
PB-16. | 7 | Report |  |  |  | Building Structural Evaluation |  | Determine commonly used structural systems in the project location for similar structures to those for proposed VA project.
PB-16. | 8 | Report |  |  |  | Building Logistics |  | Define transportation and logistical systems requirements
PB-16. | 9 | Report |  |  |  | Expansion |  | Identify strategies for flexibility to accommodate future functional growth (Show 25% conceptual blocking and circulation).
PB-16. | 10 | Report |  |  |  | Medical Low-voltage |  | Identify existing medical low-voltage systems and define preliminary types, controls, and technical requirements for new operations.
PB-17. | 0 |  |  |  | Major Building Systems
PB-17. | 1 | Report |  |  |  | System Assumptions |  | Identify assumptions, including type and quantity, for major structural systems, exterior cladding (including insulation and percentage of glazing), major conveying systems, and major HVAC systems.
PB-17. | 2 | Report |  |  |  | Basis-of-Design |  | Define Basis-of-Design for performance requirements for each major building system, including lifecycle costs for the mechanical equipment.
PB-17. | 3 | Report |  |  |  | Interstitial Space |  | Determine areas where interstitial spaces may be used
PB-18. | 0 |  |  |  | Site |  |  | Graphic Material provided as per VA BIM Standards
PB-18. | 1 | Drawings |  |  |  | Access |  | Define vehicular and pedestrian access.
PB-18. | 2 | Report |  |  |  | Service Vehicles |  | Define sizes of all delivery, emergency, waste, and fire vehicles, required access space, turning radii, and dock heights recycling, and widths.
PB-18. | 3 | Report |  |  |  | Parking |  | Quantify requirements for structured and surface parking.
PB-18. | 4 | Report |  |  |  | Renewable Energy |  | Identify viable options for on-site renewable energy use.
PB-18. | 5 | Report |  |  |  | Utilities |  | Preliminary capacity and other requirements for all needed utilities as outlined in investigative reports.
PB-18. | 6 | Report |  |  |  | Security |  | Identify site and physical security requirements for setbacks and other measures.
PB-19. | 0 |  |  |  | Construction
PB-19. | 1 | Report |  |  |  | Preliminary Joint Occupancy Plan |  | Provide a basis for a "ILSM and ICRA Joint Occupancy Plan" for concurrent construction and medical operations.
PB-19. | 2 | Report |  |  |  | Other Site Construction Work |  | Identify project coordination for all on-going or station planned construction work (10 yr. window) for the site.
PB-19. | 3 | Report |  |  |  | Phasing |  | Provide preliminary plans for construction phasing, laydown space, including on-site location of VA Resident Engineer's office.
PB-19. | 4 | Report |  |  |  | Offsite Prefabrication/Modularization |  | Analyze potential and criteria for off-site prefabrication and modularization.
PB-20. | 0 |  |  | Preliminary Site Test-fit (BIM) |  |  |  | Graphic Material provided as per VA BIM Standards
PB-20. | 1 | Drawings & Models | [5 empty] | Provide options for preliminary Departmental Blocking & Stacking test-fit in BIM
PB-21. | 0 |  |  | Design-to Budget
PB-21. | 1 | Calculations | [5 empty] | Provide VA project budget for AE of Record
PB-22. | 0 |  |  | BIM and Drawings
PB-22. | 1 | Drawings & Model(s) | [5 empty] | Provide all material in native files and .NWD (or Equal) as per VA BIM STANDARDS