## Respondants (hidden)
|  | Response | Completed |  | Finalized
Intro |  |  | 2020-06-10 | Koch | Yes
Overview |  |  | 2020-06-10 | Koch | Yes
General |  |  | 2020-06-10 | Koch | Yes
| BIM |  | 2020-09-28 | Yo | Yes
| SPECS | 2020-06-18 | 2020-06-18 | Johnson | Yes
| CPM | 2020-06-12 | 2020-06-12 | Ghobanpour | Yes
| CX | 2020-06-11 | 2020-06-18 | Tash | Yes
Civil |  | 2020-06-24 | 2020-06-24 | Symanski | Yes
Structural |  |  | 2020-09-17 | Doiron | Yes
Structural |  | 2020-06-18 | 2020-06-18 | Archilla | Yes
Structural |  | 2020-07-29 | 2020-09-17 | Ghosh | Yes
Architecture |  |  | 2020-06-18 | Koch | Yes
Architecture |  | 2020-06-12 | 2020-06-12 | Treece | Yes
Equipment |  | 2020-06-18 | 2020-06-18 | Brown | Yes
Interiors |  | 2020-07-07 | 2020-07-07 | Burdiak | Yes
Fire |  | 2020-04-24 | 2020-04-24 | Larrimer | Yes
Plumbing |  | 2020-06-18 | 2020-06-18 | Desai | Yes
Mechanical |  | 2020-06-24 | 2020-06-24 | Raychaudhri | Yes
Mechanical |  | 2020-06-18 | 2020-06-18 | Walden | Yes
Elect |  | 2020-05-13 | 2020-05-13 | Tran | Yes
Elect |  | 2020-06-18 | 2020-06-18 | Lau | Yes
Telecom |  | 2020-06-11 | 2020-06-12 | Bates | Yes
Telecom |  | 2020-06-11 | 2020-06-12 | Frakes | Yes
Environmental |  | 2020-06-18 | 2020-06-18 | Elliott | Yes
Sustainable |  | 2020-06-24 | 2020-06-24 | Symanski | Yes
Historic |  | 2020-06-18 | 2020-06-18 | Abreu | Yes
Physical Security |  | 2020-06-18 | 2020-06-18 | Lau | Yes
Elevator |  | 2020-06-24 | 2020-06-24 | Phillips | Yes
Cost |  | 2020-06-18 | 2020-06-18 | Hoover | Yes
Yes
100%

## Introduction
|  | PG 18-15 VOL DB DESIGN BUILD | MM/DD/YYYY
2024-04-01
A. | How to Use this Document
| 1 | At the top of the Heading in the GENERAL Tab, enter the Project Name, Project Number, and Contract Effective Date.
| 2 | This spreadsheet shall be used to ensure all required content is delivered at indicated milestones.
| 3 | This document will be used as a review tool to ensure all deliverables are addressed.
| 4 | The PG 18-15 DB spreadsheet for the required design build deliverables should be finalized for the project by the Government and Contractor during the design schedule development.
| 5 | Each Tab represents typical discipline(s) used on a VA project. It remains the responsibility of the DOR to coordinate disciplines (e.g., sustainability, building systems, etc.) regardless of where the deliverables are listed in the spreadsheet discipline tabs.
| 6 | The PG 18-15 DB spreadsheet is locked with the exception of the Submittal Checklist and Fast Track sections. Rows can be inserted to the spreadsheet when additional work is required for a project. Please coordinate with CSS. Columns can be inserted to the spreadsheet for items that are approved for fast tracking. See item 13 for instructions on how to edit the document for any work that is approved to be fast tracked.
| 7 | Work that is not needed can be eliminated by putting "NA" in the appropriate Submittal Checklist column.
| 8 | PHASE: Each Design delivery phase has a column:
SD/35%
DD/65%
CD/100%
DESIGN COMPLETE CONSTRUCTION DOCUMENTS (Not a review; record document for construction)
In each phase, the level of development for each submittal element is defined. The levels are:
P = Preliminary Information
U = Updated Information
F = Final Information
R = Resubmission
| 9 | SUBMITTAL CHECKLIST HEADER: An "X" must be placed in the appropriate Submittal Checklist section (Included in RFP, Submitted, Pending, Not Applicable (NA)) to note the status and inclusion of the content in the submittal. Include the location of the submittal where the information can be found. Comments may be noted if explanations are needed.
| 10 | Type of Deliverable
Report
Calculations
Aggregate (a mix of deliverable types)
Drawings (BIM and 2D Documentation)
| 11 | The PG 18-15 DB Checklist for the project must be provided in the latest version of Excel, and also printed and included at the front of the Submittal Deliverable.
| 12 | The Excel file must be saved using the official project name, submittal design package number (if applicable), and submittal phase. Example: Louisville Replacement VAMC – SP1 - SD1.xlsx
| 13 | For work that will be fast tracked, columns QRS have been provided to the right of the Submittal Checklist. Additional Packages can be added using the copy/paste function of those columns; unused columns may be deleted if not required. Each package must indicate the submission plan for each deliverable and be named and dated. Include and edit as necessary the submittal phase with the deliverable and coordinate them with all other tabs that pertain to the submittal package (as applicable). All fast Track elements are subject to approval and considered pending until approved.
B. | Table of Contents
Overview
General
Integrated Project Design
Building Information Model
Specifications
Critical Path Method
Commissioning
Civil
Structural
Architectural
FF&E
Medical Equipment
Food Service
Interiors
Interiors
Furniture Fixtures & Equipment
Signage & Wayfinding
Fire Protection
Plumbing
Mechanical
Heating, Ventilating & Air Conditioning
Steam Generation (Outside)
Steam Generation
Incineration / Waste Disposal Systems
Electrical
Telecommunications
Environmental Compliance
Sustainability
Historic
Physical Security
Elevator Transport
VA SME Michael Koch
michael.koch3@va.gov

## Overview
PG 18-15 VOL DB DESIGN BUILD
I. |  | DESIGN PHASE OVERVIEW
General
| 1 | The PG 18-15 DB requirements formatted by technical discipline does NOT direct the staffing of the work effort.
| 2 | This document contains the minimum submission requirements for the Design Phase of the major project.
| 3 | The Designer of Record (DOR) is responsible for producing a complete set of construction instructions, including 3D models (BIM), drawings, specifications, calculations, sample boards, equipment catalog cuts, performance curves, dimensions, and capacity ratings, and data (from BIM, etc.) in accordance with the RFP. The DOR shall be responsible for obtaining and using all design criteria.
| 4 | The DOR must use, manage, and submit all graphic/data information as described in the RFP and VA BIM STANDARD.
| 5 | Each progressive design submittal should build upon the previous information to provide a clear basis of design development and design philosophy fitting to the project. All previously submitted documents shall be updated to reflect review comments and further development.
| 6 | All models, drawings, booklets, and other supporting materials in each submittal shall be clearly and consistently identified throughout the design process with the project title, location, building, phase, section, and segment. Written materials must refer back to the PG 18-15 DB corresponding numerical description.
| 7 | CFM (or Construction Agent) is responsible for reviewing and commenting on all design submissions. VA may engage the services of peer reviewers to review the submissions at each review stage.
| 8 | The DOR shall provide individually packaged submissions to each unit specified in the "Distribution of Submission Materials" table located in the Distribution Tab. The DOR shall submit a completed check-list at each submission detailing all required submittal material by discipline. Any material not submitted will be marked either "Pending" with an anticipated date of submittal or "N/A", and include an explanation in the comments section.
| 9 | The DOR shall provide the following design submissions for VA design review:
SD/35%
DD/65%
CD/100%
| 10 | For seismic retrofit projects funded by Seismic EQ funds: Project shall seismically upgrade the facility in accordance with VA standards and criteria. Other functional, programmatic and physical upgrades shall be limited to the minimum changes necessary to accomplish the implementation of the seismic corrections.
| 11 | For multiple design submittal packages follow directions given in the Introduction worksheet tab.
II. |  | SD/35%
GENERAL
| 1 | These Design phase documents are developed in accordance with the RFP. Design further develops the RFP into a level of detail that includes specific functional and adjacency requirements and establishes the aesthetics of the design.
| 2 | A Project Management Plan shall be developed by the Integrated Project Team, led by the PDT.
| 3 | Specifications shall be prepared using VA Master Construction Specifications. Submissions shall show changes to master by using the "Track Changes" function. Each submission shall indicate changes from previous submission, not all changes to the master. Specifications submitted at the end of each phase (not for each review) shall include all changes.
III. |  | DD/65%
GENERAL
| 1 | This Design phase encompasses adding an increased level of detail for all aspects of the project to further define the design. Submissions at this stage must show coordination of trades and clarity of scope and design intent. The AE will perform a room test-fits to assure that all required Project Room Contents (PRC) can be accommodated. Submissions at this stage must show coordination of trades and clarity of scope and design intent. This phase will also provide visualization of the project and communicate the character of interior and exterior spaces. All value engineering shall be completed by the end of this phase, and no functional changes are anticipated after the DD review.
| 2 | Specifications shall be prepared using VA Master Construction Specifications. Submissions shall show changes to master by using "Track Changes" function. Each submission shall indicate changes from previous submission, not all changes to master.
IV. |  | CD/100%
GENERAL
| 1 | The purpose of this Design phase is to add the level of detail required for construction of the project, coordinate the trades, and finalize the project’s documentation for construction. This includes refinement of the 3D Models, 2D drawings, design details, and specifications so the project can achieve its highest value and performance suitable for the building's lifecycle.
| 2 | This Design phase involves the production of complete 3D Models, 2D drawings, specifications, and other documents necessary for the bidding and construction of the project, prepared from the prior phase. Also included at this phase are the the final phasing plan and the construction schedule.
| 3 | The DOR must provide design-intent documentation that provides the necessary information for construction. Documentation shall be complete, fully coordinated, and ready for use by the Contractor.
| 4 | The final specification submission must be complete and coordinated with the graphic documentation (3D models, 2D Drawings). The final submission must be a "clean copy" and not show changes.
V. |  | DESIGN COMPLETE CONSTRUCTION DOCUMENTS
| 1 | The Design Complete Document phase involves the production of complete, 3D models, 2D drawings, specifications, and other documents necessary for construction of the project.
| 2 | The final specification submission must be complete and coordinated with the graphic documentation (3D models, 2D drawings). The construction submission must be a "clean copy" and not show changes.
| 3 | Design Complete Documents and calculations shall be signed and sealed by DOR.
VA SME Michael Koch
michael.koch3@va.gov

## Distribution
PG 18-15 VOL DB DESIGN BUILD
DISTRIBUTION OF DESIGN DELIVERABLES
OFFICE | CFM PROJECT MANAGEMENT |  |  |  |  | CFM - VACO |  |  |  | VA - VACO |  |  | VHA
| REGIONAL PROJECT MANAGER (PM) | REGIONAL CONTRACTING OFFICER | PEER REVIEWER | COMMISSIONING CONSULTANT | CONSTRUCTION MANAGER | CONSULTING SUPPORT | VACO COST ESTIMATING | FACILITIES STANDARDS | PLANNING | TELECOMMUNICATION SERVICES (005OP213) | BOILER | SPD, PHARM, SCI, POLYTRAUMA | CAPITAL ASSET MANAGEMENT 1ONA5 | VA MEDICAL CENTER (VAMC) | VISN
PROJECT STAGE
REQUEST FOR PROPOSAL (RFP) | CR | CR | CR | CR | CR | SP / CD | SP / CD | SP / CD | SP / CD | SP | SP / CD | CR /SP | CR | CR | CR
SD/35% | CR | CR | CR | CR | CR | SP / CD | SP / CD | SP / CD | SP / CD | SP | SP / CD | CR /SP | CR | CR | CR
DD/65% | CR | CR | CR | CR | CR | SP / CD | SP / CD | SP / CD | SP / CD | SP | SP / CD | CR /SP | CR | CR | CR
CD/100% | CR | CR | CR | CR | CR | SP / CD | SP / CD | SP / CD | SP / CD | SP | SP / CD | CR /SP | CR | CR | CR
DESIGN COMPLETE CONSTRUCTION DOCUMENTS (Not a review; record document for construction) | CR | CR | CR | CR | CR | SP / CD | SP / CD | SP / CD | SP / CD | SP | SP / CD | CR /SP | CR | CR | CR
1) MAIL VA DELIVERABLES TO: VA PROJECT MANAGEMENT, CONSULTING SUPPORT SERVICE, COMMISSIONING AGENT, VAMC, VISN, AND NOTIFY THE PROJECT MANAGER ACCORDINGLY. WORK WITH USACE PROJECT MANAGER TO COORDINATE NON-VA DELIVERABLES
2) IN ALL CASES, THE PROJECT MANAGER WILL SEND THE DELIVERABLES TO: CONTRACTING OFFICER, PEER REVIEWER, TELECOMMUINCATIONS SERVICES, CONSTRUCTION MANAGEMENT, REGIONAL & VACO PROGRAM MANAGEMENT OFFICE AND REGIONAL FIRE & SAFETY, IN ADDITION, THE PROJECT MANAGER WILL DETERMINE THE REQUIREMENT FOR SPECIAL PROJECTS SUCH AS SPD, PHARMACY, SCI, POLYTRAUMA ETC.
3) UPON RECEIVING THE DELIVERABLES, THE VA PROJECT MANAGER WILL UPLOAD ALL PROJECT DOCUMENTS TO THE VA SHARE FILE SITE AND ALTER THE DST.
CR | Coordinate requirement with VA Project Manager
SP | Complete set of documents available on SharePoint Site
CD | Complete digital submittal on Compact Disc/Digital Video Disc
CH | Complete set of documents with half size drawings
CF | Complete set of documents with full size drawings

## General
[5 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[6 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package 1 -
Seq. No. | Type | Topic |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | GENERAL |  |  |  | General Requirements per subheadings below
G-1.0 | Report |  | Integrated Project Design
G-1.1 | Report |  |  | Integrated Project Team (IPT) Directory |  | Submit Integrated Project Team (IPT) directory: List of team members, contact information, roles, and responsibilities. Include as appropriate: VA's representatives/stakeholders, A/E, Commissioning Agent, designated subcontractors, community representatives, regulatory agencies, and consultants for specialty disciplines such as Traffic Engineer, Geotechnical Engineer, Environmental Engineer, automatic transportation, blast, Cost Estimate/Management, Acoustical, BIM Manager, and Historic Preservation. Update Team Directory at subsequent phases notifying VA of changes. | P | U | F
G-1.2 | Report |  |  | Quality Control Plan |  | Submit a Quality Control Plan 30-days after award. Demonstrate that the project plans and specifications have gone through a rigorous review and coordination effort. Provide an outline of the actions that the firm will take during the design process. Include each step that will be taken during the development of the various phases of design. Include BIM Design Coordination activities in the QA plan. Review to be conducted by a senior member of the firm who can initial and date when the action has been completed. | P | U | F
G-1.3 | Report |  |  | Certification of Independent Technical Review and Quality Control Review |  | Submit form indicating certification of an ITR and Quality Control Review | P | U | F
G-1.4 | Report |  |  | Project Management Plan (PMP) |  | Provide support, input, information, data, and detail to the VA Project Manager for development of the VA Project Management Plan (PMP) which will address Scope/Requirements, Schedule, Cost Management, Communications Management, Process Improvement, Staffing Management, Quality Management, Change Management, and Risk Management, and cover functionality, budgetary, aesthetic, sustainability, security, schedule, procurement method, and related requirements for the project. The VA PMP shall also outline participants roles and responsibilities, regularity of meetings, and define the process for information sharing and frequency. The AE shall assist the VA PM in updating the PMP at each design phase. | P | U | F
G-1.5 | Report |  |  | Risk Mitigation Plan |  | Provide a Risk Mitigation Plan to address risks such as schedule delays, budget overruns, and scope changes. | P | U | F
G-1.6 | Report |  |  | Applicable Criteria |  | Document all applicable codes and standards in effect at the time of the contract award and update with required changes. This record will include a listing of all industry codes and a downloaded copy of VA applicable criteria, standards, design guides and design manuals. | P | U | F
G-1.7 | Report |  |  | Design Change Summary |  | Provide a summary outlining substantive design changes, and any deviations from VA Criteria such that reviewers can easily evaluate the proposed changes. Deviations from Design Criteria must include a reference to the Criteria, the proposed deviation, and DOR justification for the deviation including cost implications, to be evaluated by the Government prior to implementation. The DOR must keep a log of all deviation requests. | P | U | F
G-1.8 | Report |  |  | Meeting Minutes |  | The Contractor shall submit minutes of meetings with VA and VA's other contractors, as well as for DOR coordination meetings. | P | U | F
G-2.0 |  | BUILDING INFORMATION MODELING
G-2.1 | Report |  |  | BIM Execution Plan (BxP) |  | Submit a Project Bim Execution Plan (BxP), including Data Security Plan, for the project as per VA BIM Standard and in accordance with the RFP. Preliminary BxP required 45 days prior to Interim 1 Design Submittal. | P | F | R
G-2.2 | Report |  |  | BIM Geo-Referencing |  | Locate Model(s) according to VA BIM Standard Appendix - 5 | F | R | R
G-2.3 | Report |  |  | Space Reservations |  | Provide a report defining the space reservations required for each system and equipment. List equipment and system by name, the size and location of the space reservation, the required use for the space reservation, and the tools and equipment that will be used in the space reservation. | P | U | F
G-2.4 | Report |  |  | Interference Management (Design Coordination) |  | Provide summary report of design coordination conflicts remaining to be resolved for building components, equipment, systems, including those in interstitial space and underground utilities. Include insulation, pipe slope, and space reservations in interference management reviews. | P | U | F
G-2.5 | Report |  |  | Design Coordination Reach out Reports |  | Invite the project Constructability Reviewers to observe the Design Coordination meetings. Conduct BIM walk-throughs of all the building systems with the Medical Center Chief Engineer and CSS and others to obtain acceptance of maintenance access and function ability. Provide report of the date of the invitations, invitee name(s), attendee name(s), date of Design Coordination meeting, meeting minutes of results of activities. | P | U | F
G-2.6 | Report |  |  | Design Coordination Reports |  | Provide report of Design Coordination conflicts remaining to be resolved for building components, equipment, systems, including those in interstitial space and underground utilities. Include insulation, pipe slope, and space reservations in all interference management reviews. Provide line progression graph showing progress of all conflict resolutions over time. | P | U | F
G-2.7 | Report |  |  | Spatial & Equipment Data |  | Provide progress report on data accumulation (See VA BIM Standard Appendix 3) in Excel format. |  | P | F
G-2.8 | Report |  |  | Certification of integrity of space reservations |  | Provide certification that no space reservations have been encroached upon at completion of CDs. | P | U | F
G-2.9 | Report |  |  | Model Compliance Report QA/QC Report |  | Submit a QA/QC report that certifies the models are compliant with VA BIM Standard and the project requirements. | P | U | F
G-2.10 |  |  | Drawing/Model Deliverables |  |  | Files formats as described in VA BIM Standard
G-2.11 | Report |  |  | Laser Scans |  | See VA BIM Standard Deliverables | F | R | R
G-2.12 | Drawings |  |  | Blocking and Stacking, Phasing |  | See VA BIM Standard Deliverables | F | R | R
G-2.13 | Report |  |  | FM Data |  | Excel / COBie format. | P | U | F
G-2.14 | Drawings |  |  | Design-Intent Drawings |  | Design-Intent Drawings (derived from Model) | P | U | F
G-2.15 | Drawings |  |  | Design-Intent Model(s) |  | Native Format, NWD (or Equal); DWG, digital 2D PDF | P | U | F
G-2.16 | Drawings |  |  | Signed and Sealed Models and Drawings |  | Final Models and Drawings shall be signed and sealed by a professional AE licensed in the geographic jurisdiction of the project. |  |  | F
G-2.17 | Drawings |  | Final Deliverables
G-2.18 | Drawings |  |  | As-Built Drawings |  | Provide Prior to Beneficial Occupancy.
G-2.19 | Drawings |  |  | FM Model |  | Provide Prior to Before Beneficial Occupancy.
G-2.20 | Report |  |  | Linking Electronic Files for Building Equipment/Systems |  | Linked and uploaded to Maximo to be provide prior to Beneficial Occupancy.
G-2.21 | Report |  |  | FM Data |  | Final upload to Maximo with AE supplied BIM viewer to be provided prior to Beneficial Occupancy.
G-3.0 |  | SPECIFICATIONS
G-3.1 | Report |  | Outline |  |  | Submit hyperlinked Table of Contents of applicable specification sections. Provide outline specification sections for building exterior materials and typical interior materials, using the “Track Changes” function. | P | U | F
G-3.2 | Report |  |  |  |  | Submit outline specifications for all disciplines using “Track Changes” function. At Interim 2 provide Outline Specifications. Lists all proposed specifications to be used and identify any special specifications required for the project. | F | R | R
G-3.3 | Report |  |  |  |  | Specifications for all technical disciplines shall be prepared using VA Master Construction Specifications. Where subsystems are performance specified, ensure that adequate design parameters are provided on drawings and/or specifications, that design responsibility (e.g. subsystem design by subcontractor's engineer) is clearly delineated, and that required submittals allow for review of subsystem design before fabrication. Submissions shall show changes to master by using "Track Changes" function. The Final submission shall not show changes. | P | U | F
G-3.4 | Report |  |  |  |  | Prepare specifications that define the contractor's responsibility for BIM deliverables as outlined in the VA BIM STANDARDS, including Construction Coordination activities. | P | U | F
G-3.5 | Report |  |  |  |  | Submit fully coordinated documents with other design disciplines for approval by Authorities Having Jurisdiction. The specifications should be considered 100% complete with no additional coordination or information required. |  |  | F
G-3.6 | Report |  |  |  |  | Provide Final Project Manual with signature and seal of architect of record on the cover. |  |  | F
G-4.0 |  | CRITICAL PATH METHOD
G-4.1 | Report |  | Construction Phasing Plan |  |  | Include phasing narrative in the Basis of Design for the final submission. | P | U | F
G-4.2 | [5 empty] | Provide phasing plans and 4D BIM. Coordinate with Architecture. | P | U | F
G-4.3 | Drawings |  |  |  |  | Provide CPM Phasing Plan diagram (see CPM Design manual in TIL). | P | U | F
G-4.4 | Drawings |  |  |  |  | Written list and drawings of systems, organized by technical disciplines, including temporary systems, swing spaces, etc. by phase. | P | U | F
G-4.5 | Aggregate |  | Concept Master Schedule Analysis |  |  | Prepare a schedule analysis showing the durations and impact of changes to the Overall Master Schedule prepared during Project Book. | P | U | F
G-4.6 | Aggregate |  | Project Master Schedule |  |  | Create a Project CPM Schedule based on the proposed design. Identify conditions that influence the Project Schedule, including site conditions that require mitigation, availability of utilities and roadways, and approvals from regulatory agencies (historic, environmental, and other permitting agencies). Project Schedule must identify major design activities, procurement phase activities and construction phasing sequence with major milestones, and VAMC overlapping activation phase. Identify CPM and Risk Analysis Consultants. Crosscheck CPM schedule with estimating consultant for cost escalation. | P | U | F
G-4.7 | Aggregate |  | Overall Construction Schedule |  |  | Submit Construction Schedule showing more details than Project schedule milestones, including phasing sequence, Long lead items and major trade work etc. This schedule shall be in cost-loaded CPM format with interrelationships. between activities and shall also be used as a basis for monthly payments. Provide schedule in Primavera P6 (preferred) or MS Project. | P | U | F
G-4.8 | Aggregate |  | Detail Design Schedule |  |  | Submit Detailed Design CPM Schedule identifying major activities, submissions, and milestones. Show activities for each design package and primary design discipline. At a minimum, include architectural, structural, mechanical, electrical, fire protection and life safety, plumbing, civil, and physical security. This schedule shall be in cost-loaded CPM format with interrelationships. between activities and shall also be used as a basis for monthly payments. Provide schedule in Primavera P6 (preferred) or MS Project. | P | U | F
G-4.9 | Report |  | Risk Management Plan |  |  | Submit risk management plan, identify SMEs and methodology on how to execute the plan. Submit Analysis in a narrative format which shall identify schedule risk areas and recommend actions to mitigate identified risks. | P | U | F
G-4.10 | Report |  | Schedule Risk Analysis |  |  | Submit Schedule Risk Analysis Report based on CPM for detailed design and anticipated overall construction and activation schedule. | P | U | F
G-4.11 | Report |  | Project Risk Register |  |  | Submit a Project Risk Register that has been approved by VA in a timely manner (monthly or as required by VA PM) covering all impacted disciplines. | P | U | F
G-5.0 |  | COMMISSIONING |  |  |  | A/E must coordinate with the commissioning team for the following deliverables:
G-5.1 | Report |  |  |  |  | Provide the Commissioning Plan (Cx Plan) coordinated with AE's Basis of Design (BOD), VA’s Project Requirements, and list of systems, components, and features to be commissioned. Include required documentation and schedule for implementation. See Commissioning Process Manual on the TIL. | P | U | F
G-5.2 | Report |  |  |  |  | Identify commissioning team and team organization. Include team member roles and responsibilities, and lines of communication. | F | R | R
G-5.3 | Report |  |  |  |  | Submit the updated narrative Basis of Design (BOD) report including Commissioning Agent's (CxA) report of document review and statement indicating how each of the items in the report shall be or has been addressed. | P | U | F
G-5.4 | Report |  |  |  |  | Identify major concerns that could affect operations, maintenance, or testing in the design phase commissioning Issues log with proposed resolution/mitigation. Identify discrepancies between Governmental Project Requirements and design narrative. Update design schedule and key milestones and roster of Commissioning Team members. At final submission verify that discrepancies between OPR and design narrative have been resolved. | P | U | F
G-5.5 | Report |  |  |  |  | Provide a Construction and Post-Construction Phase Commissioning Plan, including systems to be commissioned, an outline of construction phase roles and responsibilities, and an outline of required system documentation requirements. | P | U | F
G-5.6 | Report |  |  |  |  | Provide a report on selected control system types, configuration, and capabilities together with key decisions about equipment and systems sequences of operation. | P | U | F
G-5.7 | Report |  |  |  |  | Review technical sections of the specifications to coordinate O&M manual requirements. |  | P | F
G-5.8 | Report |  |  |  |  | Provide description of appropriate training and demonstration requirements for VA’s personnel. Include complete list of all types of equipment/systems and what Training and Demonstration is required. |  | P | F
G-5.9 | Report |  |  |  |  | Submit an updated Basis of Design (BOD) including Commissioning Agent's (CxA) report of document review and statement indicating how each of the items in the report shall be or has been addressed. | P | U | F
G-5.10 | Report |  |  |  |  | Provide a design phase commissioning issues Log with proposed resolution/mitigation. Identify major concerns that could affect operations, maintenance, or testing. Identify discrepancies between Owners Project Requirements and design narrative. Update design schedule and key milestones and roster of Commissioning Team members. At final submission verify that discrepancies between OPR and Design Narrative have been resolved. | P | U | F
G-5.11 | Report |  |  |  |  | Provide description of appropriate training and demonstration requirements for Government personnel. Include complete list of all types of equipment/systems and what Training and Demonstration is required. |  | P | F
G-5.12 | Report |  |  |  |  | Provide preliminary commissioning schedule, inclusive of design phase commissioning schedule and duration schedule for commissioning activities during construction phase commissioning. | P | U | F
G-5.13 | Report |  |  |  |  | For phased construction, coordinate with AE and owner representatives to identify all commissioning requirements within each phase, including required temporary systems. | P | U | F
G-5-14 | Report |  |  |  |  | Provide Commissioning specifications. See Commissioning specifications on the TIL. | P | U | F
G-5-15 | Report |  |  |  |  | Coordinate with AE and owner representatives and identify ALL third party testing. Incorporate third party testing in the Cx Plan and identify all required participants during testing. | P | U | F
VA SMEs
| Michael Koch |  |  |  | Michael.Koch3@va.gov | General
| Elizibeth Yo |  |  |  | Elizabeth.Yo@va.gov | BIM
| Ron Johnson |  |  |  | Ronald.D.Johnson@va.gov | Specifications
| Mo Ghorbanpour |  |  |  | Mo.Ghorbanpour@va.gov | CPM
| Michael Koch |  |  |  | Michael.Koch3@va.gov | Cx

## Structural
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | STRUCTURAL |  |  |  |  | VA submission requirements for Structural Design
S-1.0 |  |  | BASIS OF DESIGN
S-1.1 | Report |  |  | Narrative |  |  | Provide calculations and written description of the structural systems for the proposed design. Provide written descriptions of the basic structural systems to be used for foundations, substructure, superstructure, provisions for progressive collapse, and lateral force resisting system. | P | F | R
S-1.2 | Report | [5 empty] | For renovation/addition projects describe existing structural system and strategies for extending, modifying, enhancing the system. Discuss/show whether or not existing structural system meets code provisions that preclude upgrading the existing structural system to meet current code. | P | F | R
S-1.3 | Report | [5 empty] | Where necessary, provide mitigation of groundwater penetration. Include discussion of unknown conditions and potential risks involved in preliminary assumptions or site conditions that may impact construction. | P | F | R
S-1.4 | Report |  |  | Geotech Investigations |  |  | Submit plan to perform subsurface exploration and laboratory testing in the area of any proposed construction. Explain technical issues to be resolved, field and laboratory methods to be used, estimated number and depths of borings and other field methods, estimated laboratory testing, and reporting methods. | P | F | R
S-1.5 | Report | [5 empty] | Indicate whether special geotechnical investigation procedures, e.g. Shear Wave Velocity Measurements and/or Site Specific Study, need to be required for the determination of the more accurate Site Class required to assign Seismic Design Category. Coordinate with Geotechnical / Civil Engineer. | P | F | R
S-1.6 | Report | [5 empty] | Investigation methods shall be tailored to the needs of the specific project. | F | R | R
S-1.7 | Report | [5 empty] | Ground water conditions shall be investigated for each building, including significant excavations greater than 15 feet. This shall include the installation and monitoring of observation wells. When required, monitoring shall continue for at least six months to give an indication of seasonal fluctuation. | P | F | R
S-1.8 | Report | [5 empty] | Provide detailed work plan, which shall include the results of previous investigations relevant to the project. | F | R | R
S-1.9 | Report | [5 empty] | The final geotechnical report shall include resolution of all comments. Investigation methods shall be tailored to the needs of the specific project. | F | R | R
S-1.10 | Report |  |  | Blast Load Analysis and Design |  |  | Blast Basis of Design (BOD) shall provide analysis and design recommendations for building façade and screen elements including curtain walls and windows, and their connections to the supporting structural elements. These design recommendations shall be developed by close coordination between the Blast Consultant and the Structural Engineer of Record to include locations of connections of building facade elements to supporting structure along with the required connection capacities with some “vendor tolerance factor” accounting for some differences between supplier products. The contractor’s delegated design curtain wall system shall not exceed these specified maximum reactions. | P | U | F
S-2.0 |  |  | CODE ANALYSIS
S-2.1 | Report | [5 empty] | Describe the Building Structural Performance Design Criteria. | F | R | R
S-2.2 | Report | [5 empty] | Provide written description of design philosophy for the design of progressive collapse, blast, and natural disaster. | P | F | R
S-2.3 | Report | [5 empty] | Identify pre-fabricated structural items (such as pre-engineered metal buildings, precast concrete panels) and other items (Such as building facades, screens etc., that are to be protected against blast loadings) where design is delegated to others. Address design responsibilities related to the designer of record and portions of the design that is being delegated to others. | P | U | F
S-2.4 | Report | [5 empty] | State the fire resistance criteria for all portions of the structural system. | P | U | F
S-2.5 | Report | [5 empty] | In close coordination with the mechanical and electrical disciplines, identify equipment that are required to have Special Seismic Certification in accordance with the RFP. Please see VA H 18-8, Seismic Design Requirements, for a "List of Equipment and Components Typically Requiring Special Seismic Certification" for guidance. | P | U | F
S-3.0 |  |  | STRUCTURAL TYPE
S-3.1 | Report |  |  | Concrete |  |  | Describe basic material properties for concrete to be used, including compressive strength, entrained air content, maximum aggregate size, allowable water/cement ratio, unit weight or aggregate type, and anticipated admixtures. Potential for fly ash or other suitable cement replacement substitution. Concrete mixtures to be used for footings, foundations walls, slab on grade, elevated slabs, superstructure columns and beams, roof slabs. For rebar, identify bar and welded wire fabric. ASTM material designation for the rebar to be used. Indicate the anticipated uses and locations for special rebar types (epoxy coated, galvanized, and high strength). Determine floor flatness requirements. | P | U | F
S-3.2 | Report |  |  | Structural Steel |  |  | Indicate ASTM material designation for the steel to be used for each of the following items: steel columns, steel beams, base plates, built-up beams or girders, steel truss chord members, and lateral bracing system. Itemize by American Institute of Steel Construction (AISC) shape as applicable, including material types and sizes. Provide diameter, ASTM material designation, and finish for the typical bolt assembly, including nuts, washers, and bolts. List of the locations where slip-critical bolts are anticipated. Submit the test method to be used to verify the bolt tension in the slip-critical connections. List project welding materials. Provide type of base plate/anchor rod assemblies. Priming/painting of steel members including materials, locations, and slip coefficients. | P | U | F
S-3.3 | Report |  |  |  | Steel Deck |  | Provide basic information on the anticipated steel decking to be used, including profile and depth, ASTM material designation, span condition, finishes and coatings, and method of attachment. Define required shoring. Deflection criteria to be considered. | P | U | F
S-3.4 | Report |  |  | Masonry |  |  | Indicate ASTM International (ASTM) designations for typical Concrete Masonry Units (CMU), types of mortar, and lintel materials, ties, and anchors to be used. Define masonry tolerances. | P | U | F
S-3.5 | Report |  |  | Wood and Engineered Wood Products |  |  | Indicate grade and species for all anticipated wood framing products. Engineering design requirements for engineered wood products. Define typical spacing for framing members. Define special treatment requirements (such as pressure treated and fire resistive). Requirements for wood sheet goods (oriented strand board (OSB), plywood), thicknesses, and locations for use (roof deck, floor deck, exterior sheathing). | P | U | F
S-4.0 |  |  | CALCULATIONS
S-4.1 | Calculations |  |  | Structural Analysis |  |  | Submit calculations covering all parts of the structure and miscellaneous facilities. Provide copies of input data and output summaries, accompanied by diagrams that identify joints, members, and areas, according to the notations used in the data listings. Calculations shall include: | P | U | F
S-4.2 | Calculations | [5 empty] | Gravity load and lateral loads for the majority of the framing members | P | U | F
S-4.3 | Calculations | [5 empty] | Foundations | P | U | F
S-4.4 | Calculations | [5 empty] | Primary structural members | P | U | F
S-4.5 | Calculations | [5 empty] | Vibrations | P | U | F
S-4.6 | Calculations | [5 empty] | Seismic | P | U | F
S-4.7 | Calculations | [5 empty] | Progressive collapse, local conditions, and blast design. | P | U | F
S-4.8 | Calculations | [5 empty] | Adequacy of existing structure, where applicable, to account for new functional loads or new criteria. | P | U | F
S-4.9 | Calculations |  |  | Calculation Sheets |  |  | Final calculations shall be indexed, sealed, and signed by the engineer whose name appears on the Design Calculations index. Observe the following guidelines: |  |  | F
S-4.10 | Calculations | [5 empty] | State assumptions and design criteria prior to the presentation of the calculations. | P | U | F
S-4.11 | Calculations | [5 empty] | Provide calculations to verify sizes, bolts, and welds with all details. Connection design may be provided by steel fabricator's engineer in regions where this is standard practice. Refer to AISC Code of Standard Practice requirements for connection information to be shown on documents where design is delegated. |  | P | F
S-4.12 | Calculations | [5 empty] | Sketches used to describe the basis of calculations shall be drawn to approximate proportions. |  | P | F
S-4.13 | Aggregate |  | Special Inspections |  |  |  | Include all Special Inspections in accordance with PG 18-1 Section 01-45-35. | P | U | F
S-5.0 | Drawings |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and as noted below
S-5.1 | Drawings | [5 empty] | Provide drawings of the preferred structural system at the smallest scale that can clearly illustrate the concept ((minimum 1/16” =1’0” (1:200) for larger buildings and 1/8”=1’-0” (1:100) for smaller buildings)). The A/E and VA PM need to concur on drawing scale for the submission. | P | F | R
S-5.2 | Drawings | [5 empty] | Indicate foundation system including walls, footing, and pile locations. | P | F | R
S-5.3 | Drawings | [5 empty] | Indicate floor and roof framing system, including column, beam, and girder locations. Indicate lateral bracing system on the layout. | P | F | R
S-5.4 | Drawings |  |  | General |  |  | Submit the following at a minimum of 1/8” = 1’0” (3.1750 mm) scale drawings showing the selected structural systems, typical details showing relationship of structure with architectural and mechanical features, new and existing construction features, general notes, abbreviations, legends, key notes, symbol keys, key plans, column lines, north arrow, and coordinated backgrounds as per Drawing Deliverable Requirements (DDR). | P | U | F
S-5.5 | Drawings |  |  | Deep Foundation
S-5.6 | Drawings | [5 empty] | Indicate number, cap size, and size of deep foundation members (pile, pier or caisson) at each location. Indicate the design depth (tip or bottom of elevation) for bidding purposes. | P | F | R
S-5.7 | Drawings | [5 empty] | Indicate final number and size of deep foundation members at each location. Indicate the design depth (tip or bottom of pile, pier or caisson elevation) of each deep foundation member for bidding purposes. | P | F | R
S-5.8 | Drawings | [5 empty] | Locate test pile, pier, or caisson locations where uplift resistance is critical and geotechnical engineer wants verification of performance. | P | F | R
S-5.9 | Drawings | [5 empty] | Indicate completed pile, pier or caisson cap schedule including top of cap elevations, reinforcing, and anchorage. |  | P | F
S-5.10 | Drawings | [5 empty] | Provide tie-beam information including size, reinforcing, clearances and connection details to pile, pier or caisson caps. |  | P | F
S-5.11 | Drawings |  |  | Foundation System |  |  | Indicate on the foundation plans the following:
S-5.12 | Drawings | [5 empty] | Wall and slab-on-grade thickness | P | U | F
S-5.13 | Drawings | [5 empty] | Brick shelf locations | P | U | F
S-5.14 | Drawings | [5 empty] | Slab-on-grade construction | P | U | F
S-5.15 | Drawings | [5 empty] | Footing steps and elevator pits | P | U | F
S-5.16 | Drawings | [5 empty] | Waterproofing and water stop systems; Provide to the extend needed to coordinate with Architectural requirements | P | U | F
S-5.17 | Drawings | [5 empty] | Provide footing schedule on drawings. | P | U | F
S-5.18 | Drawings |  |  | Expansion Joints |  |  | All building expansion joints. Show foundation wall and slab-on-grade construction and control joints. | P | F | R
S-5.19 | Drawings |  |  | Concrete Foundation/Framing Drawings |  |  | Concrete superstructure showing beams, columns, piers, and elevated slabs with locations and sizes/thicknesses, and reinforcing. | P | U | F
S-5.20 | Drawings |  |  |  | Typical Details |  | Typical details for concrete footings, beams, columns, slabs, and walls as required for the project; Include only details that apply to the scope of work. | P | U | F
S-5.21 | Drawings |  |  |  | Slab |  | Completed concrete column, beam, pilaster, and footing schedules. Indicate information for concrete slab construction including: | P | U | F
S-5.22 | Drawings | [5 empty] | Slab joint pattern for concrete slabs-on-grade. | P | U | F
S-5.23 | Drawings | [5 empty] | Slab thickness and top of slab elevations. | P | F | R
S-5.24 | Drawings | [5 empty] | Slab reinforcing including sizes, spacing, placement, and clearances. | P | U | F
S-5.25 | Drawings | [5 empty] | Typical slab construction details, including construction and control joint details, typical details at slab-column isolation joints, slab-wall joint details. | P | U | F
S-5.26 | Drawings | [5 empty] | Indicate all changes in slab elevations, including depressions and pits, and sump pits at the bottom of all elevator pits. |  | P | F
S-5.27 | Drawings | [5 empty] | Indicate all sloped slab locations with both beginning and ending slope elevations. |  | P | F
S-5.28 | Drawings |  |  |  | Continuous and Isolated Footings |  | Footing sizes, locations, and top of footing elevations. | P | U | F
S-5.29 | Drawings | [5 empty] | Footing reinforcing sizes, spacing, and clearances. | P | U | F
S-5.30 | Drawings | [5 empty] | Required keyways and dowels. | P | U | F
S-5.31 | Drawings |  |  |  | Building Structural Walls |  | Elevation at top of wall. | P | P | F
S-5.32 | Drawings | [5 empty] | Elevation at top of brick shelf or other supports. | P | U | F
S-5.33 | Drawings | [5 empty] | Elevation at beam pockets and changes in wall heights. | P | U | F
S-5.34 | Drawings | [5 empty] | Dimension of wall thickness and dimension to column lines. | P | U | F
S-5.35 | Drawings | [5 empty] | Wall reinforcing size, direction, spacing, and clearances. | P | U | F
S-5.36 | Drawings | [5 empty] | Integral pier or pilaster size, location, reinforcing, and elevation. | P | U | F
S-5.37 | Drawings | [5 empty] | Wall penetrations including size, locations, and additional reinforcing. | P | U | F
S-5.38 | Drawings | [5 empty] | Locations and details for embedded items such as connection plates or anchors. | P | U | F
S-5.39 | Drawings | [5 empty] | Coordinate and indicate waterproofing and water stop systems shown on the architectural drawings. | P | U | F
S-5.40 | Drawings |  |  | Structural Steel Superstructure |  |  | All columns and beams. | P | U | F
S-5.41 | Drawings | [5 empty] | Column sizes and orientation. | P | U | F
S-5.42 | Drawings | [5 empty] | Beam sizes. | P | U | F
S-5.43 | Drawings | [5 empty] | Lateral bracing system. | P | U | F
S-5.44 | Drawings | [5 empty] | Connection moments, vertical, and lateral loads. Detailed design may be provided by steel fabricator's engineer in regions where this is standard practice. Refer to AISC Code of Standard Practice requirements for connection information to be shown on documents where design is delegated. | P | U | F
S-5.45 | Drawings | [5 empty] | Column schedule. | P | U | F
S-5.46 | Drawings | [5 empty] | Base plates, anchor bolts, rods, hardware, and pattern. | P | U | F
S-5.47 | Drawings | [5 empty] | Steel beam camber. | P | U | F
S-5.48 | Drawings | [5 empty] | Shear stud type and length. | P | U | F
S-5.49 | Drawings | [5 empty] | Approximate locations and support for major mechanical equipment. Identify and label equipment and weights over 1,000 lbs. on MEP drawings. | P | U | F
S-5.50 | Drawings |  |  | Steel Faming Drawings |  |  | Steel framing member sizes. Include all shear stud and camber information for floor framing members. | P | U | F
S-5.51 | Drawings | [5 empty] | Connection design loads including vertical reactions and design moments for moment connections Detailed design may be provided by steel fabricator's engineer in regions where this is standard practice. Refer to AISC Code of Standard Practice requirements for connection information to be shown on documents where design is delegated. | P | U | F
S-5.52 | Drawings | [5 empty] | Column orientation on framing plans. | P | U | F
S-5.53 | Drawings | [5 empty] | Locations requiring the installation of slip-critical bolts. | P | U | F
S-5.54 | Drawings | [5 empty] | Bridging and bracing member sizes, locations, and connections. | P | U | F
S-5.55 | Drawings | [5 empty] | Metal decking sizes, span criteria, and direction. | P | U | F
S-5.56 | Drawings | [5 empty] | Relevant typical details. Include only details that apply to the project. | P | U | F
S-5.57 | Drawings | [5 empty] | Complete column schedule, including member sizes, splice locations and types, base plate sizes and orientation, and column loads and heights. | P | U | F
S-5.58 | Drawings | [5 empty] | Non-typical or non-standard connection details. | P | U | F
S-5.59 | Drawings | [5 empty] | Lintels (loose and attached) and support angles. | P | U | F
S-5.60 | Drawings |  |  | Elevated Slab-On-Deck |  |  | Slab thickness and typical reinforcing. | P | U | F
S-5.61 | Drawings | [5 empty] | Changes in top-of-slab elevation. | P | U | F
S-5.62 | Drawings | [5 empty] | Verification that thickness is coordinated with fire-rating requirements. | P | U | F
S-5.63 | Drawings | [5 empty] | Slab flatness requirements. | P | U | F
S-5.64 | Drawings |  |  | Masonry Drawings |  |  | Typical masonry reinforcing and spacing requirements for load bearing walls. Assist the architect in reinforcing and spacing requirements for load non-bearing walls shown on architectural drawings. | P | U | F
S-5.65 | Drawings | [5 empty] | Masonry seismic anchorage and lateral support requirements. | P | U | F
S-5.66 | Drawings | [5 empty] | Indicate masonry bond beam requirements. | P | U | F
S-5.67 | Drawings |  |  | Other |  |  | Seismic design. | P | U | F
S-5.68 | Drawings | [5 empty] | Indicate progressive collapse prevention and blast load design (if required). | P | U | F
VA SME
| Juan Archilla |  |  |  |  | Juan.Archilla@va.gov
| Asok Ghosh |  |  |  |  | Asok.Ghosh@va.gov

## Architectural
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | ARCHITECTURAL |  |  |  |  | VA submission requirements for Architectural Design
A--1.0 |  |  | BASIS OF DESIGN
A-1.1 | Report |  |  | Narrative |  |  | Narrative establishing project goals, and objectives. | F | R | R
A-1.2 | Report |  |  |  | Quantities |  | Types and quantity of Architectural Significant Equipment (ASE) to be accommodated (linear accelerator, imaging, laundry, food service, etc.). | P | U | F
A-1.3 | Report |  |  |  | Concept of Operations |  | Update the VA provided Concept of Operations and finalize as the Functional Operations Manual. | P | U | F
A-1.4 | Report | [5 empty] | Provide functional (medical) and physical design program. | F | R | R
A-1.5 | Report | [5 empty] | Provide adjacency matrix for major services. | F | R | R
A-1.6 | Report |  |  |  | Code Analysis |  | Coordinate with Fire Protection. Provide a detailed listing of all applicable codes for the project, construction type, design criteria, and national standards affecting the design to ensure that the proposed design complies with the RFP, applicable regulations, codes, and standards referenced in VA handbooks, design manuals, and standards. Include title, year and publishing organization for each code/standard indicated. Provide description of Structural Design Loading Information (include criteria and reference source.) | P | F | R
A-1.7 |  |  |  |  | Code Compliance |  | Evaluate and report in the Narratives the proposed design for Code Compliance. | P | U | F
A-1.8 | Report |  |  |  | Phasing |  | Provide analysis of implementation strategies, phasing, and sequencing considerations. | P | U | F
A-1.9 | Report |  |  |  | Thermal Envelope |  | Identify and analyze all exterior enclosure elements for compatibility and compliance to energy standards, climatic requirements, and extreme weather events. | P | U | F
A-1.10 | Report |  |  |  | Seismically Restrained |  | Describe seismic constraints needed for casework, equipment, and furniture. |  | P | F
A-1.11 | Report |  |  |  | Interstitial Study - VAHBS |  | Provide report, analysis, and budgetary impacts to incorporate the VA Hospital Building System (VAHBS) including areas where interstitial space can best be utilized. | F | R | R
A-1.12 | Report |  |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  | Analyze impact of seismic correction plan on existing functional layout. Determine minimal acceptable changes necessary to implement seismic corrections. | P | F | R
A-2.0 |  |  | SPACE PLANNING
A-2.1 | Report |  |  | Narrative |  |  | Submit a narrative Basis of Design (BOD) report. This must be updated at each design submission showing all previous submission totals and deltas. Highlight all deviations from previous report. Report to include: | P | U | F
A-2.2 | Report |  |  | Area Summary |  |  | Provide a summary of net and gross area comparing the SEPS PFD baseline to the proposed design. The space summaries shall be extracted from BIM. Include room and departmental NSF, conversion factor used, departmental gross (DGSF), and building GSF, highlighting all deltas. Submit in tabular form with subtotal for each room type, department, and common areas such as lobbies, service areas, cafeteria, Mechanical/Electrical equipment, basic circulation, canteen, FMS and OI&T telecommunications, etc. This must be updated at each design submission showing all previous submission totals and deltas. All modifications to the PFD require approval from VA MC, the VA Project Manager, and VACO CFM. | P | U | F
A-2.3 | Report |  |  | Building Summary |  |  | Summarize building(s) metrics in tabular form: building(s) height, BGSF by floor and total, number of patient rooms, patient beds by floor, and building occupancy type(s). | P | U | F
A-2.4 | Report |  |  | Transportation and Logistics Studies |  |  | Provide a logistics strategy (staging, processing, vertical and horizontal transportation systems, material handling, staffing peaks, travel distances egress). Determine if proposed strategies impact project scope and identify opportunities for sharing services within the facility or with other facilities. Refer to PG 18-3, Topic 18. | P | U | F
A-2.5 | Aggregate |  |  | Expansion |  |  | Plan for 25% expansion capability, vertical or horizontal or a combination, representing a rational prospect following contemporary healthcare planning trends and projections . Include specific departmental direction/requirements for expansion for patient services (such as clinics and outpatient surgery), program support services (such as diagnostic imaging and sterile processing) and facility support services (such as engineering and housekeeping); and assure utility infrastructure connections at the point of expansion are adequate. | P | U | F
A-2.6 | Aggregate |  |  | BIM Interactive Reviews |  |  | Provide live BIM review of the design, access, and space reservations of major MEPFT equipment/distribution systems. Refer to the VA BIM Manual. Provide a key plan identifying location and direction of rendered view. Provide fit-for-purpose views demonstrating how the design meets functionality requirements. | P | U | F
A-2.7 | Aggregate |  |  | Fit for Purpose Design Verification |  |  | Provide design validation as described in the VA BIM STANDARD. | P | U | F
A-2.8 | Drawings |  |  | Visually Monitored Spaces |  |  | Provide BIM camera views for Visually Monitored Spaces as noted in the VA BIM STANDARD. Include PACU, Lobby, Clinic Reception & Waiting, Exterior views as design progresses & critical design elements. | P | U | F
A-2.9 | Drawings |  |  | Communicating the Design Aesthetic |  |  | Provide rendered visualizations as noted in the VA BIM STANDARD. Include colored images with basic materials, lighting and shades of (1) Aerial view showing facility campus, showing arrival approach to facility at eye level of patient (car/wheelchair); (2) Drop-off entry to facility and lobby at eye level (patient car/walking/wheelchair); (3) Kiosk and registration areas at eye level (walking wheelchair); (4) Other views as necessary to present the solution. | P | U | F
A-2.10 | Drawings |  |  | Swing Space/Design and Construction Phasing Plan (4D) |  |  | Provide a 3D/4D communication plan for swing space and sequence of work. Indicate construction barriers/fences, proposed laydown space and operational logistics. Refer to the VA BIM STANDARD. | P | U | F
A-3.0 |  |  | ROOM DATA SHEETS |  |  |  | Electronic 2D PDFs (minimum scale 1/4" = 1"-0" (1:50) linked to the plan sets as per the requirements in the DDR.
A-3.1 | Drawings | [5 empty] | Provide the proposed layouts for complex procedure rooms, patient rooms, typical exam room(s) on enlarged Architectural project-specific floor plans identifying the critical dimensions and equipment for the project that has been exported from SEPS. Room Data Sheets for typical room types include: | P | U | F
A-3.2 | Drawings | [5 empty] | JSN, Room Codes, and other information as described in the BIM Standards for coding. | P | U | F
A-3.3 | Drawings | [5 empty] | Minimum room dimensions and clearances. | P | U | F
A-3.4 | Drawings | [5 empty] | Door size and special requirements (fire rating, vision panel, finish hardware, access control, etc.) | P | U | F
A-3.5 | Drawings | [5 empty] | Wall types (fire ratings, shielding, acoustic, etc.). | P | U | F
A-3.6 | Drawings | [5 empty] | Architectural casework configuration and location. | P | U | F
A-3.7 | Drawings | [5 empty] | Special features such as humidity control, eye wash, lighting. | P | U | F
A-3.8 | Drawings | [5 empty] | Locker quantities and type. | P | U | F
A-3.9 | Drawings | [5 empty] | Structural requirements for both room and equipment. | P | U | F
A-3.10 | Drawings | [5 empty] | HVAC requirements for both room and equipment. | P | U | F
A-3.11 | Drawings | [5 empty] | Room Finishes. | P | U | F
A-3.12 | Drawings | [5 empty] | Reflected ceiling plans for project specific rooms, complex and typical. | P | U | F
A-3.13 | Drawings | [5 empty] | Depict normal, emergency, isolated and UPS requirements. Show lighting, medical gases, plumbing fixtures and controls, data connections, all communication systems (telephone, nurse call, PA, intercom, Wi-Fi). | P | U | F
A-3.14 | Drawings | [5 empty] | Equipment (fixed and movable) with rough-in requirements; Verify space needs for functional use. Identify equipment by VA Acquisition Code and denote ASE. Coordinate information provided by the equipment planner. Coordinate information provided by the equipment planner, interior designer and food service planner as required. | P | U | F
A-4.0 |  |  | ARCHITECTURAL DRAWING DELIVERABLES |  |  |  | Follow the requirements in the DDR, the VA BIM STANDARD and as noted below.
A-4.1 | Drawings |  |  | Title/Cover Sheet(s) |  |  | Cover Sheets: project name and address, VA project number, location map, signature block, name and address of VA, architect, engineers, and other consultants; Project Data with index of drawings, legend of abbreviations and symbols; Project Codes and Standards Sheet with a list and summary of the applicable project codes, applicable VA Standard Manuals and Guides by name and issuance date. | P | U | F
A-4.2 | Drawings |  |  | Site Plans |  |  | Provide a site plan (min. 1"=30.0') indicating demolition, building location, parking, pedestrian and vehicular circulation, emergency vehicle access, loading docks, and all other major landforms and site features. (Coordinate with Civil Engineering discipline). | P | U | F
A-4.3 | Drawings |  |  | Demolition Plans |  |  | Demolition floor and ceiling plans for areas to be renovated and areas below where work in space below is required (minimum 1/8"=1'-0" (1:100) with finish schedule and wall types. Coordinate with phasing plans, Interim Life Safety Measures (ILSM) and Infection Control Risk Assessment (ICRA). Describe compliance with VA FPDM Section 1.4. | P | U | F
A-4.4 | Drawings |  |  | Floor Plans |  |  | Provide floor plans showing departmental adjacencies, major circulation routes and layouts for each floor, including interstitial floors, showing internal organization of each department, vertical and horizontal circulation, location of mechanical and electrical equipment rooms, utility shafts, patient and staff entrance, receiving/shipping, and location of section cuts (minimum scale 1/16” =1’-0” (1:200). Included column centerline and overall building dimensions. Air Barrier System: air barrier system plans and details (i.e. window flashing details, penetration in air barrier details, door flashing details, roofing /ceiling barrier interface details). Coordinate with Civil Engineering discipline for finished floor of structures and flood zones. | P | U | F
A-4.5 | Drawings | [5 empty] | Provide floor plans identifying room square footages: Net Program / Net Actual in accordance with the RFP. | P | U | F
A-4.6 | Drawings | [5 empty] | With each submittal, update the Department Plans to show the programmed and as-planned DGSF amounts. | P | U | F
A-4.7 | Drawings | [5 empty] | Floor plans should identify partition types, sections cuts locations, interior and exterior elevation location, detail locations, large scale plan areas, interior vision panels, millwork, architectural casework, plumbing fixtures, major and fixed equipment. Equipment items must be identified by JSN on other drawings. Indicated proposed future expansion and include interior and exterior dimensions including general notes. Include fire extinguisher and fire hose connection cabinets as applicable. | P | U | F
A-4.8 | Drawings | [5 empty] | Identify project specific departmental areas for enhanced study thru enlarged plans to be submitted with SD 2. (e.g. surgery, SPS, nursing units, radiology, ED and Behavioral Health Department). | F | R | R
A-4.9 | Drawings | [5 empty] | Provide 1/8"=1'-0" (3.1750 mm) scale floor plans depicting travel distances from nurse station to patient room(s) and support room to patient room(s), work flow within SPS, surgery & other complex areas. | P | U | F
A-4.10 | Drawings | [5 empty] | Delineate on the drawings special conditions such as storage racks/shelving location, height and configuration (including mobile shelving); atria; open ceilings, or architecturally sensitive areas; audiometric booths; walk-in freezers and cold rooms; computer rooms and raised flooring; loading docks and exterior canopies; residential sleeping, patient lifts, air curtains at logistics, etc. which may have an impact on sprinkler design and installation. | P | U | F
A-4.11 | Drawings |  |  | Accessibility, ABA |  |  | Address compliance with the ABA (Architectural Barriers Act) Accessibility Standard for Federal Facilities, in accordance with VA FPDM Section 1.5. Provide ABA graphic annotation on drawings of door swing clearances both interior and exterior, fixture clearances (toilets, sinks, drinking fountains, push plates for doors, etc.) and turning space for all toilet and bathing facilities, dressing, fitting and locker rooms, patient bedrooms, etc. per ABA and PG 18-13 VA Barrier Free Design Standard. | P | U | F
A-4.12 | Drawings |  |  | ILSM/ICRA Plans |  |  | Provide Interim Life Safety Measures (ILSM) and Infection Control Risk Assessment (ICRA) drawings at minimum scale 1/8"=1'-0" (1:100). Construction Safety as required showing construction barriers/fences. Describe compliance with VA FPDM Section 1.4. ICRA/PCRA drawings should also show on drawings the following: risk matrix (type, patient group, class, etc.), temporary walls or barriers, sticky mats, negative air machines, egress routes, temporary exits, identify access points (staff, construction, etc.) debris routes, anterooms if applicable, monitors (manometer, laser particle, pressurization, etc.), area of work highlighted, etc. | P | U | F
A-4.13 | Drawings |  |  | Ceiling Plans |  |  | Reflected ceiling plans (architectural and MEP) at minimum scale 1/4"=1'-0" (1:50). Identify bulkheads, light fixtures, supply and return grilles, ceiling mounted equipment, exit signs, and other devices. Locate ceiling grid. Examples include speakers, telemetry antennas, nurse call lights, diffusers, access panels, etc. Coordinate with any ceiling or wall mounted signage/wayfinding and any overhead equipment movement/rotation limitations with possible interference or conflict. Provide ceiling sandwich section cuts of above ceiling conditions / pinch points and areas of high congested areas should be provided for coordination. | P | U | F
A-4.14 | Drawings |  |  | Roof Plans |  |  | Provide 1/8"=1'-0" (1:100) scale roof plans depicting all roof features (drains, overflows, slopes, crickets, ridges, valleys, penetrations, equipment, davits, walk pads, etc.). Indicate all green roof types and areas. | P | U | F
A-4.15 |  |  |  | Color Coded Departmental Plans |  |  | Submit floor plans color-coded by functional area. | P | U | F
A-4.16 | Drawings |  |  | Enlarged Floor Plans |  |  | Provide floor plans at 1/4"=1'-0" (1:50) scale for all specialty areas and medical unique (DVA Template specific - such as operating rooms, DTRs, patient rooms, exam rooms, toilet rooms, etc.). | P | U | F
A-4.17 | Drawings |  |  | Exterior Elevations |  |  | Provide building elevations at a minimum of 1/8"=1'-0" (1:100) with fenestration, penthouses, materials, finish floor elevations, floor-to-floor heights, overall building height, window and louver types, entrances, canopies, skylights, roof overflow/ downspout and adjacent grades. Include separate elevations indicating base building with expansion shown on floor plans. Show proposed future expansions (both vertical and horizontal) by dotted lines on site plans, architectural floor plans, engineering floor plans, and in elevations and sections. Provide location of future elevators (Patient, visitor, support) as well as circulation diagrams. Provide building elevations of complex areas at a minimum scale of 1/8"=1'-0" (1:100). | P | U | F
A-4.18 | Drawings |  |  | Building Sections |  |  | Provide building sections at minimum scale 1/16"=1'-0" (1:200) through major portions of building. | P | P | F
A-4.19 | Drawings |  |  | Wall Sections |  |  | Provide wall sections indicating floor-to-floor heights, overall building heights, materials, fenestrations, and assemblies. | P | P | F
A-4.20 | Drawings |  |  | Wall Types |  |  | Provide each wall type at minimum scale of 1"=1'-0" (1:10). Indicate acoustic and sound attenuation, shielding protection and fire ratings. Identify UL, STC or other acceptable testing agency design numbers. | P | P | F
A-4.21 | Drawings |  |  | Construction Details |  |  | Construction details at scale large enough to clearly show components and assembly: windows, storefront, waterproofing, roof accessories, equipment mounting and suspension shielding, etc. Provide 3D PDF details for all complex roof/wall/window interfaces and include in electronic 2D drawing sets. | P | P | F
A-4.22 | Drawings |  |  | Vertical Transit Plans & Details |  |  | Vertical transit details for stairs, elevators, lifts, dumbwaiters, linen and trash chutes, and pneumatic tube stations. Provide plans at minimum scale of 1/4"=1'-0" (1:50), sections and details at scale large enough to convey design intent. | P | U | F
A-4.23 | Drawings |  |  | Door Schedules |  |  | Door schedule with door and frame details, threshold details, door number, door and frame types, dimensions, ratings, materials, glazing, security requirements, and finish hardware. | P | U | F
A-4.24 | Drawings |  |  | Door Types |  |  | Provide graphical depiction of each door type. | P | U | F
A-4.25 | Drawings |  |  | Interior Elevations |  |  | Provide interior elevations at minimum scale of 1/4"=1'-0" (1:50) showing medical gases, power, data, communications, millwork, architectural casework, equipment and other built-in items. Identify PRC items by JSN and as noted in the VA BIM STANDARD. Dimension elements (outlets, switches, med gas, wall mounted equipment, etc.) both horizontal and vertical for installation and coordination. Provide enlarged details of headwalls and other critical elements (fully dimensioned) at scale large enough to convey design intent (1/2" = 1'-0" min). | P | U | F
A-4.26 | Drawings |  |  | Phasing Plans |  |  | Provide plans showing the phasing sequencing considerations etc. | P | U | F
A-4.27 | Drawings | [5 empty] | Within each department/function bounding show DGSF actual/program, highlighting all deltas, include FMS and OI&T telecommunications area (combined and separated). | P | U | F
A-5.0 |  |  | FM Data
A-5.1 | Report |  |  | COBie Format |  |  | Provide FM Data according to VA BIM STANDARD . |  | P | F
VA SME
| Michael Koch |  |  |  |  | Michael.Koch3@va.gov
| David Treece |  |  |  |  | David.Treece@va.gov

## FF&E
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | MEDICAL EQUIPMENT |  |  |  |  | VA submission requirements for Laboratory/Medical Casework and Food Service
Q-1.0 |  |  | BASIS OF DESIGN
Q-1.1 | Report |  |  | Project Equipment List |  |  | Provide design iteration equipment schedule export in spreadsheet (.xlsx, .csv) format. File shall include all coding in the SEPS BIM Excel Export file listed in the VA Spatial & Equipment Data Spreadsheet and attribute types (e.g., dimensions, cost, etc.) from SEPS with updated quantities and Department, Functional Area and Room data. Population of product specific information such as utilities, cost, etc. is optional (columns U thru AQ) for standard JSNs. Use the SEPS BIM Excel Export file to transfer information for equipment to BIM for room test fits. | P | F | R
Q-2.0 |  |  |  | Room by Room Equipment List |  |  | Provide room by room (RxR) listing in PDF format for all rooms in original PFD and/or subsequent room requirement revisions. RxR will include, at minimum, all equivalent data fields provided in the solicitation's Project Room Contents List. RxR should match equipment shown on Equipment Plans (drawings). | P | F | R
Cut Sheets
Q-3.0 | [6 empty] | Provide cut sheets for all equipment denoting Acquisition Code (CC, VC, VV) in .pdf format. Coordinate cut sheet submittal with other disciplines as required by the project. | P | F | R
Q-3.1 | Report | [5 empty] | Provide by JSN summary with Manufacturer and Model in spreadsheet format (.xls, .csv). | P | U | F
Q-4.0 |  |  |  | Equipment Plans |  |  | As per the VA BIM STANDARD and below.
Q-4.1 | Drawings | [5 empty] | Provide floor plans at 1/4"=1'-0" (1:50) minimum scale that graphically indicate locations and dimensions of proposed and existing equipment as listed in the Project Equipment List. Equipment plans shall reference the Room Data Sheets for typical rooms, and shall show all unique rooms with equipment layouts. All equipment shall be shown to fit into rooms and be usable. Assign utility codes to equipment as applicable. JSN shall identify all equipment and reference the Project Equipment List, cut sheets, and specifications. Project Equipment Lists shall not be shown on the plans, but shall be included in the specifications. VACO will identify areas during Interim 1 for over the shoulder reviews of select complex areas and repetitive room types at mid points during the Interim 2 phase. | P | U | F
Q-4.2 | Drawings |  |  |  | ASE |  | Provide floor plans at 1/4"=1'-0" (1:50) minimum scale that graphically indicate all locations for Architecturally Significant Equipment (ASE). Provide a list of rooms and ASE equipment in those rooms for coordination by the Contractor as per the VA BIM STANDARD. | P | U | F
Q-5.0 |  |  |  | Equipment Budget Estimate |  |  | Excel Spreadsheet
Q-5.1 | Report | [5 empty] | Provide an Equipment Budget Estimate categorized by Acquisition Codes VC and VV. | P | U | F
Q-6.0 |  |  |  | Activation Deliverables Package (Electronic Files) |  |  | All Digital Files provided to the Activation Team in the formats below
Q-6.1 | Drawings | [5 empty] | Equipment Floor plans at minimum scale of 1/4" - 1'-0" (1:50) with graphic depiction of room locations of all equipment: 1) Digital PDF; 2) DWG; 3) Native BIM file format. |  | P | F
Q-6.2 | Report | [5 empty] | Project Equipment List of all equipment and with separate category for ASE: 1) Digital PDF; 2) Excel; 3) Medical Center Web Based Equipment Program (if applicable). |  | P | F
Q-6.3 | Report | [5 empty] | Room Data Sheets: 1) Digital PDF; 2) DWG; 3) Native BIM file format. |  | P | F
Q-6.4 | Report | [5 empty] | Equipment Cut Sheets: 1) Digital PDF; 2) PDF. |  | P | F
Q-6.5 | Report | [5 empty] | Equipment Budget Estimate: 1) Digital PDF; 2) Excel. |  | P | F
|  | FOOD SERVICE EQUIPMENT |  |  |  |  | VA submission requirements for Food Service Equipment
FS-1.0 |  |  | BASIS OF DESIGN
FS-1.1 | Report |  |  | Food Service Equipment List |  |  | Submit the refined Food Service equipment list as part of the Project Equipment List. Food Service equipment list shall be provided with item numbers that correspond to item number keys shown on the equipment drawing plan(s). See Project Equipment List under Medical Equipment. All applicable items requiring utilities are to be coded with a Utility Code as defined in the MIL-STD 1691. | P | F | R
FS-2 |  |  |  | Cut Sheets |  |  | Provide in a digital PDF or 8 1/2"x11" format
FS-2.1 | Report | [5 empty] | Provide cut sheets for all Food Service equipment denoting Acquisition Code (CC, VC, VV) and ASE. Cut sheets shall bear item numbers that match item numbers shown on the equipment drawing plan(s) and schedule(s). | P | F | R
FS-3.0 |  |  |  | Meeting Notes
FS-3.1 | Report | [5 empty] | Document meetings and decisions with VHA staff and stakeholders to develop Food Service equipment lists and plans. | P | F | R
FS-4.0 |  |  |  | Food Service Equipment Plans |  |  | As per VA BIM STANDARD and below:
FS-4.1 | Drawings | [5 empty] | Provide floor plans at 1/4"= 1'-0" (1:50) that graphically indicate locations, dimensions, and ASE of proposed and existing equipment as listed in the Project Equipment List. Food Service Equipment plans shall show all rooms with equipment layouts. All equipment shall be shown to fit into rooms and be usable. Assign utility codes to equipment as applicable. JSN codes shall identify all equipment and reference the Project Equipment List, cut sheets, and specifications. Project Equipment Lists shall not be shown on the plans, but shall be included in the specifications. VACO may require over the shoulder reviews at mid points during the development of Interim 2. Show kitchen hood fire suppression interface to electrical/gas shutdowns as required on MEP Models and drawings. the Food Service equipment plan shall be identified with numbered keys that correspond to the Project Equipment list, cut sheets, and specifications. |  | F | R
FS-5 |  |  |  | Food Service Equipment Budget Estimate |  |  | Excel Spreadsheet
FS-5.1 | Report | [5 empty] | Provide a Food Service Equipment Budget Estimate using Activations software system and categorized for Acquisition Codes VC and VV. | P | F | R
FS-6 |  |  |  | Activation Deliverables Package (Electronic Files) |  |  | As per Activations Deliverable Package
FS-6.1 | Report | [5 empty] | Include Food Service in Medical Equipment Activation Deliverables Package |  | F | R
VA SME
| Dickens Precil |  |  |  |  | dickens.precel@va.gov | Eastern Region Equipment Planner
| Joshua Barto |  |  |  |  | jushua.barto@va.gov | Central Region Equipment Planner
| James Flanders |  |  |  |  | james.flamders2@va.gov | Western region Equipment Planner
| Jacob Brown |  |  |  |  | Jacob.J.Brown@va.gov | SEPS Coordination

## Interiors
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
ID |  | INTERIOR DESIGN |  |  |  |  | VA submission requirements for Interior Design
ID-1.0 |  |  | General Interior Design Requirements |  |  |  | Provide General Interior Design requirements as stated in the RFP.
ID-1.1 | Report |  |  | Narrative |  |  | Provide narrative describing interior design concept, how it meets the needs of the users and the facility, and budget considerations. Discuss appropriateness of material and color selections , how they address patient needs, how they relate to the overall building design, and their appropriateness for the geographical location of the facility. | P | U | F
ID-1.2 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction plan on all interior designs. Determine minimal acceptable changes necessary to implement seismic corrections. | P | F | R
IF |  | FINISHES
IF-1.0 |  |  | Basis of Design |  |  |  | Provide Table of Contents for all Interior Finishes submittals.
IF-1.1 | Report |  |  | Narrative |  |  | Provide a narrative describing the overall interior design and how it meets the needs of the users and the facility. Refer to the RFP for additional narrative requirements. | P | U | F
IF-1.2 | Report |  |  | Finish Schedule |  |  | Provide a detailed Room Finish Schedule in tabular format, which identifies room number and room code and that is keyed to the VA Specification Section 09 60 00 Schedule For Finish. Room Finish Schedule is to include finish materials and color selections for all exposed surfaces. Identify deviations from PG 18-14 in a separate column, to include CFM approval/documentation supporting all deviations. Ensure that all information on Room Finish Schedule is consistent with Specification Section 09 06 00 Schedule For Finishes. | P | U | F
IF-1.3 | Aggregate |  |  | Sample Boards |  |  | Provide material and finish sample boards. Identify and key each item on the Binder Sample Boards to the contract documents to provide a clear indication of how and where each item will be used. Arrange finish samples to the maximum extent possible by room type in order to illustrate room color coordination. Provide separate discussions and sample boards for specialty areas such as Behavioral health, etc. Refer to the RFP for additional sample board requirements. | P | F
IF-1.4 | Aggregate |  |  |  | Presentation Boards |  | Provide framed presentation color boards for interior finishes are required. Refer to the RFP for additional presentation board requirements. |  |  | F
IF-2.0 |  |  | DRAWINGS |  |  |  | Interior design related drawings shall be provided with each submittal and must indicate the placement of extents of material, finishes and colors and must be sufficiently detailed to define all interior work. Interior Finish drawings are to follow the VA BIM STANDARD and other criteria as stated in the RFP. The minimum scale for Interior Finish drawings is 1/8" = 1'-0" (1:100).
IF-2.1 | Drawings |  |  | Public Spaces |  |  | Provide fully developed design for major public spaces. Provide full color renderings as required in the RFP. Submit elevations, perspectives or other presentations to describe the materials, lighting, and appearance of those spaces. Coordinate with Architecture and other disciplines as required by the project. | P | F | R
IF-2.2 | Drawings |  |  | Finish Plans |  |  | Provide plans indicating wall and floor patterns and color placement, material transitions and extents of interior finishes. Include wall protection plans. Provide enlarged plans that clearly delineate wall and floor patterning, where applicable. | P | U | F
IF-2.3 | Drawings |  |  | Interior Elevations, Sections and Details |  |  | Indicate material, color and finish placement as necessary to convey design intent of feature walls, nurse station or other built-in architectural casework/millwork, miscellaneous details, etc. Coordinate requirements with Architecture. Provide interior elevations necessary to convey design intent for finishes and color selections. (See Architectural requirements.) If applicable, identify artwork placement opportunities and color schemes to assist in wayfinding. | P | F | R
IF-2.4 | Drawings |  |  | Architectural Casework |  |  | Coordinate with Architecture. Provide product cut sheets for all "CC" casework. Provide material finishes that are smooth and non-porous (to minimize contamination) and ensure that countertops and casework corners have rounded edges to maximize safety for patients, visitors and staff. | P | U | F
IF-2.5 | Drawings |  |  | Millwork and Features |  |  | Coordinate with Architecture. Provide material finishes that are smooth and non-porous (to minimize contamination) and ensure that countertops and casework corners have rounded edges to maximize safety for patients, visitors and staff. | P | U | F
IF-2.6 | Drawings |  |  | Toilet Rooms & Showers |  |  | Coordinate with Architecture. Provide fully developed design for all Toilet Rooms and shower spaces. Define elevations and thresholds to ensure proper material transition and drainage. These may need to be at a larger scale in order to convey design intent. | P | U | F
FFE |  | FURNISHING, FIXTURES, & EQUIPMENT (FFE) |  |  |  |  | Furniture (movable), fixed furnishings, not including medical and food equipment.
FFE-1.0 |  |  | Basis of Design - FFE Requirements |  |  |  | Provide FFE requirements as stated in the RFP.
FFE-1.1 | Report |  |  | Table of Contents |  |  | Provide Table of Contents for all Interior Finishes submittals. | P | U | F
FFE 1.2 | Report |  |  | Narrative |  |  | Provide a narrative description of the furniture, to include functional, safety and ergonomic considerations, durability, sustainability, aesthetics, compliance with evidence-based design principles and compatibility with the building design. | P | U | F
FFE-2.0 |  |  | Room Data Sheets |  |  |  | Coordinate with Architecture.
FFE-2.1 | Drawings |  |  | Room Data Sheets |  |  | Provide FFE information for Room Data Sheets. | P | F | R
FFE-3.0 |  |  | FFE Cut Sheets
FFE-3.1 | Report |  |  | FFE Cut Sheets |  |  | Provide cut sheets for all FFE denoting Acquisition Code (CC, VC, VV). Coordinate cut sheet submittal with other disciplines as required by the project. Refer to the RFP and other requirement documents for additional information. |  | P | F
FFE-4.0 |  |  | FFE List
FFE-4.1 | Report |  |  | Meeting Notes |  |  | Provide all meeting minutes with documentation of decisions made by VHA staff and stakeholders. | P | U | F
FFE-4.2 | Report |  |  | SEPS PRC |  |  | Refine the SEPS PRC after user meetings with VHA staff and stakeholders. Provide an updated excel file of the Project Equipment List (with all required coding) for all updated Room Contents. Coordinate with Medical Equipment. | P | U | F
FFE-4.3 | Report |  |  | Existing Inventory List |  |  | List of existing inventory of items or artifacts to be re-used/relocated that require coordination with construction (if applicable). Identify how the existing artwork and artifacts would be reused. Include how existing furnishing, artwork, and artifacts will be coded or identified. Refer to the RFP and other requirement documents for additional information. | F | R | R
FFE-5.0 |  |  | FFE Sample Boards
FFE-5.1 | Aggregate |  |  | FFE Sample Boards |  |  | Provide Binder Sample Boards depicting physical finish samples of all major furnishings items Identify and key each item on the Binder Sample Boards to the items proposed in the FFE. Refer to the RFP and other requirement documents for additional information. | P | F
FFE-5.2 | Aggregate |  |  | FFE Presentation Boards |  |  | Provide framed presentation color boards for all major FFE furnishings and artwork will be required (in addition to the Binder Sample Boards). Refer to the RFP and other requirement documents for additional information. |  |  | F
FFE-6.0 |  |  | FFE Plans
FFE-6.1 | Drawings |  |  | FFE Plans |  |  | FFE drawings to include Government-furnished and government-installed medical and non-medical equipment, modular furniture components, loose furniture, accessories and artwork. Ensure that locations for these items are identified on the plans, and that all furnishings and equipment are assigned a Joint Schedule Number (JSN); Ensure building utilities and structures are coordinated and designed to interface with these items. Installation of utilities and other construction coordination requirements for FFE are detailed in the Project Room Contents Report (PRCR) and are cross-referenced to the Joint Schedule Number (JSN). Refer to RFP, Project Room Contents (PRC), and Medical & Food Equipment criteria for coordination with FFE.. FFE drawing scale is to be 1/4" = 1'-0". |  | F | R
FFE-7.0 |  |  | FFE Budget Estimate
FFE-7.1 | Report |  |  | FFE Plans |  |  | Itemized FFE Cost Estimate: Provide an itemized cost estimate of furnishings keyed to the plans and specifications of products included in the package. Estimate shall be categorized by acquisition code, and itemized budget estimate is to be provided at each submittal phase with updated information. This cost estimate should be based on GSA price schedules. Refer to RFP and other requirement documents for information. | P | U | F
FFE-8.0 |  |  | Activation Deliverables Package (Electronic Files) |  |  |  | The following items are to be provided in a separate electronic package for use by the VA Activations team; all digital files are to be provided to the Activation Team in the formats as stated in the RFP.
FFE-8.1 | Drawings |  |  | Drawings |  |  | All drawings listed above: (1) Digital PDF; (2) DWG; (3) Native BIM file format |  | P | F
FFE-8.2 | Report |  |  | FFE List |  |  | FFE List: 1) Digital PDF; 2) Excel; 3) Medical Center Web Based Equipment Program. |  | F | R
FFE-8.3 | Drawings |  |  | Room Data Sheets |  |  | Room Data Sheets (see architecture requirements): (1) Digital PDF; (2) DWG; (3) Native BIM file format |  | F | R
FFE-8.4 | Drawings |  |  | FFE Cut Sheets |  |  | FFE & Artwork Cut Sheets: (1) Digital PDF |  | F | R
FFE-8.5 | Report |  |  | FFE Budget Estimate |  |  | FFE Cost Estimate: (1) Digital PDF; (2) Excel |  | F | R
FFE-8.6 | Aggregate |  |  | Finish Samples of FFE Products |  |  | FFE Finish Sample Boards: (1 Digital PDF); (2) Actual sample boards for designated POCs (listed in submittal register). |  | F | R
SW |  | SIGNAGE AND WAYFINDING |  |  |  |  | VA submission requirements for Signage and Wayfinding
SW-1.0 |  |  | Basis of Design |  |  |  | Provide a table of contents for all Signage and Wayfinding submittals
SW-1.1 | Report |  |  | Narrative |  |  | Describe wayfinding concept, to include wayfinding strategies that include navigating from the exterior (site) toward the facility entrances and then throughout the interior of the facility and returning to the exterior and exiting the site. Adhere to the VA Signage Design Guide and the VA Healing Environments Design Guide. Include a narrative hierarchy description of each sign type. Consider wayfinding needs for the visually impaired (i.e., color, texture, contrast). | P | U | F
SW-2.0 |  |  | Catalog Cut Sheets
SW-2.1 | Report |  |  | Signage Cut sheets |  |  | Provide Signage Cut sheets for each sign type proposed on the project, to include both interior and exterior signage. Cut sheets shall include manufacturer name and name of signage series/model number, along with details such as font style and size, dimension of sign module, material finishes and other salient features. | P | U | F
SW-2.2 | Report |  |  | Sign Message Schedule |  |  | Provide Sign Message Schedule on drawings and in electronic spreadsheet format. Include Room Number, Room Name, Sign Message, Sign Symbols (if required), Directional Arrow (if required), and Special Instructions (if required). Coordinate with all drawings for consistency. Refer to RFP and other requirement documents for information. | P | U | F
SW-3.0 |  |  | DRAWINGS
SW-3.1 | Drawings |  |  | Interior Signage Drawings |  |  | Submit floor plans, detail drawings and sketches indicating signage finishes, sign types and wayfinding features. Show signage in context with floor and wall patterns, lighting, and other elements. Interior signage plans to be developed and coordinated with the overall Wayfinding Master Plan. Minimum scale of Interior Signage Drawings is to be 1/8" = 1'-0". Refer to RFP and other requirement documents for information. | P | U | F
SW-3.2 | Drawings |  |  | Site Signage |  |  | Signage plan and signage schedule, with signs keyed to site locations, construction details, and sign face graphics. Site location signage to include signage for surface parking lots, parking garages, outdoor pavilions, exterior healing gardens, etc., as applicable. Coordinate internally illuminated signs with Electrical Drawings. | P | U | F
SW-4.0 |  |  | Sample Boards
SW-4.1 | Aggregate |  |  | Signage Finish Samples |  |  | Provide sample boards for sign finishes. Provide finishes denoting color/texture/pattern information, keyed to each sign type. | P | F
VA SME
| Orest Burdiak |  |  |  |  | orest.burdiak@va.gov

## Fire Protection
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | FIRE PROTECTION |  |  |  |  | VA submission requirements for Fire Protection Design
F-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) at each phase with updated information. Report to include:
F-1.1 | Report |  | Narrative |  |  |  | Description of the project and executive summary for key items addressed within the Fire Protection Basis of Design. See the VA Fire Protection Design Manual (VA FPDM) and PG-18-03 Topic 1 for fire protection requirements and other references. | P | F | R
F-1.2 | Report |  |  | General Code Analysis |  |  | Code analysis that includes height and area limitation evaluation, construction type requirements, and occupancy classifications. Code analysis to assess compliance with NFPA 101 including accessible means of egress for other than healthcare occupancies. Description of building construction type and building separation in accordance with Chapter 2 of the VA Fire Protection Design Manual. The analysis shall reference to NFPA 220 for fire resistive ratings and NFPA 101 for occupancy types per PG-18-03 Topic 1. Coordinate with Architectural Code Analysis. Reference the International Building Code (IBC), depending on occupancy classification, as reference for fire resistance rating for each element of construction. | P | F | R
F-1.3 | Report |  |  |  | Fire Protection Codes and Standards |  | Listing of all applicable governing and referenced codes either required directly by the VA FPDM or via other codes referenced therein; include editions. | P | F | R
F-1.4 | Drawings |  |  |  | Fire Protection During Construction |  | See Arch tab under ILSM tasks. | P | F | R
F-1.5 | Report |  |  |  | Site Considerations |  | Description of fire department access for each facility complying with NFPA 1. Describe overall site accessibility, property lines, public way, clear yard setbacks, fire separation distances between structures, secured access impacting emergency response, on-site hazardous material locations per NFPA 1, and any coordination items necessary for emergency response personnel awareness. Description should include location of fire department connections (FDCs), fire alarm control unit and panels and microphone for two-way communication systems. | P | F | R
F-1.6 | Report |  |  |  | Existing Systems |  | Description of fire protection features for existing facility. Describe sprinkler system type, hazardous material locations, and any items necessary for emergency response personnel awareness. | P | F | R
F-1.7 | Report |  |  | Building Features |  |  | Incorporate Building Features as denoted below:
F-1.8 | Report |  |  |  | Occupancy Classification |  | Identification of space and occupancy classification in accordance with VA FPDM Chapter 4 and NFPA 101. | P | U | F
F-1.9 | Report |  |  |  | Special Occupancies/Protection |  | Compliance with specialty occupancies such as, but not limited to, health care, laboratories per NFPA 45, parking structures, high-rises, hazardous materials/processes, underground buildings, combustible storage, IT/communication uses per NFPA 75/76, emergency power systems per NFPA 110/111, and others identified in VA FPDM Chapter 3, NFPA 101 Chapter 11, or NFPA 1. Where applicable to each special use, describe the configuration and address classification, fire resistive construction, fire extinguishing/alarm systems, and any other items necessary to demonstrate compliance. | P | U | F
F-1.10 | Report |  |  |  |  | Information Technology and Telecommunications | Description of passive fire protection features and active fire protection and detection in accordance with the VA FPDM. | P | U | F
F-1.11 | Report |  |  |  |  | Laboratories | Description of the location within the facility and fire protection features of laboratories, where provided, in accordance with NFPA 45 including the laboratory classification, fire separations due to occupancy and the quantities of flammable and combustible liquids stored, and standpipe requirements, if any. | P | U | F
F-1.12 | Report |  |  |  |  | Atrium Smoke Control Systems | Description of the smoke evacuation system required for the atrium in accordance with the VA FPDM. | P | U | F
F-1.13 | Report |  |  |  |  | VA Hospital Building System (VAHBS) | Description of the fire protection features of the VAHBS where the VAHBS is used in the design in accordance with VA FPDM. | P | U | F
F-1.14 | Calculations |  |  |  | Type of Construction, Building Height and Area |  | Height and area limitation evaluation, construction type requirements, and building separation, in accordance with VA FPDM Section 2.1 /2.2 and NFPA 220. | P | F | R
F-1.15 | Report |  |  |  | VA Hospital Building System (VAHBS) |  | Description of the fire protection features of the VAHBS where the VAHBS is used in the design in accordance with VA FPDM. | P | U | F
F-1.16 | Report |  |  |  | Fire Resistive Construction |  | Incorporate Fire Resistive construction as denoted below:
F-1.17 | Report |  |  |  |  | Structural and Exterior Fire Resistance | Provide basis of design UL assemblies associated with each fire-resistance rated assemblies for structural protection including beams, columns, horizontal assemblies, secondary members; address exterior rated or load bearing wall requirements. Description should indicate materials to be used and fire resistive rating of each construction element. | P | U | F
F-1.18 | Report |  |  |  |  | Combustible Materials | Description of combustible material requirements of VA FPDM and IBC Section 603. | P | U | F
F-1.19 | Report |  |  |  |  | Interior Finishes | Description of permitted interior finish requirements based upon occupancy. | P | U | F
F-1.20 | Report |  |  |  |  | Interior Separations, Openings, and Penetrations | All applicable requirements for any fire-resistive construction used, including assembly ratings, requirements for opening and penetrations, protection of construction joints. Include analysis of the requirements for fire dampers and smoke dampers in reference to NFPA 101 and the corresponding references {i.e., NFPA 90A}. (Do not follow the requirements in the International Building Code (IBC) nor the International Mechanical Code (IMC). | P | U | F
F-1.21 | Report |  |  |  | Means of Egress |  | Address compliance with VA FPDM and NFPA 101. Ensure that the exit access features in the means of egress are fully coordinated and functional to meet the project goals, needs of patient security, and access control requirements while also complying with the means of egress requirements of NFPA 101. | P | U | F
F-1.22 | Report |  |  |  |  | Fire and Smoke Dampers | Analysis of the requirements for fire dampers and smoke dampers in reference to NFPA 101 and the corresponding references {i.e., NFPA 90A}. Ensure fire and smoke dampers are fully coordinated with all disciplines to meet lifecycle maintenance access.(Do not follow the requirements in the International Building Code (IBC) nor the International Mechanical Code (IMC). Include requirements for inspection, testing, maintenance access. | P | U | F
F-1.23 | Report |  |  | Water Supply for Fire Protection |  |  | Description of the water supplies, water distribution system layout, sizes and hydrant locations and fire department connections for each building and all operating features as a water distribution and supply network. Include fire hydrant flow test data. | P | U | F
F-1.24 | Report |  |  |  | Fire Pumps |  | Analysis of the requirements for fire pumps and description and locations of fire pump(s) and drivers based on water supply and demand and electrical power available. | P | U | F
F-1.25 | Report |  |  | Fire Extinguishing Systems |  |  | Description of type and locations of sprinkler systems and analysis of sprinkler system requirements including estimated demands and the use of air or nitrogen or antifreeze for areas subject to freezing. Description of zoning of systems in accordance with the VA FPDM. | P | U | F
F-1.26 | Report |  |  | Fire Alarm Systems |  |  | Description for the type of fire alarm system (general evacuation or defend in place; type of notification) in accordance with the VA FPDM Chapter 7. Description of zoning in accordance with the VA FPDM. | P | U | F
F-1.27 | Report |  |  |  | Smoke, Carbon Monoxide, and Heat Detection |  | Description of the location of any required smoke detection, carbon monoxide detection, and heat detection as required by the VA FPDM and NFPA 101. | P | U | F
F-1.28 | Report |  |  |  | Off premises connection |  | Description of the connection to the base loop or the campus fire alarm system and the method and means of communication to a remote supervisory station. | P | U | F
F-1.29 | Report |  |  |  | Interfaces |  | Description of fire alarm system interfaces with other fire protection equipment and building systems including, but not limited to, control valves, sprinkler systems, dry pipe systems, pre-action systems, deluge systems, kitchen hood extinguishing systems, clean agent systems, smoke and fire dampers, air handling units (fan shut down), door locks, door hold-open release, elevators, tank and room temperature alarms, tank level indicators, fire pumps, and emergency generators. | P | U | F
F-1.30 | Report |  |  |  |  | Clean Agent Fire Systems | Description of clean agent extinguishing system including all areas to be protected. | P | U | F
F-1.31 | Report |  | Catalog Cut Sheets |  |  |  | Provide Fire Protection Devices catalog cut sheets. | P | F | R
F-1.32 | Report |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  |  | Analyze impact of seismic correction plan on all fire protection systems. Describe minimal acceptable changes necessary to implement seismic corrections. | P | F | R
F-2.0 |  |  | CALCULATIONS
F-2.1 | Calculations |  |  | Water Supply Sizing |  |  | Submit calculations to size fire pumps (when required), water supply available/maximum demand, on-site water storage/reservoirs, and water flow testing results raw data. | P | U | F
F-2.2 | Calculations |  |  | Egress |  |  | Occupant load and egress calculations for each floor that justify the number of exits and egress width provided; show both required and actual. | P | U | F
F-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
F-3.1 | Drawings |  | General Sheets |  |  |  | Provide listing of edited VA standard symbols, abbreviations, and standard details. | P | U | F
F-3.2 | Drawings |  | Site Fire Protection and Code Plan |  |  |  | Show items described in the narrative: fire department access for each facility complying with NFPA 1, overall site accessibility, property lines, public way, clear yard setbacks, fire separation distances between structures, secured access impacting emergency response, on-site hazardous material locations, and any coordination items necessary for emergency response personnel awareness. Show building perimeter where used for frontage increase, fire department connections, PIV's, fire hydrants, water distribution main/size, water storage tanks, hazardous material locations, fire pump room, backflow prevention devices, main fire alarm control unit and annunciator locations. | P | U | F
F-3.3 | Drawings |  | Code Plans |  |  |  | Graphically indicate all passive protection items addressed in the BOD Narrative. 1. When work is only done on a portion of a floor, the entire floor must be shown on the drawings to permit egress evaluation. 2. Locked cross corridor doors must be shown including the direction in which the door is locked, to permit egress evaluation. Provide life safety plans at 1/16"=1'-0" (1:200) showing: Occupancy classifications, Suites in Healthcare Occupancies (Only), including the type (sleeping, patient care non-sleeping, non-patient care) and suite area size; Maximum travel distance between any point in a suite and an exit access door to another suite, an exit access corridor door, or a horizontal exit door; Fire rated barriers (including all vertical shafts); Hazardous areas per occupancy chapter of NFPA 101; Electrical rooms housing dry transformers in excess of 112.5 kVA to be rated for 1 hr. Smoke barriers, smoke compartment area sizes; Occupant loads; Horizontal exits, exit door capacity for each exit door; Maximum travel distances to exits, maximum travel distances to smoke barriers (for healthcare and Ambulatory HC); Maximum common paths of travel; Length of all dead end corridors; Fire extinguisher cabinets and fire hose connection cabinets (Detail on Architectural Drawings); Areas of refuge; Hazardous material storage locations. Identify egress requirements based on occupant load. Show any structural fire resistance items necessary. These plans will become the initial TJC Statement of Conditions Life Safety Plans; the final as-built version shall be provided in PDF and DWG formats. | P | U | F
F-3.4 | Drawings | [5 empty] | Indicate room names, room numbers, door locations and swings, smoke- and fire-rated barriers, and sprinkler/standpipe risers to floor plans. | P | U | F
F-3.5 | Drawings | [5 empty] | Locate fire extinguisher and fire hose cabinets. Ensure that fire extinguisher cabinet locations are being placed with due consideration for patient security. |  | P | F
F-3.6 | Drawings | [5 empty] | Indicate fireproofing of structural members where applicable. | P | U | F
F-3.7 | Drawings | [5 empty] | Locate exit signs and emergency lighting |  | P | F
F-3.8 | Drawings |  |  | Fire-Resistance-Rated Construction |  |  | Depict structural fire-resistance requirements and locations based on Type of Construction; additionally, barriers requiring fire resistance rated supporting construction must be specifically identified for coordination with the structural design. Show any occupancy separations, fire walls, fire barriers, smoke barriers, compart mentation, fire area separations, separation from hazards (vertical and horizontal for all, including perimeter curtain wall containment); indicate requirements for vertical openings and horizontal penetrations. Summarize associated opening and penetration ratings for each rated assembly (IE: interior and exterior doors/windows, ductwork, conduit/piping, construction joints, etc.). Indicate any delineation in Interior Finish requirements. | P | U | F
F-3.9 | Drawings |  |  | Hazardous Locations |  |  | Locate hazardous materials storage, handling and use that exceed the maximum allowable quantities. | P | U | F
F-3.10 | Drawings |  | Fire Extinguishing Systems |  |  |  | Indicate sprinkler control valve locations and associated zones at a legible scale that shall show an entire floor per drawing. Where smoke compartments are provided, the sprinkler system shall be zoned and supervised by the fire alarm system by smoke compartment. | P | U | F
F-3.11 | Drawings | [5 empty] | Indicate room names, room numbers, door locations and swings, smoke- and fire-rated barriers, and sprinkler/standpipe risers to floor plans. Identify psychiatric areas requiring institutional-type heads on the drawings. Refer to equipment or architectural drawings that affect sprinkler design (storage racks, library racks, mobile shelving, walk-in cooler/freezer, audiometric booths, etc.), Specific occupiable areas not to be protected by automatic sprinklers. Identify areas that will be provided patient lifts and associated tracks. | P | U | F
F-3.12 | Drawings | [5 empty] | Indicate sprinkler/standpipe risers supply piping; Above ground piping including (do not show sprinkler layout) o Connection to underground supply o Sprinkler mains o Fire department connections o Risers o Standpipes and hose connections o Control valves o Terminations of sprinkler system drains to a safe location (exterior to bldg.) o Water flow, water pressure, and tamper switches o Air and nitrogen system switches | P | U | F
F-3.13 | Drawings | [5 empty] | Locate terminations of sprinkler main and inspector test drain. | P | U | F
F-3.14 | Drawings | [5 empty] | Indicate sprinkler design hazards per NFPA 13. | P | U | F
F-3.15 | Drawings | [5 empty] | Provide details of the fire pump system, an enlarged plan of fire pump room, including elevation and detail of fire pump, Rated enclosure (or separation) in accordance with NFPA 20, Accessibility by fire department, Details of the fire pump location, controller, piping, and test header, Details of the jockey pump, Reference electrical drawing for power. Plan shall include all fire pump-related mechanical and electrical equipment and accessories to ensure adequate space provided for installation, operation and maintenance of said equipment. | P | U | F
F-3.16 | Drawings | [5 empty] | Indicate the kitchen hood fire suppression system; Show interface to electrical/gas shutdowns as required on MEP drawings. | P | U | F
F-3.17 | Drawings | [5 empty] | Clean agent system (if any) • Area to be protected by clean agent system • Location of clean agent supply containers • Passive fire protection features • Clean agent alarm system riser diagram • Clean agent alarm system floor plans showing all devices • All interface locations to be shown including Interface to AHU (by number) for shutdown (reference to HVAC drawings), Door hold-opens, Smoke dampers, Power supplies for panels, Connection to fire alarm system, Abort switches, Emergency power off switches • Input/output matrix and sequence of operation | P | U | F
F-3.18 | Drawings |  | Fire Alarm Systems |  |  |  | Provide fire alarm, and smoke zones at a legible scale that shall show an entire floor per drawing. Where smoke compartments are provided, the zoning of the fire alarm shall coordinate to coincide with the configuration of the smoke compartments. | P | U | F
F-3.19 | Drawings | [5 empty] | Indicate fire alarm risers showing new equipment and/or necessary changes if modification to the existing system is required. | P | U | F
F-3.20 | Drawings | [5 empty] | Provide an input/output matrix; sequence of operations. | P | U | F
F-3.21 | Drawings | [5 empty] | Define interconnection of HVAC system (dampers, fans) with duct smoke detectors and/or fire alarm system. | P | U | F
F-3.22 | Drawings | [5 empty] | Indicate interface of new and existing fire alarm system. | P | U | F
F-3.23 | Drawings | [5 empty] | Indicate all interface locations to be shown including: o Interface to AHU (by number) for shutdown (reference to HVAC drawings) o Door hold-opens o Elevator recall and shutdown o Smoke dampers o Kitchen hood suppression systems o Sprinkler flow and tamper switches o Air and nitrogen switches o Fire pumps o Door locking o Clean agent system control unit o Power supplies for panels o Connection to off-premises receiving station o Atrium smoke control | P | U | F
F-3.24 | Drawings | [5 empty] | Indicate zoning of each fire alarm initiating device. | P | U | F
F-3.25 | Drawings | [5 empty] | Locate and detail annunciator panel when provided. | P | U | F
F-3.26 | Drawings | [5 empty] | Coordinate with reference notes on HVAC drawings that indicate interconnection of HVAC system (dampers, fans) with duct smoke detectors and/or fire alarm system. | P | U | F
VA SME
| Doug Stultz |  |  |  |  | Douglas.stultz@va.gov
| Peter Leszczak |  |  |  |  | Peter.Leszczak@va.gov

## Plumbing
[5 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[6 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | PLUMBING |  |  |  | VA submission requirements for Plumbing Design
P-1.0 |  |  | Basis of Design
P-1.1 | Report |  |  | Narrative |  | Plumbing designer shall coordinate with both civil and mechanical engineers to provide descriptions of the proposed utilities for the building: fuel gas, oxygen, and water sources, sewage disposal systems, irrigation, and water services, roof drainage, etc. Provide solutions to water or sewage treatment, pumping, and storage if required. | P | U | F
P-1.2 | Report |  |  | Water Analysis |  | Provide supply water analysis testing results and proposed water treatment solutions demonstrating compliance with all water quality requirements for domestic water services (hot and cold), HVAC requirements, and medical equipment including special water treatment systems such as reverse-osmosis, deionized water etc. Demonstrate coordination of treatment with any municipal water treatment or local biocides utilized. Identify acid or chemical resistant piping. | P | U | F
P-1.3 | Report |  |  | Renewable Solar Energy |  | Explanation and technical backup information as to how the project shall meet the project goal for hot water generation using renewable solar energy. Show Life Cycle Cost Analysis calculations. | P | U | F
P-1.4 | Report |  |  | Potable Water |  | Determine potable water baseline and required reduction target. Define strategies to achieve the reduction goals. | P | U | F
P-1.5 | Report |  |  |  |  | Provide a graphical representation of water usage savings with reference to the contributing technologies and their weighted contributions . | P | U | F
P-1.6 | Report |  |  | Systems Coordination |  | Coordinate invert elevations at the interface with site utilities including domestic water, solar heated water, sanitary, storm drainage, etc. Indicate invert elevations, sizes, slopes, and materials on the plans. | P | U | F
P-1.7 | Report |  |  | Condensation |  | Indicate proposed insulation systems for the domestic water and storm drainage piping. | P | U | F
P-1.8 | Report |  |  | Utility Companies |  | Coordinate with utility companies, where applicable. Provide written approval of utility availability by utility companies or regulatory review agencies, where applicable. | P | F | R
P-1.9 | Report |  |  | Catalog Cuts |  | Provide catalog cuts for plumbing fixtures, plumbing equipment, medical gas and vacuum and dental gas and vacuum equipment used as the basis of design. | P | U | F
P-1.10 | Report |  |  | Legionella Control |  | Provide documentation and design demonstrating compliance with VHA Directive 1061 and the VA Plumbing Design Manual coordinating with any facility Water Management Plan regarding the prevention of Legionella disease and scald injury from potable water distribution systems. | P | U | F
P-1.11 | Report |  |  | Medical Gasses |  | Address sources/producers for all medical and laboratory gases whether centralized or portable. Identify NFPA 99 system categories for each system, and how redundancy, continuity, and reliability requirements are being met. Address the coordination of terminal inlets/outlets and manufactured assemblies as per most current NFPA 99. Identify quantity, type and location of patient ventilators if applicable. | P | U | F
P-1.12 | Report |  |  | Water and Sanitary Sewer |  | Address how domestic water and sanitary sewer redundancy, continuity, and reliability requirements are being met. Address facilities approach to achieve the thermal eradication requirement. | P | U | F
P-1.13 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  | Analyze impact of seismic correction plan on plumbing and sanitary systems. Determine minimal acceptable changes necessary to implement seismic corrections. | P | U | F
P-2.0 |  |  | CALCULATIONS
P-2.1 | Calculations |  |  | Systems and Equipment Sizing |  | Plumbing engineer shall coordinate with other engineer disciplines for systems and equipment sizing where necessary. Show calculations for equipment and pipe sizing. | P | F | R
P-2.2 | Calculations |  |  | Water Usage |  | Provide potable water baseline and reduced consumption calculations to achieve the VA water consumption reduction goals. | P | F | R
P-2.3 | Calculations |  |  |  |  | Indicate proposed products to be used to meet water efficiency requirements. | P | F | R
P-2.4 | Calculations |  |  |  |  | Show how the sewage water from the 96 hour retention tank would drain to sewer lines or lift pump if required. | P | U | F
P-2.6 | Calculations |  |  | Storm Water Discharge |  | Provide storm water computations, sizing, calculations, and site analysis to comply with local, state, and federal regulations. Indicate methodology of software used. | P | U | F
P-2.5 | Calculations |  |  |  |  | Provide calculations for storm water and sizes of rain leader, overflow pipes, or scuppers. | P | F | R
P-2.6 | Calculations |  |  | Water Pressure Testing |  | If water pressure measurement is older than 1 year a Fire Protection Engineer must perform a new fire flow test for water pressure and flow at two fire hydrants serving each building in project. | F
P-2.7 | Calculations |  |  | Water Supply Pressure |  | Provide domestic water supply pressure drop calculations to validate booster pump sizing and to demonstrate compliance with the VA Plumbing Design Manual minimum pressure requirements. Calculations must show all significant system pressure losses as well as identify the most stringent supply pressure requirements to be met (e.g. washer/disinfector etc.). | P | U | F
P-2.8 | Calculations |  |  | Medical Gasses |  | Provide calculations for medical gas and vacuum systems and dental gas and vacuum systems including source sizing and pipe sizing. Calculations must be coordinated with and include corresponding node to node diagrams. | P | U | F
P-2.9 | Calculations |  |  | Acoustics |  | Provide acoustic analysis of all medical gas and vacuum system and dental gas and vacuum system producers (e.g. vacuum pumps, medical air compressors etc.) and steps taken to ensure compliance with the specified noise levels in coordination with other disciplines. | P | U | F
P-2.10 | Calculations |  |  | Soil, waste, and vent |  | Provide calculations for soil, waste and vent system including pipe sizing. Provide calculations of natural gas system and pipe sizing. | P | U | F
P-3.0 |  |  | DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and below
P-3.1 | Drawings |  |  | Demolition Plans |  | Provide 1/8” = 1’0” (1:100) scale demolition plumbing floor plans. | P | U | F
P-3.2 | Drawings |  |  | Utility Plans |  | Provide location, types, and sizes of existing and proposed utilities. Plumbing Designer, Civil Engineer, and Landscape Architect shall collaborate and coordinate plans. Provide location of existing and proposed storage facilities (if required) and/or areas of lawn irrigation. Indicate any areas of specialty systems. Existing and proposed underground utilities shall be modeled in BIM (see General Tab). | P | F | R
P-3.3 | Drawings |  |  | Utilities |  | Plumbing Designer, Architect, Mechanical and Electrical Engineer shall collaborate and coordinate plan(s) for emergency and normal power requirements for: medical gases and systems, plumbing fixtures, water and sanitary storage, distribution, and control systems. | P | U | F
P-3.4 | Drawings |  |  | Riser Diagrams |  | Provide isometric and flow diagrams of domestic water, sewer and vent, storm water, and natural gas systems. | P | F | R
P-3.5 | Drawings |  |  | Schematic Diagrams |  | Provide single line schematic diagrams of the site distribution and domestic water systems demonstrating how hot & cold water is: distributed, balanced, circulated, isolated by valve, stored, flushed, sampled, heated and cooled, treated, drained, and monitored including temperature. Indicate location of makeup systems, outdoor air intakes, no flow and low flows portions of the piping, possible cross connections between potable and non-potable water system and major building water equipment. Identify any areas in which water is processed differently (e.g., hemodialysis and sterile processing). | P | U | F
P-3.6 | Drawings |  |  | Schematic Diagrams |  | Provide riser diagrams of all medical gas, laboratory and vacuum systems including functional diagrams of the central supply systems. Show all inlets/outlets, zone valves, service valves, alarm locations etc. Identify each outlets/inlet location where ventilators are to be served. Include table of alarms for all local, area and master alarms. Identify zone valve box/area served for all area alarms and show locations of alarm sensors. |  | F | R
P-3.7 | Drawings |  |  | Plan Drawings |  | Provide 1/8" = 1'-0" (1:100) scale floor plan drawings and riser diagrams indicating room names, locations of existing and new equipment, and plumbing fixtures using VA fixture numbers and VA BIM Standards Coding requirements. Indicate interface of new systems with existing. Show location of air compressors, vacuum pumps, medical gas zone valves and alarm locations, sewage ejectors, domestic water heaters and main risers, roof drains and overflow, pipe sizes, medical gas cylinders manifolds, and backup water supply. Submit schedules, notes, and legends for equipment and distribution systems on drawings. Examine choke points with other trades and validate floor to floor heights. | P | U | F
P-3.8 | Drawings |  |  | Plan Drawings |  | Provide location of grease traps and waste recovery systems. | P | F | R
P-3.9 | Drawings |  |  | Plan Drawings |  | Coordination with medical equipment. Show the utility services and connection points to all medical equipment. Utilities include but are not limited to steam, domestic water, deionized water, medical gas, R/O water, Dealkalizing Systems, and floor drains. | P | U | F
P-3.10 | Drawings |  |  | New Building Equipment |  | Provide 1/4” = 1’0” (1:50) scale floor plans showing location and sizing of new equipment that services the building. Show clearance requirements. The footprints shown for major plumbing and med gas equipment should be based on actual sizes of equipment. Details at appropriate scale. | P | U | F
P-3.11 | Drawings |  |  | Architecturally Significant Equipment (ASE) |  | Provide 1/4” = 1’0” (1:50) plans showing location and sizing of utility connections to ASE identified equipment. | P | F | R
VA SME
| Snehal Desai |  |  |  | Snehal.Desai@va.gov

## Mechanical
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | HEATING, VENTILATING & AIR CONDITIONING |  |  |  |  | VA submission requirements for Heating, Ventilating & Air Conditioning
M-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) report updated at each submittal with the following information:
M-1.1 | Report |  |  | Narrative |  |  | Provide a Narrative describing the following:
M-1.2 | Report |  |  |  | Concept Energy & Resource Consumption |  | Provide assessment of the existing building energy and resource consumption baseline. (For new buildings, document the existing inventory baseline.) Include investigation of the use of high-efficiency, low-pressure hot water boilers for heating application. | P | U | F
M-1.3 | Report |  |  |  | Energy Saving |  | Discuss how the design meets the increased demand and what type of energy-saving measures have been examined. Describe how the requirements of energy efficiency and energy savings have been met. | P | U | F
M-1.4 | Report |  |  |  | Spare Capacity |  | Discuss how the design meets the HVAC needs of the project including expansions of existing systems and plants (if applicable). | P | U | F
M-1.5 | Report |  |  |  | Three HVAC System Alternatives |  | Submit the Life Cycle Cost Analysis (LCCA) for the selection of air handling unit systems as detailed in the HVAC Design Manual. Detail the three different types of HVAC systems analyzed, the criteria and rationale and the LCCA for evaluating the three systems. Coordinate with the VA HVAC Design Manual wherein the restrictions on the system type and the capacity limitations are outlined. | F
M-1.6 | Report |  |  |  | Energy Efficiency and Conservation |  | Identify the project specific energy conservation criteria to be met based on the applicable VA criteria. Describe the proposed energy efficiency and conservation measures in the HVAC system design and the life cycle cost analysis. Refer to VA guidelines for the mandated energy conservation requirements and energy consumption goals. State the logic and criteria for selecting each conservation measure. Also, perform energy modeling and justify the proposed measures. | P | U | F
M-1.7 | Report |  |  |  | HVAC System |  | Provide detailed description of the heating, ventilating, and air conditioning (HVAC) systems and equipment for each functional space. | P | U | F
M-1.8 | Report |  |  |  | HVAC System |  | Provide the mechanical system size, and space requirements. Include redundancy requirements and emergency epidemic operations for the systems. | P | U | F
M-1.9 | Report |  |  |  | Seismic |  | Describe the impact of seismic requirements (if applicable) on the HVAC systems. | P | U | F
M-1.10 | Report |  |  |  | Severe Weather Impacts |  | Describe the potential impact of severe weather and climate conditions (hurricanes, ice, snow, flood, humidity, coastal areas, wind borne rain) on the HVAC equipment. | P | U | F
M-1.11 | Report |  |  |  | Zones |  | Describe the planned zoning of the spaces and the rationale, including those proposed with dedicated HVAC systems. Describe the locations of the equipment serving each zone, focusing on the serviceability and maintainability of each major piece of equipment. | P | U | F
M-1.12 | Report |  |  |  | Backup Systems |  | Identify redundant/backup/emergency systems/equipment. | P | U | F
M-1.13 | Report |  |  |  | Acoustical Impact |  | Describe acoustical and vibration impact of mechanical systems/equipment to stacked or adjacent spaces including new and existing equipment. | P | U | F
M-1.14 | Report |  |  |  | System Interaction |  | Provide description of the interaction between the existing HVAC systems and the new requirements. State the impact on the existing HVAC systems. Examples include: additional Testing, Adjusting, and Balancing (TAB) effort, replacement of components, suspended ceiling, painting, and fixtures. Also identify the extents of pre-construction TAB planned in order to define and document the existing systems baseline performance and any deficiencies as well as to ensure the existing system is restored to it's baseline performance after construction. | P | U | F
M-1.15 | Report |  |  |  | ECC |  | Analyze the feasibility of using the existing central Engineering Control Center (ECC) for the automatic temperature control requirements of the new project. Address the key issues of the available spare capacity and open-protocol BACnet compatibility. |  |  |  | F |  |  |  | Must be determined in RFP and documented here.
M-1.16 | Report |  |  |  | Operational Sequence |  | Provide description of the mechanical sequences of operation. State that the energy model represents these operational parameters and uses actual equipment performance curves from the design selections (mechanical, plumbing, and lighting). |  | P | F
M-1.17 | Report |  |  |  | Metering Requirements |  | Provide evidence of coordination of the metering requirements with the existing facilities, Military installation, or VA Station/campus as applicable and provide a brief description of the scope of work and extent of coordination involved. Define the work by a single line schematic diagram showing components and the interface between systems. | P | U | F
M-1.18 | Report |  |  |  | Room Data Sheets |  | Provide evidence of coordination of HVAC requirements on room data sheets (see Architectural requirements). | P | U | F
M-1.19 | Report |  |  |  | Coordination |  | Provide evidence of discipline coordination to accommodate all Architecturally Significant Equipment to include, but not limited to: sterilizing equipment, kitchen equipment, automatic cart washer, fume hoods, biological safety cabinets, radiology, and nuclear medicine equipment specified for the project. Present all VA-approved deviations from HVAC design criteria. Design submissions can not presume the approval of any pending or proposed criteria deviations. (Any request for deviation from HVAC design criteria must be approved by VA and occur no later than the Interim 2 Design Submittal). | P | U | F
M-1.20 | Report |  |  | Energy Model |  |  | Energy Model for Mechanical Systems. See Sustainability Manual for criteria. | P | U | F
M-1.21 | Report | [5 empty] | Submit energy modeling report using operational parameters of all designed systems and uses actual equipment performance curves from the design selections (mechanical, plumbing, and lighting). Discuss any adjustments and their effects from the previous submittal. | P | U | F
M-1.22 | Report |  |  | Mechanical Equipment |  |  | Provide complete selection data, including catalog information (i.e. cut sheets) for all HVAC equipment. |  | P | F
M-1.23 | Report |  |  | O&M |  |  | Provide narratives discussing direct access for O&M of major equipment and a practical means of future replacement. | P | U | F
M-1.24 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction on all heating, ventilating and air conditioning systems. Describe the changes needed to meet seismic criteria. | P | U | F
M-2.0 |  |  | CALCULATIONS
M-2.1 | Calculations |  |  | Selected HVAC System |  |  | Provide an analysis of the selected HVAC system to include all zone level and space level assumptions and parameters, and physical security requirements. Computerized analysis shall be prepared by using either a public domain program or the privately developed software programs. Provide lifecycle cost calculations. Submit the name and version of the program used for computerized analysis. (Prior approval by VA is required for the use of private programs, as opposed to public domain programs.). Include the analysis for incorporating Combined Heat and Power (including LCCA) as required by VA Sustainable Design Manual. Provide analysis of HVAC systems (water and air) on the epidemic mode. | P | U | F |  |  |  |  | LCCA to be done during RFP development and provided to AE of Record for review and concurrence, updated as needed.
M-2.2 | Calculations |  |  | Selected Concept Analysis |  |  | Provide 8,760-hour basis energy analyses together with the energy model to optimize the orientation and other related system components and proposed massing scheme. Envelope and glazing are optimized; all other variables (occupancy, regulated and unregulated loads) in the energy model shall remain fixed for all schemes considered. Final design submittal must analyze only the final orientation of the building. For analysis, use ASHRAE latest climate data. | P | U | F
M-2.3 | Calculations |  |  | Life Cycle Cost Analysis |  |  | Conduct a complete life cycle cost analysis with heating and cooling requirements, include specific recommendations and full back‑up data. State the heating and cooling capacities of each departmental area used in the life cycle cost analysis. State the block cooling and heating loads for each new and/or existing building. | P | U | F
M-2.4 | Calculations |  |  | Load Calculations |  |  | Provide detailed heating, cooling, and ventilation load calculations, U-Factors calculations, and psychometric analysis for each room and each zone. Accompany these calculations with the architectural drawings 1/8"=1'-0" (1:100) scale and Model showing correlation between each zone boundary and the floor area and abbreviated/coded room numbers used with computer input data sheets. Submit the input manuals for the computer programs with indications of the capabilities and limitations of the programs. Submit a level of detail of the calculations consistent with the development of the architectural drawings. Initial load calculation submissions may be zone level calculations with subsequent submissions being room-by-room and zone level. |  | P | F
M-2.5 | Calculations |  |  | Piping Stress Analysis |  |  | Provide piping thermal expansion/stress analysis for all steam and steam condensate systems (and other piping system 6 inches and larger) including calculations for all piping supports, hangars, anchors and expansion loops. Provide node to node diagrams coordinating the locations with the analysis. For all other piping systems, provide support and hanger load calculations and locations. |  | P | F
M-2.6 | Calculations |  |  |  | Air-Handlers |  | Provide capacities of all AHU's, exhaust fans, ventilating units including air flow, static pressure, and required fan-motor horsepower. The leakage of air delivery systems shall be accounted for. Provide psychometric charts for each air-handling unit showing the entire psychrometric process including the cooling and heating coil condition and computation of humidification loads. Include epidemic mode for AHUs for the zones/areas defined by VA Design Manual. |  | P | F
M-2.7 | Calculations |  |  | Chilled Water Plant |  |  | For the proposed chilled water plant, submit:
M-2.8 | Calculations |  |  |  | Quantity |  | Quantity and type of chillers, capacity in tons of refrigeration including equipment process load, and the electrical requirements. |  | P | F
M-2.9 | Calculations |  |  |  | Pertinent Data |  | Pertinent data for the chilled water plant accessories, that is, chilled water and condenser water pumps, and cooling tower. |  | P | F
M-2.10 | Calculations |  |  |  | Coordination |  | Coordination of the cooling tower location with other disciplines for calculations on items related to cooling towers. |  | P | F
M-2.11 | Calculations |  |  |  | Acoustics |  | Sound/acoustic and dispersion analyses to ensure that the noise generated by the air-handling units and the fans comply with VA requirements and the design does not pose any potential for short-circuiting of air or health hazard due to emissions by cooling tower, emergency generator, or boilers. |  | P | F
M-2.12 | Calculations |  |  |  | Acoustics |  | Acoustic analysis of all systems and steps taken to ensure compliance with the specified noise levels in coordination with other disciplines. |  | P | F
M-2.13 | Calculations |  |  |  | Exhaust Dispersion |  | Provide exhaust dispersion analysis for all exhaust sources and intakes per the VA HVAC Design Manual (e.g. boilers, emergency generators, laboratory exhaust, cooling towers etc.). |  | P | F
M-2.14 | Calculations |  |  |  | Backup |  | Provide back-up details and calculations of the chilled water optimization study and selected pumping arrangement. |  | P | F
M-2.15 | Calculations |  |  | Heating System |  |  | For the heating system, submit:
M-2.16 | Calculations |  |  |  | Heating Requirements |  | Total heating load based on the space heating requirements, domestic hot water load, humidification loads, and the equipment steam demand. |  | P | F
M-2.17 | Calculations |  |  |  | Zoning |  | Written description of the proposed zoning of the heating system indicating such features as distribution of ventilation load, perimeter heat load, and reheat load associated with air terminal units. | P | U | F
M-2.18 | Calculations |  |  | Energy Analysis |  |  | Energy analysis with optimized envelope and glazing properties, and all reductions necessary to achieve the federally mandated energy consumption target. State all occupancy, regulated and unregulated load assumptions, and schedule parameters used in the analysis. State all modeled system operational characteristics. Use actual equipment performance curves from the design selections (mechanical, plumbing, and lighting). | P | U | F
M-2.19 | Calculations |  |  | Preliminary Electrical Power |  |  | Indicate requirement of normal or emergency power for each piece of equipment. | P | U | F
M-2.20 | Calculations |  |  | Ventilation Rates |  |  | Table of ventilation rates for each space showing ASHRAE 170, ASHRAE 62.1 and VA Design Manual calculated rates and the governing values. | P | U | F
M-2.21 | Calculations |  |  | Steam Consumption |  |  | Estimated steam consumption from all sources. | P | U | F
M-2.22 | Calculations |  |  | Room-by-room Calculations |  |  | For room-by-room calculations, submit:
M-2.23 | Calculations |  |  |  | Coil/Fan-Motor Gains |  | Coil entering and leaving conditions and fan-motor heat gains for supply and return air fans. |  | P | F
M-2.24 | Calculations |  |  |  | Balance Sheet |  | Room‑by‑room air balance sheet for each air-handling unit and room showing supply, return, exhaust, make‑up, and transfer air quantities with the required air balance (e.g. positive, negative, or neutral) with respect to adjoining spaces. Provide AII and PE isolation room differential pressure calculations based on the VA air pressure setting requirement. Demonstrate overall building positive air balance. |  | P | F
M-2.25 | Calculations |  |  | Equipment Spreadsheet |  |  | Excel spreadsheet for each air-handling system. Provide the details of supply, return, exhaust, make-up, and relief air, for each room. In addition, for each room provide area, height, volume, value of one air change per hour, actual calculated air changes per hour, and required minimum air changes per hour. Show pressurization, and space loads to be able to verify that the supplied airflow is sufficient to meet those requirements. |  | P | F
M-2.26 | Calculations |  |  | HVAC Equipment |  |  | Complete engineering calculations and selection of major HVAC equipment, such as chillers, cooling tower, air-handling units, heating and ventilating units, return and exhaust fans, circulating pumps, and energy recovery equipment, heat exchangers, PRV stations, and humidification equipment. |  | P | F
M-2.27 | Calculations |  |  | Chiller Plant |  |  | Analysis for use of a chiller plant waterside-economizer cycle. | P | U | F
M-2.28 | Calculations |  |  | Flow & Head |  |  | Flow and head calculations for pumping systems for peak and minimum block loads.
M-2.29 | Calculations |  |  |  | Pumps |  | Selection of all pumps with the pump head calculations based on the actual piping layout and takeoffs, and pressure drop through the equipment selected for the systems. |  | P | F
M-2.30 | Calculations |  |  |  | Fans |  | Selection of all fans with the fan static pressure calculations based on the actual duct layouts and takeoffs, and static pressure drop through the equipment for the systems. (Detailed calculations are required even if variable speed drives are used.) |  | P | F
M-2.31 | Calculations |  |  |  | Expansion Tanks |  | Sizing and selection of all expansion tanks based on the actual piping layout and volume computation. |  | P | F
M-2.32 | Calculations |  |  |  | Convertors |  | Sizing and selection of all steam to hot water convertors and heat exchangers based on the flow requirement of each terminal unit, that is, duct-mounted reheat coil, box (air terminal unit). mounted reheat coil, unit heaters, convectors, finned tube radiators, and radiant ceiling panels. |  | P | F
M-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
M-3.1 | Drawings |  |  | Floor Plans |  |  | Submit Floor Plans depicting the following:
M-3.2 | Drawings |  |  |  | Distribution |  | 1/8"=1'-0" (1:100) scale HVAC floor plans for typical areas showing the proposed routing of the main air distribution and piping layouts. Ductwork and piping may be shown in single line. Provide other formats as per the VA BIM STANDARD. | P | U | F
M-3.3 | Drawings | [5 empty] | 1/8"=1'-0" (1:100) scale HVAC floor plans for all areas showing (at minimum) main supply, return, and exhaust air ductwork with sizes based on the updated calculations. Show single line ductwork floor plans for proposed main distribution ducts be provided starting at SD1. This helps to identify choke points and verify floor to floor heights. Finally, main ductwork should be shown in two line format starting at DD. | P | U | F
M-3.4 | Drawings |  |  |  | MERs |  | 1/4"=1'-0" (1:50) floor plans of the typical mechanical equipment rooms (MERs) with at least two cross-sections showing all floor and ceiling mounted equipment, major ductwork, and piping. Show all ductwork and piping. The floor plans must show clearance requirements including code clearances or manufacturer's recommendations for operations and maintenance, whichever is more stringent. The footprints shown for AHUs and major equipment should be based on the proposed equipment (basis of design). | P | U | F
M-3.5 | Drawings |  |  |  | Mechanical Spaces BIM Walk-throughs |  | Live BIM walk-throughs of the mechanical spaces as defined in the VA BIM STANDARD. |  | P | F
M-3.6 | Drawings |  |  |  | Mechanical Rooms |  | Locations and sizes of all mechanical equipment rooms and principal vertical shafts. | P | U | F
M-3.7 | Drawings |  |  |  | Layout |  | Interdisciplinary layout of mechanical room equipment showing all major pieces of equipment and their required operational and maintenance clearances. Drawings must get progressively detailed where the first submission may be a block layout and later submissions showing all individual equipment. Interdisciplinary equipment (e.g. motor controllers, electrical panels, controls cabinets etc.) must be included to the level needed to demonstrate overall space and clearances. | P | U | F
M-3.8 | Drawings |  |  | Diagrams |  |  | Submit the following diagrams, as per the VA BIM STANDARD and below: | P | U | F
M-3.9 | Drawings |  |  |  | Single-Line |  | Single-line air and water flow diagrams of existing heating plants, cooling plants, air-handling processes, and zone level (not space level) air and water distribution for the proposed options. |  | P | F
M-3.10 | Drawings |  |  |  | Flow & Riser |  | Flow and riser diagrams for each air handling systems, exhaust (general and special) systems, and all hydronic systems, such as: chilled water system, hot water system, steam system, and glycol heat recovery system. Where interfacing with existing systems, submit existing capacities and loading of these systems, and new estimated loads with pumping arrangement, and control valves for complete understanding of existing systems to be used or interfaced with the new systems. |  | P | F
M-3.11 | Drawings | [5 empty] | Airflow relationship diagram indicating “clean” areas that are positively pressurized with respect to adjoining areas and the “dirty” areas that must be under negative pressure with respect to adjoining areas, including but not limited to SPD, labs, ORs, vivarium, and isolation rooms. | P | U | F
M-3.12 | Drawings |  |  |  | Control Systems |  | Updated control diagrams for each type of typical air and hydronic system used for development in previous submission by providing written description of the sequence of operation on the floor plans. Explain the function and role of each control device and describe the safety/alarms and normal operating controls of each system. Submit a schedule showing electrical control interlock of each component. Submit a single-line diagram of the direct digital control architecture. |  | P | F
M-3.13 | Drawings |  |  |  | Outside/Exhaust/Relief Air |  | Dedicated drawings showing locations of all intakes, reliefs and exhaust sources. Resolve issues affecting air intake louver locations, considering visibility, historical considerations, noise, physical security requirements, hurricane and storms, and health hazard and odors caused by short circuiting of exhaust air from sources such as kitchens, laboratory/fume hoods, isolation rooms, emergency generators, boilers, cooling towers, and idling trucks at waiting areas. Coordinate with the Dispersion Analysis. | P | U | F
M-3.14 | Drawings |  |  |  | Temperature Control |  | Individual room air distribution and temperature control arrangement for all typical spaces, such as patient bedrooms, operating suite, laboratory areas, and conference rooms, on duct and piping layouts. |  | P | F
M-3.15 | Drawings |  |  | Demolition Plans |  |  | Final demolition drawings indicating scope of work for demolition. | P | U | F
M-3.16 | Drawings |  |  | Phasing |  |  | HVAC work associated with phasing plan. (The phasing plan must be be reviewed and approved by the VA Medical Center, in consultation with the VA PM, to address and resolve such issues as vacating occupied spaces and creating swing spaces, scheduling utility shutdowns, and addressing parking and traffic disruptions). | P | U | F
M-3.17 | Drawings |  |  | Design Coordination |  |  | Drawings and Models of the interstitial spaces reflecting layout and service access requirements of all utilities (HVAC, plumbing, electrical and others) and. Provide live BIM interactive reviews for all interstitial and mechanical areas per VA BIM STANDARD. | P | U | F
M-3.18 | Drawings |  |  |  | Clearances |  | Show duct and ceiling clearances, where ductwork crosses, with 1/4’ = 1’0” (1:50) scale for local sections. Show all ductwork, regardless of sizes and/or complexity of layout at true size. Refer to VA BIM STANDARD for modeling requirements. |  | P | F
M-3.19 | Drawings |  |  | Fire Protection |  |  | Coordinate fire/smoke dampers and duct smoke detectors with fire protection engineer and show on HVAC plans. |  | P | F
M-3.20 | Drawings |  |  | Ventilation Rates |  |  | Ventilation rates for all spaces in chart format showing compliance with ASHRAE 62.1, ASHRAE 170 and the VA Design Manual requirements, dehumidification, and pressurization criteria for all spaces occupied, and unoccupied conditions. | P | U | F
M-3.21 | Drawings |  |  | Engineering Control Center |  |  | Planned capabilities, include the features of energy management and conservation. Submit a point schedule for analog/digital input/outputs to be included in Engineering Control Center (ECC). |  | P | F
M-3.22 | Drawings |  |  | Underground Piping |  |  | Extent of the outside chilled water and condenser water piping. Indicate how the piping shall be laid in tunnels, trenches, or by direct burial. For the direct burial layout, show a profile of the relative elevations of the new pipes with the existing utilities and define the scope of work where necessary for re-routing existing utilities. | P | U | F
M-3.23 | Drawings |  |  |  | Large Scale Floor Plans |  | HVAC floor plans for all mechanical equipment rooms, with at least two cross-sections taken at right angles to each other at 1/4” = 1’-0” (6.3500 mm) scale. Show all equipment located on roof and/or grade. Coordinate to show the walking pads in the Model and on the architectural drawings. | P | U | F
M-3.24 | Drawings |  |  |  | Small Scale Floor Plans |  | HVAC floor plans for all areas showing all ductwork and piping at 1/8"=1'-0" (1:100) scale. Include: | P | U | F
M-3.25 | Drawings |  |  |  |  | Duct Pressure | Duct pressure classification and leakage classes on the floor plans for all air distribution systems. Identify the duct sections with demarcation symbols where the change in pressure rating takes place. |  | P | F
M-3.26 | Drawings |  |  |  |  | Duct and Pipe Sizes | All duct/pipe sizes and air/fluid quantities. Ductwork and piping on separate drawings. |  | P | F
M-3.27 | Drawings |  |  |  |  | Layouts | Utilities layout and accessibility of equipment for servicing and maintenance in the interstitial spaces. |  | P | F
M-3.28 | Drawings |  |  |  |  | Quantities | Air quantities for each room and each air inlet/outlet, expressed in cubic feet per minute, and fluid quantity (where required) in gallons per minute (liters per second). |  | P | F
M-3.29 | Drawings |  |  |  |  | Accessories | All volume dampers, fire dampers, smoke dampers, automatic control dampers, rises and drops in ductwork, and air inlets/outlets, on the air distribution floor plans. |  | P | F
M-3.30 | Drawings |  |  |  |  | Specialties | All piping specialties, such as expansion loops, anchors, valves, drip assemblies, and balancing fittings, on the piping floor plans and drain valves at low-points. |  | P | F
M-3.31 | Drawings |  |  |  |  | Room Name/Numbers | Indicate architectural room names and numbers. | P | U | F
M-3.32 | Drawings |  |  |  |  | Smoke/Fire Barriers | Indicate fire walls, fire barriers (including hour rating), smoke barriers, smoke partitions, and smoke compartments. |  | P | F
M-3.34 | Drawings |  |  |  | Water Distribution |  | Outside chilled water and condenser water distribution showing pipe sizes and insulation with plans, profile, sections, details, and all accessories, such as, anchors, expansion loops/joints, valves, manholes, capped and flanged connections, and the interface between the new and existing work. Show rerouting any utilities, cuttings of roads, pavements, and trees, as well as the extent of new and demolition work. | P | U | F
M-3.35 | Drawings |  |  |  | Temperature Control |  | Automatic temperature control drawings. Show all duct detectors, control valves/dampers static pressure sensors, and differential pressure control assemblies, whose actual physical location is critical for the intended sequence of operation on floor plans. For projects involving a central Engineering Control Center (ECC), provide a point schedule with intended analog/digital input/outputs, graphics capabilities, and requirements of the other trades to be included in the ECC. Provide a riser diagram showing locations of all field data-gathering panels and their interface with the ECC. Show the actual location of the ECC and peripherals on floor plans. The written sequence of operation describing the role of each individually numbered device should be shown on the floor plans on the same drawing on which the control schematic diagram is shown. Do not write the sequence in the specifications. Each sequence should describe the start-up, capacity control, safeties, morning warm-up cycle where applicable, and night setback cycle where applicable. | P | U | F
M-3.36 | Drawings |  |  |  | Details |  | Edit VA details to suit the project. Include any special details deemed useful and necessary for the project. |  | P | F
M-3.37 | Drawings |  |  |  | Demo |  | HVAC demolition drawings showing the extent of demolition work. Indicate sizes of ductwork and piping to be dismantled. Show capacities and sizes of the existing equipment to be removed. Show points of connection, disconnection, blank-offs, and dead-end flanges with isolating valves. Coordinate demolition and restoration work with other disciplines. State the revised capacities of the existing systems affected by the demolition work together with additional efforts involved in testing, balancing, and adjusting them. | P | U | F
M-3.38 | Drawings |  |  |  | Architecturally Significant Equipment (ASE) |  | Provide plans at 1/4” = 1’0” (1:50) scale showing location and sizing of utility connections to ASE identified equipment. | P | U | F
M-3.39 | Drawings |  |  |  | Schedules |  | Updated schedules of equipment that includes chillers, boilers, pumps, air handling units, terminal units, cooling towers, and all equipment required for operations. |  | P | F
M-3.40 | Drawings |  |  |  | Steam and Condensate Piping |  | Drawings must demonstrate condensate control features (e.g. piping slope, locations of traps, flash tanks etc.), and flexibility/expansion features (e.g. anchors, expansion compensation, flexible connectors etc.). |  | P | F
|  | STEAM DISTRIBUTION (OUTSIDE) |  |  |  |  | VA submission requirements for Outside Steam Distribution
SD-1.0 | Report |  | BASIS OF DESIGN
SD-1.1 | Report |  |  | Narrative |  |  | Provide a Narrative describing the following:
SD-1.2 | Report |  |  |  | Life Cycle Cost Analysis |  | Life cycle cost analysis for the selected steam distribution systems and selected routing of the system. Analyze the test results on existing systems (where applicable). Consider all other relevant issues. | P | U | F
SD-1.3 | Report |  |  |  | Geotechnical |  | Confirmation of acceptable soil conditions related to classification of underground factory-fabricated pre-engineered systems, if used. | P | U | F
SD-2.0 |  |  | CALCULATIONS
SD-2.1 | Calculations | [5 empty] | Provide steam and condensate loads that shall be imposed on new or existing distribution facilities. | P | U | F
SD-2.2 | Calculations | [5 empty] | Provide calculations of pipe sizing. |  | P | F
SD-2.4 | Calculations | [5 empty] | Provide performance requirements for all steam traps. |  | P | F
SD-2.5 | Calculations | [5 empty] | Provide pipe stress calculations. Select the proper expansion facilities for piping in manholes, tunnels and trenches. |  | P | F
SD-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
SD-3.1 | Drawings |  |  | Site Plan |  |  | Submit a site plan indicating:
SD-3.2 | Drawings | [5 empty] | Description of distribution systems including locations of all manholes and pipe expansion devices including drips and traps. |  | P | F
SD-3.3 | Drawings | [5 empty] | Overall dimensions and arrangement of major piping in trenches and tunnels and other underground utilities. |  | P | F
SD-3.4 | Drawings | [5 empty] | Scaled drawings at 1/4” =1’0” (1:50) of plan views and sections of manholes. |  | P | F
SD-3.5 | Drawings | [5 empty] | Concrete trench, access, and tunnel drawings, indicating the basic piping layout and pipe supports in plans and sections. List all safety devices required. Show standard details for safety device testing requirements for each device including drips and traps. |  | P | F
|  | STEAM GENERATION |  |  |  |  | VA submission requirements for Steam Generation
SG-1.0 | Report |  |  | Assessment |  |  | Submit an initial assessment including the following:
SG-1.1 | Report | [5 empty] | Information on proposed system steam pressures, types of condensate return systems (pumped, gravity, vacuum), and line sizes. | P | U | F
SG-2.0 |  |  | BASIS OF DESIGN
SG-2.1 | Report |  |  | Narrative |  |  | Submit a narrative describing the following:
SG-2.2 | Report | [5 empty] | When a new steam generating facility is proposed, identify the types of fuels evaluated. Submit the rationale for the selected fuel and the rationale for the fuels that were not selected. | P | U | F
SG-2.3 | Report | [5 empty] | Discuss coordination of the metering requirements with the existing facilities, Military installation, or VA Station/campus as applicable and provide a brief description of the scope of work and extent of coordination involved. |  | P | F
SG-2.4 | Report | [5 empty] | Combined new (estimated) and existing steam loads, including maximum and minimum summer and winter demands and total annual production. Provide breakdown of new steam loads into categories of end use, such as building heating, humidification, reheat, domestic hot water, sterilization, line losses, kitchen, and laundry. |  | P | F
SG-2.5 | Report | [5 empty] | Selection of major equipment and calculations of equipment sizing. |  | P | F
SG-3.0 |  |  | CALCULATIONS
SG-3.1 | Calculations |  |  | Calculations |  |  | Submit estimated steam and condensate loads to be carried by the systems. | P | U | F
SG-3.2 | Calculations | [5 empty] | Estimate peak steam demands for the new facilities and any change in existing steam demands. | P | U | F
SG-3.3 | Calculations | [5 empty] | Determine existing maximum and minimum summer and winter steam demands and total annual production, if a steam plant exists. Submit a verification of the accuracy. Include a graph showing the relationship between outside temperature and winter steam demands. | P | U | F
SG-3.4 | Calculations |  |  | Life Cycle Cost Analysis |  |  | Provide life cycle cost analysis of the steam supply system, including fuel selection. Include analysis of the plant location. Present test results on existing equipment and systems; evaluate all other relevant issues. | P | U | F
SG-3.5 | Calculations | [5 empty] | Provide life cycle cost analysis for selected equipment to be applied for heat-recovery. | P | U | F
SG-3.6 | Calculations | [5 empty] | Provide data on emissions regulations and the methods for compliance. | P | U | F
SG-3.7 | Calculations | [5 empty] | Provide piping thermal expansion/stress analysis for all piping systems subject to thermal expansion including calculations for all piping supports, hangers, anchors and expansion loops. Provide node to node diagrams coordinating the locations with the analysis. |  | P | F
SG-3.8 | Calculations | [5 empty] | Provide performance requirements for all control and regulating valves, flow meter systems, steam traps, and heating and ventilating systems. |  | P | F
SG-3.9 | Calculations |  |  | Submissions |  |  | Provide calculations to support the sizing of all major piping systems and pump selection. Include catalog cuts of two manufacturers on all equipment selections. |  | P | F
SG-3.10 | Calculations | [5 empty] | Provide calculations to support steam load and equipment sizing for all major equipment, including boilers, pumps, heat recovery devices, tanks, and emissions control devices. |  | P | F
SG-3.11 | Calculations | [5 empty] | Conduct a stress analysis under all heating loads on piping systems to include each possible valve configuration. |  | P | F
SG-4.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
SG-4.1 | Drawings |  |  | Drawings |  |  | Indicate location of the existing steam plant and location of new or expanded steam generating facilities, as applicable. Show outside fuel related storage and handling facilities. | P | U | F
SG-4.2 | Drawings | [5 empty] | Provide plan layouts for new plant or modification to existing plant, showing location of equipment and personnel facilities. | P | U | F
SG-4.3 | Drawings | [5 empty] | Indicate final location of new steam generating facilities on a site plan. | P | U | F
SG-4.4 | Drawings | [5 empty] | Provide single-line flow diagrams of all systems, feed water, steam, and condensate. (existing and proposed options). | P | U | F
SG-4.5 | Drawings | [5 empty] | Indicate sections of the steam plant showing major equipment, major piping systems, and personnel facilities. | P | U | F
SG-4.6 | Drawings | [5 empty] | Indicate locations of all equipment, major piping, and pipe supports in plans and sections. Show demolition work. Draw plans and sections at 1/4” = 1’0” (1:50) scale. |  | P | F
SG-4.7 | Drawings | [5 empty] | Provide schedules, equipment lists, and site plans. |  | P | F
SG-4.8 | Drawings | [5 empty] | Show access to all equipment and valves that require normal maintenance, testing, or operation to include by-pass valves. DA Tank access to manways, sight glasses, relief valves etc. Boiler and economizer access to all valves. Header Valve access, flow meters, make up valves and by-passes, etc. The boiler bottom blown down valves are located outside of the foot print or vertical plane of the boiler. |  | P | F
SG-4.9 | Drawings | [5 empty] | Provide schematic control diagrams for the burner management system and flame safeguard systems. |  | P | F
SG-4.10 | Drawings |  |  |  | Emissions |  | Verify that a check for changes in applicable emissions regulations that may affect the design or operation of the steam plant has been performed and any necessary changes have been made to the final design. |  | P | F
|  | WASTE DISPOSAL SYSTEMS |  |  |  |  | VA submission requirements for Incineration/Waste Disposal
WD-1.0 |  |  | BASIS OF DESIGN
WD-1.1 |  |  |  | Alternatives for Waste Disposal |  |  | Submit an Basis of Design (BOD) report including:
WD-1.2 | Report | [5 empty] | Analysis of viable alternatives for waste disposal and proposed solution. Provide rationale for the selection or rejection of alternatives. | P | U | F
WD-1.3 | Report | [5 empty] | Description of the proposed systems and equipment. Include quantities and function. Identify and address any related physical security needs. | P | U | F
WD-1.4 | Report | [5 empty] | Provide equipment selections. |  | P | F
WD-1.5 | Report | [5 empty] | Discussion of the existing systems and new system including: | P | U | F
WD-1.6 | Report | [5 empty] | Demonstrate that the waste disposal system complies with regulatory requirements (e.g. incineration system, etc.). |  | P | F
WD-1.7 | Report |  |  | Site Assessment |  |  | Site considerations such as clean/dirty side - dumpster/dock requirements. | P | U | F
WD-2.0 |  |  | CALCULATIONS
WD-2.1 | Calculations |  |  | Calculations |  |  | Estimate the types and quantities of waste that shall be generated by the new facility. Provide life cycle cost analysis on for the new waste disposal system. Present test results on existing systems (if applicable); evaluate all other relevant issues. Provide load calculations on the amount and types of waste and equipment sizing calculations. | P | U | F
WD-2.2 | Calculations | [5 empty] | Identify emissions control devices. |  | P | F
WD-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
WD-3.1 | Drawings |  |  | Plans |  |  | Submit site plan indicating alternatives for locating an incinerator system. Indicate the location of the existing incinerator, if applicable. | P | U | F
WD3.2 | Drawings | [5 empty] | Submit plan view layout of new system or modification to existing system showing locations of major equipment. | P | U | F
WD-3.3 | Drawings | [5 empty] | Provide 1/4” = 1’0” (1:50) scale plans and sections indicating major equipment. | P | U | F
WD-3.4 | Drawings | [5 empty] | Submit locations of all equipment and major piping on 1/4” = 1’0” (6.3500 mm) scale plans and section. Identify and locate HVAC controls, air filtration and circulation. | P | P | F
WD-3.5 | Drawings | [5 empty] | Indicate demolition work on 1"= 50.0' (site plans) and 1/4” = 1”0” (1:50) for interior scale plans and sections. | P | U | F
WD-3.6 | Drawings |  |  | Schedules |  |  | Submit completed schedules and equipment lists. |  | P | F
VA SME
| Tim Beggs |  |  |  |  | Timothy.Beggs@va.gov
| Don Walden |  |  |  |  | Don.Walden@va.gov
| Doug Ryan |  |  |  |  | Douglas.Ryan@va.gov

## Electrical
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | ELECTRICAL |  |  |  |  | VA submission requirements for Electrical
E-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) at each phase with updated information. Report to include:
E-1.1 | Report |  |  | Narrative |  |  | Indicate electrical design approach in narrative form. Describe how the existing site utility service and distribution, switchgear, primary feeders, power transformers, and distribution equipment will supply the new loads for normal, stand-by, and essential electrical systems. If site and utilities are insufficient, provide a description of the upgrades required. | P | U | F
E-1.2 | Report |  |  | Utility Company |  |  | Provide detailed description of the extent of new utility work (if required). | F | R | R
E-1.3 | Report |  |  | Physical Security |  |  | Provide description of physical security requirements and implementation into electrical design. | P | F | R
E-1.4 | Report |  |  | Uninterruptible Power System (UPS) |  |  | Description of requirements for uninterruptible power system (UPS) and loads to be served. (Comply with PSDM for telecommunications areas). | P | F | R
E-1.5 | Report |  |  | Building Electrical Power Requirements |  |  | Provide description of loads associated with normal and essential electrical system and/or stand-by electrical power system to determine preliminary emergency and/or stand-by electrical power generation capacity required to support the building electrical power requirements. | P | F | R
E-1.6 | Report |  |  | Existing Electrical Systems |  |  | Provide a plan describing the impact of the new construction work to the existing electrical power distribution systems. Describe how connection to existing electrical distribution system will occur. | P | F | R
E-1.7 | Report |  |  | Present Demand Load |  |  | Present demand load (medium voltage switchgear and primary feeder) and projected additional load of new construction. | P | U | F
E-1.8 | Report |  |  | Electrical Design Approaches |  |  | Descriptions of the electrical design approaches for the specialty areas (including but not limited to X-ray Rooms, Intensive Care Units and Operating Room Suites). | P | U | F
E-1.9 | Report |  |  | Determination Method |  |  | Provide methodology by which fault current, protective device coordination, arc flash, generator sizing, load, feeder and equipment sizing, voltage drop, harmonic distortion, lightning protection risk analysis, and lighting calculations, grounding system design and initial testing requirements were made. | P | F | R
E-1.10 | Report |  |  | Emergency Power |  |  | Identify the type of emergency power needed; address and classify per NFPA 99 and NFPA 110/111. | F | R | R
E-1.11 | Report | [5 empty] | Provide an evaluation for the selection of battery packs, central inverter, or generator for life safety equipment. | P | U | F
E-1.12 | Report | [5 empty] | Identify largest loads of mechanical systems (for generator sizing and in-phase transfers) | P | F | R
E-1.13 | Report | [5 empty] | Provide a description of the load shed and restoration system. | P | U | F
E-1.14 | Report |  |  | Distribution Panel |  |  | For shelled rooms to be built-out later provide distribution panels of appropriate size to similar equipment. | F | R | R
E-1.15 | Report |  |  | Existing Facility Demand Load |  |  | Existing facility demand load (medium voltage switchgear and primary feeder) and projected additional load of new construction based on square footage. | F | R | R
E-1.16 | Report |  |  | Lighting Control Systems |  |  | Description of Lighting Control Systems. | F | R | R
E-1.17 | Report |  |  | Electrical Site Design |  |  | Description of Electrical Site design requirements:
E-1.18 | Report |  |  |  | Redundant Power Requirements |  | Redundant power requirements and strategy (i.e. primary selective or radial). | F | R | R
E-1.19 | Report |  |  |  | Back-Up Generator Type |  | Describe implementation of back-up generator type (i.e. Central Plant generators or on-site generators). | F | R | R
E-1.20 | Report |  |  |  | Utility Company Requirement |  | Provide previous submission documents modified to meet the utility company's requirements. Update the written summary of proposed electrical service/methods/equipment based on discussions and agreements with the electrical utility. | F | R | R
E-1.21 | Report |  |  | Room Data Sheet |  |  | Coordinate electrical requirements on room data sheets. (See Architectural requirements.) | P | F | R
E-1.22 | Report |  |  | Cut Sheets |  |  | Provide major equipment cut sheets for primary and secondary electrical distribution systems, lighting fixtures, and special equipment. | P | F | R
E-1.23 | Report |  |  | Utility Company Correspondence |  |  | Provide copies of all correspondence and minutes of meetings with all utility company representatives. | P | U | F
E-1.24 | Report |  |  | Utility Company Incoming Service |  |  | Provide written approval by the utility company of the design of the electrical incoming service. | P | U | F
E-1.25 | Report |  |  | Wet Procedure Locations |  |  | For operating rooms, surgical delivery rooms, and similar locations not designed as wet procedure locations, provide an NFPA 99 risk analysis to justify declassification from the code requirement. | P | F | R
E-1.26 | Report |  |  | Code and Criteria |  |  | Identify design references, (VA design guides, NEC, IEE, NFPA, etc.) | F | R | F
E-1.27 | Report |  |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | "Describe seismic requirements and how it will be implemented in equipment, materials, and installation thereof. For existing projects, analyze impact of seismic correction on all electrical system and determine changes necessary to implement. | P | F | R
E-2.0 |  |  | CALCULATIONS
E-2.1 | Calculations |  |  | Existing Peak Demand |  |  | Existing peak demand readings at point of connection to serve new equipment/building. | F | R | R
E-2.2 | Calculations |  |  | Normal Power System |  |  | Normal power system load calculations to support electrical equipment sizing and ratings. 'Demand factors' based on the type of load, needs to be applied. | P | U | F
E-2.3 | Calculations |  |  | Stand-By Power System |  |  | Stand-by power system load calculations associated with essential electrical system and/or stand-by electrical power system to determine emergency and/or stand-by electrical power generation capacity required to support the building electrical power requirements. 'Demand factors' based on the type of load, needs to be applied. | P | U | F
E-2.4 | Calculations |  |  | Electrical Systems |  |  | Estimated connected loads based on panel schedules for each area function’s lighting and power, normal and essential electrical systems. 'Demand factors' based on the type of load, needs to be applied. |  | P | F
E-2.5 | Calculations |  |  | Panel and Switchboard |  |  | Panel and switchboard schedules for load analysis. 'Demand factors' based on the type of load, needs to be applied. |  | P | F
E-2.6 | Calculations |  |  | Generator Sizing |  |  | Generator sizing calculation based upon input loads by Automatic Transfer Switch (ATS) system, load steps. Apply seasonal demands to narrow down the generation capacity of the essential power system. 'Demand factors' based on the type of load, needs to be applied. | P | U | F
E-2.7 | Calculations |  |  | Lightning Protection |  |  | Lightning protection risk analysis. | F | R | R
E-2.8 | Calculations |  |  | Generator Fuel Storage |  |  | Generator fuel storage requirements. | P | F | R
E-2.9 | Calculations |  |  | Faults and lighting |  |  | Fault current, protective device coordination and lighting calculations. |  | P | F
E-2.10 | Calculations |  |  | Faults |  |  | Provide calculations for arc flash, voltage drop, harmonic distortion. |  | P | F
E-3.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
E-3.1 | Drawings |  |  | Utilities |  |  | Identify, locate, and determine capacity (if applicable) of normal power, emergency power, and pathways for low voltage systems. | P | U | F
E-3.2 | Drawings |  |  | Site Plan |  |  | Site plan(s) showing existing and new underground work for electrical power distribution system. Coordinated drawings shall show all new services to site and buildings; all new medium voltage cable installations; all manholes, duct banks, transformers, roadway, parking, and grounds lighting; and the medium voltage service point. | F | R | R
E-3.2 | Drawings |  |  | One-Line Diagram |  |  | Provide one-line diagram for medium voltage (below 69kV) and low voltage (below 600V) electrical power distribution system. One-line diagram shall show major normal, essential electrical, and standby electrical systems, main electrical components, and the correlation between the systems. | P | U | F
E-3.3 | Drawings |  |  | Main Electrical Areas |  |  | Plans showing locations of main electrical areas, such as main electrical switchgear, main electrical vaults, generator rooms, and/or energy center and indicating their approximate dimensions. On the plans, show outlines of major electrical equipment items in these rooms, nurse call, PA, intercom and outlines of minimum working clearance as required by the applicable National Electrical Code. | P | U | F
E-3.4 | Drawings |  |  | Large Scale Lighting Plan(s) |  |  | Plans showing lighting for key rooms/areas (i.e. public lobbies, conference rooms, patient rooms). Provide plans at 1/4” = 1’0” (1:50) minimum scale. | P | U | F
E-3.5 | Drawings |  |  | Large Scale Main Electrical Areas |  |  | Provide plans (main electrical room layouts) at 1/4” = 1’0” (1:50) minimum scale. Electrical equipment rooms and electrical closets shown stacked vertically. Show all electrical power distribution equipment to scale. Include clearances for installation in front, side and top as per NEC' required clearances for safety, maintenance, and operation of equipment. Mechanical ductwork, water pipes, etc. do not run over panels. | P | U | F
E-3.7 | Drawings |  |  | Demolition Plan |  |  | Demolition drawings, indicating scope of work for demolition, spaces to be made available from demolition, and construction phasing impacts of demolition. | P | U | F
E-3.8 | Drawings |  |  | One-Line Diagram |  |  | System furniture wiring requirements (If applicable) | P | F | R
E-3.9 | Drawings |  |  | Electrical Plan(s) |  |  | Provide 1/8” = 1’-0” (1:100) scale floor plans that show all power, signal, and lighting layouts. Lighting for key rooms/areas. Show room titles on floor plans. Show location of all equipment, lighting fixtures, outlets, and devices. Provide complete wiring/circuiting of devices and equipment. Show motor protective devices, and controller and feeder sizes. Show proposed phasing scheme of electrical work if applicable. | P | U | F
E-3.10 | Drawings |  |  | Architecturally Significant Equipment (ASE) |  |  | Provide 1/4” = 1’0” (1:50) scale plans showing location and sizing of utility connections to ASE identified equipment. | P | U | F
E-3.11 | Drawings |  |  | Legend / Details / Schedules |  |  | Provide legend symbol list, abbreviations, details and schedules. Schedules shall include transformer, distribution switchboard, distribution panelboards, and branch-circuit panel board load schedules. | P | U | F
E-3.12 | Drawings |  |  | Final Drawings |  |  | Final drawings signed and sealed by Engineer of Record registered in the jurisdiction where the project is to be built. |  |  | F
VA SME
| Dat Tran |  |  |  |  | Dat.Tran2@va.gov
| Hy Dang |  |  |  |  | Hy.Dang@va.gov

## Telecommunications
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | TELECOMMUNICATIONS |  |  |  |  | VA submission requirements for Telecommunications
T-1.0 |  |  | BASIS OF DESIGN |  |  |  | Submit the Basis of Design (BOD) report updated at each submittal with the following information:
T-1.1 | Report |  |  | Narrative |  |  | The Telecommunications Basis of Design Narrative is a description of each communications system required in the project: its function, criticality, connectivity, integration and dependencies on other systems, owner, operator, and provider. The Narrative includes any initial assumptions and unknowns in each submittal that need to be mitigated prior to subsequent submittals, or Final Design. The Narrative includes the locations of major systems components, any systems required supporting infrastructure, compliance information, and important design decision reasoning (only associated with design development in each submittal, except for the final design submittal where all reasoning is included); based on existing requirements, other developing systems or facilities designs and requirements, other existing and changed conditions, meeting discussions and design review comments. These items and additional Narrative items are provided in subsections of this Topic below. | P | U | F
T-1.2 | Report |  |  |  | System Compliance |  | Confirmation that all provided systems, spaces, and supporting infrastructure provided under contract are compliant with VA Technical Information Library (TIL) Manuals, Guides, Specifications, and Telecommunications Requirements documentation, as well as the applicable codes, and standards, and guides as identified in the RFP, amendments and contract modifications. | P | U | F
T-1.3 | Report |  |  |  | Programming Differences |  | Validate all interconnected systems' interfaces, hardware, software, cabling, and connectors are compatible, and that software can be programmed to insure successful operations between systems and equipment. | P | U | F
T-1.4 | Report |  |  |  | Interdisciplinary Coordination |  | Confirm coordination with all applicable disciplines for the telecommunications requirements in this report. | P | U | F
T-1.5 | Report | [5 empty] | Provide proprietary systems identified in the RFP, and any systems identified post construction contract award. | P | U | F
T-1.6 | Report |  |  |  |  | Electrical | Identify power requirements for telecom needs. Detail the planned power density of equipment at the IT equipment enclosure level at ultimate design loading conditions. Describe how power capabilities will increase to achieve ultimate design loads in the design. Identify branch for each system (i.e. mass notification on LS or nurse call on critical). | P | U | F
T-1.7 | Report |  |  |  |  | Mechanical | Identify HVAC requirements for telecom needs. Detail the HVAC systems and operating parameters planned for entrance rooms, MCR, and TRs. Describe how HVAC capabilities will increase to achieve ultimate design loads in the design. | P | U | F
T-1.8 | Report |  |  |  |  | Mechanical | Describe how the Computational Fluid Dynamics (CFD) assessment of the design of the MCR at commissioning load, ultimate design load, and in all contingency conditions satisfies the environmental parameters of published standards. Describe the process, setpoints, and outcomes of the CFD analysis. | P | U | F
T-1.9 | Report |  |  |  | Expandable Design |  | Ensure design of communications pathways and spaces with allowable future growth | P | U | F
T-1.10 | Report |  |  |  |  | LED Lighting | Assess additional requirements on Telecommunications for new technologies such as advancements in LED lighting. | P | U | F
T-1.11 | Report |  |  |  |  | Power over Ethernet (PoE) requirements | Perform Risk Assessment AND Cost Benefit Analysis (CBA) FOR EACH (Unless OEM incorporates PoE as a part of their equipment and system), FMS, Critical, Emergency, Life & Public Safety, Medical and OIT Communications Equipment and Systems THAT MAY REQUIRE CAT 6A cable, and incorporate estimated PoE requirements for other systems (etc. lighting, electrical, etc.) to determine TOTAL COST AND SITE PREP IMPACT FOR PROJECT. Each equipment AND system require this study on a case-by-case bases. | P | U | F
T-1.12 | Report |  |  |  | Physical Security Design Resiliency Manual (PSDRM) Requirements. |  | Provide a summarized description of the resultant RFP PSDRM evaluation results regarding telecommunications, integration, infrastructure and space requirements. | P | U | F
T-1.13 | Report |  |  |  | Cybersecurity Requirements. |  | Provide a summarized description of the cybersecurity requirements for each system, submittals and responsible parties associated with each. | P | U | F
T-1.14 | Report |  |  |  | Commissioning |  | Provide a summarized description of commissioning for systems identified in the RFP, include special considerations or requirements. Coordinate the commissioning and testing of power and HVAC systems with the testing of communications systems monitoring and alerting systems to insure that during those supporting systems outages and cutovers that the status of (directly or indirectly impacted) critical communications equipment, connected systems, and environment is being monitored correctly, and that automated notification is provided the appropriate personnel. | P | U | F
T-1.15 | Report |  |  |  | Telecommunications Related Phasing |  | Coordinate and track schedules of communications systems and facilities construction milestones: accreditation, procurement, installation, integration, testing/commissioning, and approvals. Within the Narrative provide the design and coordination status for each system, dependencies, issues, resolved issues, and critical milestones with responsible parties. | P | U | F
T-1.16 | Report |  |  |  | FMS Systems |  | Complete Vetted List is Required (The information within PG 18-12 for Facilities Management Service (FMS) Communications Systems and Equipment is confusing, and may need to be expanded or changed. This includes but is not limited to: Nurse Call and/or Code Blue; Picture Archiving and Communication Systems (PACS); Television (Master Antenna [MATV], Community Antenna [CATV], Closed Circuit [CCTV] [for education] & Satellite TV [SATV]; Radio (Paging [Code Blue, Emergency & Routine]), Microwave, Satellite Radio/Telephone & Radio Entertainment; Public Address (Overhead Paging, Mass Notification, and intercommunications [Intercom]); Physical Security Management (Access Control, Motion Intrusion Detection, Duress and/or Panic Alarm & Security Surveillance Television [SSTV]); Patient, Staff and Asset Monitoring (Medical Telemetry, Patient/Staff Location, and Cardiac); Energy Management; Emergency (Fire Alarm/Mass Notification, Police, and Disaster). These systems and equipment are located in the FMS area of Telecom Rooms and Antenna Equipment Headend Rooms. | P | U | F
T-1.17 | Report |  |  |  | OIT Systems |  | From the FMS Systems definition in the PG 18-12 Design Guide 2011. Headend, host servers, or equipment associated with archiving, packetized storage, or transport of confidential info generated by FMS systems will be serviced and managed by OIT. From the OIT Systems definition in the PG 18-12 Design Guide 2011. OIT equipment is not permitted to actively process life safety data, nor any FMS systems data. | P | U | F
T-1.18 | Report |  |  |  | Commercial or Other Systems |  | Provide specific descriptions of the commercial and other systems required per the RFP, including the example systems listed below. | P | U | F
T-1.19 | Report |  |  |  |  | FMS | Provide specific description of the required FMS Emergency Voice System (not VoIP or call manager) function and operation ensuring it replaces the PBX that normally handles them. Ensure location, type, and quantity for required FMS emergency voice (not VoIP or call manager) interfaces and operates with like communications systems. Use CFM approved TIL Master Specification 27 31 00-Emeergency Voice Switching Equipment and System; or, 27 31-31 Emergency Voice Switching Equipment and System Extension for this purpose. | P | U | F
T-1.20 | Report |  |  |  |  | DAS | Distributed Radio Antenna (Within Building) Equipment and System (DAS), ensure the DAS is provided in each VA Medical and Administrative Facility, per Homeland Security (HLS) direction after 9-11. Use CFM Approved TIL Specification 27 53-19 – DISTRIBUTED RADIO ANTENNA (WITHIN BUILDING) EQUIPMENT AND SYSTEM. Ensure the edited specification specifically describes and requires the DAS is used FOR ONLY EMERGENCY RESPONDER USE WITH NO ADD ONs. | P | U | F
T-1.21 | Report |  |  | Room Data Sheet |  |  | Coordinate telecommunications requirements with room data sheets. (See Architectural requirements.) | P | U | F
T-1.22 | Report |  |  |  |  | Cabling | Determination of all cabling requirements, types, counts and accessories. Ensure all national code analog equipment and cables types and counts are addressed. | P | U | F
T-1.23 | Report |  |  |  |  | Sizing | Confirmation that telecommunications space physical sizing, interconnection and locations are addressed. | P | U | F
T-1.24 | Calculations |  |  |  |  | Calculations | Show calculations for the following systems. a. Television loss calculations for coax based systems b. Antennae systems calculations for signal level and loss. c. Public Address Amplifiers Power calculations. d. Calculations to justify the size of each cable, raceway, and cable tray for both inside plant and outside plant e. Power Over Ethernet Type and Temperature Rise Calculations for Cable Gauge, Temperature Rating Selection and Bundling. f. Submit heat map for Wireless Local Area Network design | P | U | F
T-1.25 | Report |  |  |  |  | MCR | If new MCR is being constructed, description of structured cabling backbone between new MCR and campus TRs. Describe how existing MCR-TR fiber backbone will be switched over to new diverse path MCR-TR fiber backbone runs terminating in the new MCR. | P | U | F
T-1.26 | Report |  |  |  |  | MCR | If new MCR is being constructed, description of structured cabling elements within the MCR (between MDAs and HDAs and between HDAs and server cabinets). Describe any applicable seismic requirements and how those requirements will be implemented for communications infrastructure and equipment. | P | U | F
T-2.0 |  |  | VA ACQUISITION CODES
T-2.1 | Aggregate |  |  | Responsibility Matrix: Supplier/Installer |  |  | Consult with Project VA Representatives with respect to identifying any changes to or within the source documents in the PG 18-5 Equipment Guide List (https://cfm.va.gov/til/equip.asp) and the PG 18-12 OIT Design Guide 2011 document. These have the documents for planning and developing equipment requirements for Veterans Affairs (VA) facilities. Acquisition Codes are here and the code has two parts, first is the responsible party for furnishing item/system, then the responsible party for installing item/system; where "V"=VA, and "C"=Contractor. For example "VC" means VA furnished, and Contractor Installed. Note per the DVA EPgMP there is also a VA Furnished Contractor Relocated (VCR) code. The PG 18-5 (https://cfm.va.gov/til/equip.asp) has a listing of services, departments, and spaces, each with equipment and acquisition codes. The PG 18-5 (https://cfm.va.gov/til/equip.asp) also contains the following: Equipment Guide List Index, Veterans' Health Administration (VHA) guides. Can Download (All VHA sections), or (VBA and NCA sections). | P | U | F
T-3.0 |  |  | APPROVALS
T-3.1 | Report |  |  | AHJ Approval |  |  | TIP, FMS, and Spectrum Management verified by AHJ SMCS (see TDM). Contact AHJ SMCS for technical assistance if required at any point throughout the design. Telecommunications space (entrance rooms, MCR, TRs) verified by OIT Data Center & Infrastructure Engineering project. | P | U | F
T-3.2 | Report |  |  | Utility Company Approval |  |  | Describe the extent of utility company work required. Include copies of all correspondence and minutes of meetings with all utility company's representatives. | P | U | F
T-3.3 | Report | [5 empty] | Provide copies of all correspondence and minutes of meetings with utility company representatives. Include a written summary of any conversations with the telecommunications utilities. | P | U | F
T-3.4 | Report | [5 empty] | Provide written approval by the telecommunications utility companies of the design for incoming services. | P | U | F
T-4.0 |  |  | DRAWINGS and MODELS |  |  |  | As per the VA BIM STANDARD and below
T-4.1 | Drawings |  |  | Symbols, Notes, & Abbreviations |  |  | Include a drawing identifying telecommunications symbols, notes and abbreviations for the 2D documentation. | P | U | F
T-4.2 | Drawings |  |  | Interdisciplinary Coordination |  |  | Confirm coordination of allocation for telecommunications equipment installation, connection, and space requirements with other disciplines (Architect, Electrical, Plumbing, Civil, Structural, etc.) | P | U | F
T-4.3 | Drawings |  |  | Expandable Design |  |  | Ensure design of communications pathways and spaces with allowable future growth. | P | U | F
T-4.4 | Drawings |  |  | Location of Telecommunications Spaces |  |  | Confirmation that telecommunications spaces are not located next to elevator machine room, electrical room, surgical room and associate areas, radiology, MRI et cetera. | P | U | F
T-5.0 |  |  |  | Diagrams |  |  | Submit the following diagrams:
T-5.1 | Drawings |  |  |  | Phasing |  | Proposed Phasing for FMS Special and OIT Communications work. | P | U | F
T-5.2 | Drawings |  |  |  | Conceptual |  | Updated conceptual diagrams for all proposed and connected communications systems, including, but not limited to FMS Special Communications and OI&T Communication Infrastructure System Plant (TIP). | P | U | F
T-5.3 | Drawings |  |  |  | Zoning |  | Zoning diagram for above ceiling utilities. Show the areas served by each FMS Special Communications and OIT telecommunications room and for the zones for the Public Address system. Zoning diagram should detail the floor area served by each Telecommunications Room to ensure that maximum cable distances between the TR and the work area outlets is within specification. Zoning diagram should also include all telecommunications services supported by each TR, including video distribution, nurse call, et cetera. Show pathways and conveyance equipment, identifying capacities and proposed cable loads. Provide unique Nurse Call Zone light Identifiers and a Provide Zone Light Activation Matrix. Perform Diamond Analysis for horizontal distribution. | P | U | F
T-5.4 | Drawings |  |  |  | Electrical |  | One‑line and riser diagrams of the normal electrical power and the emergency power distribution. Locate, size, and identify electrical, FMS & OIT Communications and Interface Systems as approved by the Electrical Engineer and RCDD FMS & OI&T Communications Design Professional(s). Show typical branch circuit wiring of offices, exam rooms, patient rooms, and lab areas. One-line electrical should show power distribution to MCR and each TR, including the branch circuit configuration for racks, cabinets, and supporting mechanical equipment in each space. | P | U | F
T.5.4.1 | Drawings |  |  |  |  | Bonding | Telecommunications Bonding and Grounding Diagrams and Details are within the Telecommunications Drawing Package and these supplement Electrical Power and Safety Bonding and Grounding Diagrams and Details within the Electrical Drawing Package. Bonding plan for the site, building, telecommunications spaces, racks, and cabinets. Include unit bonding conductors, rack bonding busbars, rack bonding conductors, telecommunications bonding conductor, cable tray bonding conductors, primary bonding busbar, secondary bonding busbars, and connecting paths. Routing for bonding conductors should be shown in both plan and elevation views. Demonstrate TIA-607 compliance. | P | U | F
T.5.4.2 | Drawings |  |  |  |  | Power Chain | Show electrical distribution for IT equipment enclosures at the room and rack/cabinet level for the entrance rooms, MCR, and TRs. Distribution components such as busbars, taps, Zone PDUs, and Rack PDUs should be identified. | P | U | F
T-5.5 | Drawings |  |  |  | Riser Diagrams |  | Ensure items included for PSRDM criticality and redundancy, and in compliance with NFPA 99 Category 1 and 2 requirements for redundancies and single point of failure. FMS Special Communications and OIT Communications TIP Riser Diagrams; ensure design does not have a single point of failure. Riser diagrams also need to show all systems interfaces. Telecommunications riser diagrams should include all telecommunications media, the associated pathways, the media specifications, media quantities and cable fiber counts from building entrance to all distribution spaces. Conduits or sleeves connecting stacked TRs should be detailed with size and quantity. | P | U | F
T-5.6 | Drawings |  |  | Site Plan |  |  | Site plan updated to show existing and proposed FMS, OIT and other telecommunications services and infrastructure required by the project, including those items identified in the PSRDM and as required by NFPA 99 Category 1 and 2 systems. (Ensure the TIP does not have a single point of failure especially at the MCR.) Site plan must include maintenance hole locations, vault locations and specifications, pedestals, monuments, conduit pathways, and pathway specifications. | P | U | F
T-5.7 | Drawings | [5 empty] | Identify diversely routed distribution pathways between entrance rooms, MCR, and TRs for the campus. | P | U | F
T-5.8 | Drawings |  |  | Demolition Plans |  |  | Demolition plans shall Identify all telecommunications services and work required by the site (including existing to be retained) to be renovated. If an entire wing or area is demolished, provide reference note(s) to the architectural drawings. | P | U | F
T-5.9 | Drawings |  |  | Telecommunication Spaces |  |  | Provide 1/8” = 1’0” (1:100) scale floor plans showing all telecommunications equipment area layouts. | P | U | F
T-5.10 | Drawings |  |  |  | Locations |  | Telecommunication space risers to include 3D (BIM) model to verify vertical alignment. | P | U | F
T-5.11 | Drawings | [5 empty] | Provide locations for the Telephone Room, Entrance/DEMARC Rooms, Engineering Control, Police Control, Emergency Management Control and OSP Emergency Management Control (if not a part of the EMCR) Rooms on the Telecommunications Drawings. | P | U | F
T-5.12 | Drawings | [5 empty] | Ensure all telecommunications rooms, MCR, Antenna Head End and like areas (see minimums in T-5-11) do not have illegal obstructions present in and around (provide VA required EMI, RFI & EI filtering) each location, are shown on the Telecommunications Drawings. | P | U | F
T-5.13 | Drawings |  |  |  | Equipment |  | Identify all major FMS & OIT communications equipment and other systems equipment (regardless of provider) are drawn to scale. Ensure all means and OSHA clearances and other identified accessibility requirements are provided for installation, maintenance, servicing, removal and replacement of telecommunications equipment and systems are depicted and noted on the Telecommunications Drawings. | P | U | F
T-5.13.1 | Drawings | [5 empty] | Provide data on racks, cabinets, and accessories including vertical exhaust ducts, inter-cabinet cable routing and grommets, and cable management accessories (e.g. ring and finger managers, radius bend assists, horizontal and vertical cable managers). | P | U | F
T-5.13.2 | Drawings | [5 empty] | Provide drawing(s) and details of structured cabling plant for the MCR (between MDAs and HDAs and between HDAs and server cabinets). Include media characteristics, quantities, and distances. | P | U | F
T-5.13.3 | Drawings | [5 empty] | Locate FMS & OI&T TIP cable locations. Locate all FMS & OI&T Communications Equipment and Systems are drawn to scale. Indicate FMS & OI&T Communications Equipment and Systems to be installed in the proposed Main Computer, Main Telephone, Telephone Operator’s, Telecommunications, Antenna Head End, Police Control, Engineering Control, Emergency Management Control and OSP Emergency Control (if not a part of the EMCR) Rooms are depicted and noted on the Telecommunication Drawings. Comply with TDM, EDM and OI&T DG. | P | U | F
T-5.14 | Drawings |  |  | Floor Plans |  |  | Provide floor plans including complete notes, legends, symbols list and details. Indicate room titles and area functions, location, and sizes of main computer, telephone room, and telecommunications rooms (ensure FMS and OIT systems are installed in the same room). Show locations of equipment, AC Power and Communications outlets, cable trays, regular and interconnecting conduits. | P | U | F
T-5.15 | Drawings |  |  | Construction Drawings |  |  | Provide telecommunication drawings stamped by certified RCDD professional. | P | U | F
T-5.16 | Drawings |  |  | Floor Plans |  |  | Drawings should show details of all end user devices and outlets. | P | U | F
T-5.17 | Drawings |  |  | Elevations |  |  | Show elevations of FMS, OIT Equipment, MCR and TRs to include back board elevations and interaction of mechanical, electrical, and telecommunications equipment. | P | U | F
T-5.18 | Drawings |  |  | Elevations |  |  | Provide elevation drawings for racks and cabinets showing equipment details (bonding and telecommunications terminations in rack and cabinet elevations including Equipment Distributors, Horizontal Distribution Areas, and Main Distribution Areas). Distribution components such as patch panels, fiber distribution cabinets, cassettes, and cable bundles should be identified by design characteristics, including polarity and required expansion space. Elevations for all wall mounted Displays (monitors/TVs). Elevation details must include dimensioned locations for the display, any backboxes, structural support or backing material, mounting brackets, electrical outlets and communication / low voltage outlets. Electrical outlets and communication / low voltage outlets demonstrating adherence to required separation and the detail should indicate outlet locations do not interfere with intended mounting bracket location. | P | U | F
T-5.19 | Drawings |  |  | Labeling Plan |  |  | Provide plans to properly label telecommunications spaces, equipment, electrical distribution, and telecommunications media. | P | U | F
T-5.20 | Drawings |  |  | CFD Analysis |  |  | Provide drawings from CFD analysis showing the operation of the MCR at commissioning and at ultimate design loading in all necessary normal and contingency operating states to show that the design is efficient and effective. | P | U | F
T-5.21 | Drawings |  |  | Cable Pathway Details |  |  | Provide Outside Plant cable pathway pull plans, rack elevations and cable run lists for all infrastructure for all disciplines to be submitted prior to installation. These would include manhole and vault room drawings showing all wall surfaces in the space and detailing the route and splicing locations of optical fiber cable passing through them (“Butterfly Details”). The underground structures should be detailed on the drawings and be detailed through drawing submittals. | P | U | F
T-5.22 | Drawings |  |  | Seismic Projects |  |  | Provide all details showing the methods of anchoring telecommunications equipment and infrastructure. | P | U | F
T-6.0 |  |  | ANTENNA REQUIREMENTS
T-6.1 | Report |  |  | Antenna |  |  | Ensure Antenna HE Room has properly sized roof or wall coax cable penetrations and roof or wall strengthening is in place to support required and additional radio antennas. The design must not only support roof mounted equipment and infrastructure but also a means to safety support personnel accessing roof mounted communications systems: cell phone, satellite TV, 4G,5G, ELMR antennas, etc., and protective and grounding equipment. | P | U | F
T-6.2 | Report |  |  | Lightning Protection System |  |  | Ensure external Antenna Farm Lightning Protection System is in place and connected to the Facility Lightning Protection System or a certified Earth Ground. | P | U | F
T-6.3 | Report |  |  | CCGS |  |  | Ensure internal Circulating Communications Ground System (CCGS) is in place. | P | U | F
T-6.4 | Report |  |  | SMS-Security Management System |  |  | Ensure Security Management System (SMS) is in place. | P | U | F
T-7.0 |  |  | SPECIFICATIONS
T-7.1 | Report |  |  | Specifications |  |  | Show list of Specifications. | P | U | F
T-7.2 | Report |  |  | Specifications |  |  | Edit and mark-up Specifications. | P | U | F
T-7.3A70:H80H73A71:H80A68:H80H73A71:H80A66:H80H73A71:H80A64:H80H73A71:H80A63:H80H73A71:H80A62:H80H73A71:H80A61:H80H73A71:H80A60:H80H73A71:H80A59:H80H73A71:H80A58:H80H73A71:H80 | Report |  |  | Manufacturer Product Data Used as Specifications |  |  |  | P | U | F
VA SME
| Shawn Lee |  |  |  |  | Shawn.Lee6@va.gov
| Kelly Bates |  |  |  |  | Kelly.Bates@va.gov

## Environmental Compliance
[5 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[6 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | Environmental Compliance |  |  |  | VA submission requirements for Sustainability
EC-1.0 |  |  | BASIS OF DESIGN
EC-1.1 | Report |  |  | Goal |  | The DOR shall identify all applicable Federal, State, and Local Environmental Protection Standards, Regulations and Requirements governing air quality, water quality, solid waste and hazardous waste. Identify all environmental hazards, liabilities, and compliance matters. Identify how to reach such determinations and define approach to mitigating each one. Example areas to identify would be Asbestos Presence and/or Contamination, Lead Contamination, Lead Containing Materials and Building components, Hazardous Materials and/or Waste Storage, Polychlorinated Byphenyls (PCB) containing articles or spilled materials. Document how the existing environmental permits and/or changes to the existing facility environmental permits meets project requirements. Examples are Stormwater Pollution Prevention Plan, Spill Prevention Control and Countermeasures Plan, Hazardous Waste Generator Status. | P | U | F
EC-2.0 | Report |  |  | Environmental Management Plan (EMP) |  | The purpose of the EMP is to present an overview of known or potential environmental issues, requirements, regulations and permits that must be considered and addressed during construction. Incorporate construction related objectives and targets from both CFM Environmental Staff and the facility's Green Environmental Management System Coordinators (GEMS) or Environmental staff into the EMP, as applicable. Include in the EMP measures for protecting natural and cultural resources, required reports, permits requirements, regulatory consultations and other measures to be taken. | P | U | F
EC-2.1 | Report | Identification of Existing Conditions |  |  |  | The below reports shall identify existing conditions at the Site and shall be incorporated into the EMP: | P | U | F
EC-2.2 | Report | Asbestos Management Plan (AMP) |  |  |  | Review facility Asbestos Management Plan and incorporate Project to it. See VHA Directive 7714 for specific requirements. | P | U | F
EC-2.2.1 | Report |  | Develop Implementation Plan for AMP |  |  |  | P | U | F
EC-2.3 | Report | Lead Contamination identification and management. |  |  |  |  | P | U | F
EC-2.4 | Report | Facility Hazardous Waste Management Plan |  |  |  | Incorporate applicable waste identification, characterization, and disposal based on the requirements of the facility as they are ultimately responsible for the handling of the waste. | P | U | F
EC-2.4.1 | Report |  | Regulated waste inventory and determination |  |  |  | P | U | F
EC-2.4.2 | Report |  | Action plan for disposal |  |  | Include method of packaging and disposal as well as treatment standard to be used. Also, include training requirements needed for the removal, collection, packaging and transportation of the hazardous waste identified. | P | U | F
EC-2.5 | Report | Spill Prevention Control and Countermeasures Plan |  |  |  | Provide Spill Prevention Control and Countermeasures Plan. Identity equipment used during construction/demolition activities. | P | U | F
EC-2.6 | Report | Environmental Permit Identification, Submissions and Plans |  |  |  | Prepare a report that confirms the required site environmental permits and required environmental permits necessary for project execution. Document in the plan how all permit requirements, timeframes, agency coordination and required submissions for permit applications and approvals will be achieved. | P | U | F
EC-2.7 | Report | Historic Preservation and SHPO Section 106 Report |  |  |  | The following information shall be prepared by the A-E; a. Brief statement of work for the project. b. A detailed statement as to why replacement is proposed over repair. c. Whether the items being removed/replaced are original to the buildings/structures. If not, when were they installed? d. Dimensions (thickness, height, width), details, materials, and condition (dry rot, broken, etc..) of the items being repaired/replaced. e. One (1) set of 10% plans, specifications, and construction schedule. The AE and/or PM shall forward the submittals via the CFM Environmental Program for review and inclusion in the NEPA Implementation. | P | U | F
EC-2.8 | Report | National Environmental Policy Act Review, Implementation |  |  |  | The AE shall review the project NEPA & NHPA documentation to ensure compliance with conditions of the previously executed NEPA and NHPA documentation and impact analysis as well as all Ft Bliss (Host) environmental Requirements. For the current project the AE and PM shall engage Ft Bliss and VA OCFM Environmental Program to document their compliance with the terms and requirements of the previously executed NEPA documentation and Finding of No Significant Impact. In situations where NEPA documentation is proceeding the design effort, the AE shall provide design information, drawings and site information to Army and VA Environmental Staffs ALONG WITH a report describing how the A/E will ensure compliance during the project with each of the mitigations, restrictions and/or restrictions in the NEPA documents during the project. | P | U | F
EC-3.0 | Drawings | Provide asbestos/lead abatement drawings |  |  |  | Provide Drawings with reports | P | U | F
EC-3.1 | Drawings |  | Temporary Environmental Controls |  |  | The AE shall review the Temporary Environmental Control Specification and or other Project/Site specific Environmental regulatory requirements, to ensure design documents meet the requirements of the specification and include any and all necessary environmental control requirements in the drawings and design package. | P | U | F
EC-3.2 | Drawings |  | Asbestos Abatement |  |  | Provide Drawings with reports | P | U | F
EC-3.3 | Drawings |  | Lead Abatement |  |  | Provide Drawings with reports | P | U | F
VA SME
| Fernando Fernandez |  |  |  | Fernando.Fernandez@va.gov
| Bruce Mack |  |  |  | Bruce.Mack@va.gov

## Sustainability
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | SUSTAINABILITY |  |  |  |  | VA submission requirements for Sustainability
SU-1.0 |  |  | BASIS OF DESIGN
SU-1.1 | Report |  |  | Goal |  |  | Document the project sustainability goals and discuss how they are being accomplished with respect to siting, energy use reduction, potable water use reduction, sustainable materials, renewable energy, and protecting indoor environmental quality. Provide Narrative for each credit; explain why or why not attempting. Identify if Campus or building certification will be used. Submit LEED Score card @ each design submittal. Define which path of LEED is being used (For healthcare, new construction, etc.) Include CFM Sustainability Scorecard as well. Utilize the online LEED system & provide all documentation required to achieve the points attempted. Indicate members of the D-B team that are LEED Accredited Professionals. | P | U | F
SU-1.2 | Report |  |  |  | Registration with LEED Online |  | Register every building in LEED Online. If the Government has not already registered the project, report who is the primary administrator and ensure Government has access to the project online. |  | F | R
SU-1.3 | Report |  |  |  | LEED Design Review Results |  | Provide a copy of the LEED design review report provided by GBCI. Provide one report per building or Campus if applicable. |  |  | F
SU-1.4 | Report |  |  |  | ASHRAE 90.1 Performance (10 CFR 433) |  | Demonstrate that all new buildings within the project: 1) Meet all minimum requirements of the version of ASHRAE 90.1 currently in force under 10 CFR 433.100 (as stated in the RFP), and 2) are designed to perform 30% better than the ASHRAE baseline building, if LCC-effective. If LCC-effectiveness cannot be achieved, demonstrate that energy performance has been optimized to a level that is LCC-effective. | P | U | F
SU-1.5 | Report |  |  |  | Diversion of Construction and Demolition Waste |  | Analyze local markets to determine availability of construction and demolition waste diversion to recycling or reuse opportunities. If opportunities for recycling/reuse exist, ensure that construction specifications require a minimum of 50% diversion. | P | U | F
SU-1.6 | Report |  |  |  | Renewable Energy |  | Demonstrate that a minimum of 10% of the facility's annual electrical energy will be provided from onsite renewable energy. Demonstrate that 30% of the facility's hot water will be provided by solar hot water. (See VA Sustainable Design Manual). | P | U | F
SU-2.0 |  |  | CALCULATIONS
SU-2.1 | Calculations |  |  |  | Renewable Energy |  | Provide calculations showing that 10% of the facility's annual electrical energy will be provide from onsite renewable energy and that 30% of the facility's hot water will be provided by solar hot water. | P | U | F
VA SME
| James Symanski |  |  |  |  | James.Symanski@va.gov

## Historic
[6 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[7 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | HISTORIC |  |  |  |  | VA submission requirements for Historic
H-1.0 |  | BASIS OF DESIGN |  |  |  |  | Submit the Basis of Design (BOD) report updated at each submittal with the following information:
H-1.1 | Report |  |  | Finish Schedule |  |  | Provide Room Finish Schedule in tabular format that identifies room number (both Design & Wayfinding), materials, and color selections for all exposed surfaces as required in H-2.1 as well as for interior spaces and materials identified as historic. (Coordinate with Architecture/Interior) Document compliance with required treatment of historic surfaces and their preservation. | P | U | F
H-1.2 | Report |  |  | Sample Boards |  |  | Provide material and finish sample boards. Provide final colors, finishes, furniture and fabrics, all keyed to floor plans for exterior and interior areas identified as historic only. |  | P | F
H-1.3 | Drawings |  |  | Communicating the Design Aesthetic |  |  | Provide rendered visualizations as noted in the VA BIM STANDARD pursuant to A.3.9 for exterior and interior areas identified as historic only. | P | U | F
H-2.0 |  | SPACE PLANNING
H-2.1 | Drawings |  |  | Zones |  |  | Provide a description of the tentative preservation zoning of interior/exterior spaces. Describe the locations of the each zone, focusing on efforts to maintain original spaces. For exterior and interior areas the identification of preservation zones will be by designations of priorities for protection. Architect will discuss with VA HP Office. | P | U | F
H-2.2 | Drawings |  |  | Swing Space/Design and Construction Phasing Plan (4D) |  |  | If swing space impacts Historic resources or sites, provide a 3D/4D communication plan for swing space and sequence of work. Indicate construction barriers/fences, proposed laydown space and operational logistics. Refer to the VA BIM STANDARD pursuant to A-3.10. | P | U | F
H-3.0 |  |  | ROOM DATA SHEETS |  |  |  | Electronic 2D PDFs (minimum scale 1/4" = 1"-0" (1:50) linked to the plan sets as per the requirements in the DDR for Historic designated spaces only.
H-3.1 | Drawings | [5 empty] | Minimum room dimensions and clearances. (Coordinate with Architecture). | P | U | F
H-3.2 | Drawings | [5 empty] | Door size and special requirements (fire rating, vision panel, finish hardware, access control, etc.)(Coordinate with Architecture/Interior). | P | U | F
H-3.3 | Drawings | [5 empty] | Wall types (fire ratings, shielding, acoustic, etc.). Coordinate with Architecture). | P | U | F
H-3.4 | Drawings | [5 empty] | Architectural casework configuration and location. (coordinate with Architecture/Interior). | P | U | F
H-3.5 | Drawings | [5 empty] | Room Finishes. (Coordinate with Interior). | P | U | F
H-4.0 |  |  | ARCHITECTURAL DRAWING DELIVERABLES |  |  |  | Follow the requirements in the DDR, the VA BIM STANDARD and as noted below for Historic designated spaces.
H-4.1 | Drawings |  |  | Title/Cover Sheet(s) |  |  | Cover Sheets: project name and address, VA project number, location map, signature block, name and address of VA, architect, engineers, and other consultants; Project Data with index of drawings, legend of abbreviations and symbols; Project Codes and Standards Sheet with a list and summary of the applicable project codes, applicable VA Standard Manuals and Guides by name and issuance date. | P | U | F
H-4.2 | Drawings |  |  | Site Plans |  |  | Provide a site plan indicating Historic designated spaces (min. 1"=30.0') indicating demolition, building location, parking, pedestrian and vehicular circulation, emergency vehicle access, loading docks, and all other major landforms and site features. (Coordinate with Civil Engineering discipline). | P | U | F
H-4.3 | Drawings |  |  | Demolition Plans |  |  | Demolition floor and ceiling plans for Historic designated areas to be renovated and areas below where work in space below is required (minimum 1/8"=1'-0" (1:100) with finish schedule and wall types. Coordinate with phasing plans, Interim Life Safety Measures (ILSM) and Infection Control Risk Assessment (ICRA). Describe compliance with VA FPDM Section 1.4. | P | U | F
H-4.4 | Drawings |  |  | Floor Plans |  |  | Provide floor plans showing departmental adjacencies, major circulation routes and layouts for each floor, including interstitial floors, showing internal organization of each department, vertical and horizontal circulation, location of mechanical and electrical equipment rooms, utility shafts, patient and staff entrance, receiving/shipping, and location of section cuts in all Historic designates spaces. (minimum scale 1/16” =1’-0” (1:200). Included column centerline and overall building dimensions. Coordinate with Civil Engineering discipline for finished floor of structures and flood zones. | P | U | F
H-4.5 | Drawings |  |  | Roof Plans |  |  | Provide 1/8"=1'-0" (1:100) scale roof plans depicting all roof features (drains, overflows, slopes, crickets, ridges, valleys, penetrations, equipment, davits, walk pads, etc.). Indicate all green roof types and areas impacting Historic designated spaces. | P | U | F
H-4.6 | Drawings |  |  | Exterior Elevations |  |  | For Historic designated spaces, provide building elevations at a minimum of 1/16"=1'-0" (1:200) with fenestration, penthouses, materials, finish floor elevations, floor-to-floor heights, overall building height, window and louver types, entrances, canopies, skylights, and adjacent grades. Include separate elevations indicating base building with expansion shown on floor plans. Provide building elevations of complex areas at a minimum scale of 1/4"=1'-0" (1:50). | P | U | F
H-4.7 | Drawings |  |  |  | Building Sections |  | For Historic designated spaces, provide building sections at minimum scale 1/16"=1'-0" (1:200) through major portions of building. | P | U | F
H-4.8 | Drawings |  |  |  | Wall Sections |  | For Historic designated spaces, provide wall sections indicating floor-to-floor heights, overall building heights, materials, fenestrations, and assemblies. |  | P | F
H-4.9 | Drawings |  |  |  | Wall Types |  | For Historic designated spaces, provide each wall type at minimum scale of 1"=1'-0" (1:10). Indicate sound attenuation and fire ratings. Identify UL or other acceptable testing agency design number. |  | P | F
H-4.10 | Drawings |  |  | Construction Details |  |  | Construction details at scale large enough to clearly show components and assembly: step construction, wall enclosures, windows, storefront, waterproofing, roof accessories, equipment mounting and suspension shielding, etc. For Historic designated spaces, provide 3D PDF details for all complex roof/wall/window interfaces and include in electronic 2D drawing sets. |  | P | F
H-4.11 | Drawings |  |  | Vertical Transit Plans & Details |  |  | Vertical transit details for stairs, elevators, lifts, dumbwaiters, linen and trash chutes, and pneumatic tube stations. For Historic designated spaces, provide plans at minimum scale of 1/4"=1'-0" (1:50), sections and details at scale large enough to convey design intent. |  | P | F
H-4.12 | Drawings |  |  | Door Schedules |  |  | Door schedule with door and frame details, threshold details, door number, door and frame types, dimensions, ratings, materials, glazing, security requirements, and finish hardware. (coordinate with Architecture). |  | P | F
H-4.13 | Drawings |  |  | Door Types |  |  | For Historic designated spaces, provide graphical depiction of each door type. (Coordinate with Architecture). |  | P | F
H-4.14 | Drawings |  |  | Interior Elevations |  |  | For Historic designated spaces, provide interior elevations at minimum scale of 1/4"=1'-0" (1:50) showing medical gases, power, data, communications, millwork, architectural casework, equipment and other built-in items. Identify PRC items by JSN and as noted in the VA BIM STANDARD. (Coordinate with Architecture) |  | P | F
VA SME
| Hector Abreu |  |  |  |  | Hector.Abreu@va.gov
| Angela McArdle |  |  |  |  | Angela.McArdle@va.gov

## Physical Security
[5 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[6 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | PHYSICAL SECURITY |  |  |  | VA submission requirements for Physical Security
PS-1.0 |  |  | BASIS OF DESIGN
PS-1.1 | Report |  |  | Narrative |  | Basis of Design (BOD) including the physical security requirements and a report including verification that a qualified Security Specialist and Structural Blast Specialist shall be retained by the DOR. The design shall address the physical security requirements as defined in VA Physical Security and Resiliency Design Manual. Create subsections corresponding to each of the chapters of the Physical Security standard, (i.e., Site Considerations, Building Entrances and Exits, Functional Areas, and Building Envelope, Structural System, Utilities and Building Services, Building Systems, and Security Systems). | P | F | R
PS-1.2 | Report |  |  | Designations of Facilities (Critical, Essential, Ancillary) |  | Obtain approval from Authority-having-Jurisdiction per PSRDM, in writing to any exception to the Physical Security and Resiliency Design Manual (PSRDM). | F | R | R
PS-1.3 | Report |  |  | Requirements |  | Address Telecommunications System and Areas’ security requirements that must conform to approved standards and specifications. | F | R | R
PS-1.4 | Report |  |  | Requirements |  | Identify Telecommunications Areas to be addressed to including PACS Police Service control and management of all Spectrum Management OI&T physical spaces. | P | F | R
PS-1.5 | Report |  |  | Requirements |  | Assess Concept assessments including applicable Crime Prevention through Environmental Design (CPTED) principles. | F | R | R
PS-1.6 | Report |  |  | Requirements |  | Describe physical security requirements and an overview of provisions to be implemented including setbacks, building envelope, structural system, monitoring, intrusion detection, and other systems that must be considered. Include special construction requirements such as lead, electromagnetic, and RF shielding, pneumatic tube systems, automated materials handling systems, security requirements for pharmacy, designated COOP facilities, and Security Operations Center. | P | U | F
PS-1.7 | Report |  |  |  |  | Include RFP information to identify and locate primary and backup utility sources for water, power, emergency power, fuel, communications, and sewer. | F | R | R
PS-1.8 | Report |  |  |  |  | Coordinate security requirements on room data sheets. | P | U | F
PS-1.9 | Report |  |  |  |  | Provide connection matrix for security devices. |  | P | F
PS-1.10 | Report |  |  |  |  | Provide catalog cut sheets for proposed security equipment: CCTV, monitors, access control systems, PACS, and screening equipment. |  | P | F
PS-2.0 |  |  | CALCULATIONS
PS-2.1 | Calculations |  |  | Dynamic Analyses |  | Provide blast-loading, environment and dynamic analyses, of typical glazing, exterior envelope elements, vulnerable interior, and exterior structure. | P | U | F
PS-3.0 |  |  | DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and below
PS-3.1 | Drawings |  |  | Site Plans |  | Provide Site Plan (1"=100.0') scale showing:
PS-3.2 | Drawings |  |  |  |  | Perimeter barrier (Coordinate with Civil Engineer). | P | F | R
PS-3.3 | Drawings |  |  |  |  | Perimeter barrier with pedestrian access points (Coordinate with Civil Engineer). | P | F | R
PS-3.4 | Drawings |  |  |  |  | Location of vehicle access points - private, public, commercial (Coordinate with Civil Engineer). | P | F | R
PS-3.5 | Drawings |  |  |  |  | Type of access control procedures and devices. | P | F | R
PS-3.6 | Drawings |  |  |  |  | Location of active and passive barriers (Coordinate with Civil Engineer). | P | F | R
PS-3.7 | Drawings |  |  |  |  | Vehicular circulation and parking (Coordinate with Civil Engineer). | P | F | R
PS-3.8 | Drawings |  |  |  |  | Site lighting (Coordinate with Electrical Engineer). | P | F | R
PS-3.9 | Drawings |  |  |  |  | Guard stations, vehicle barriers, inspection facilities, and vehicle stacking areas (Coordinate with Civil and Electrical Engineer). | P | F | R
PS-3.10 | Drawings |  |  |  |  | Camera locations (Coordinate with telecommunications and electrical disciplines). | P | F | R
PS-3.11 | Drawings |  |  | Security Camera Sightlines |  | Review security camera sight lines with location of landscape features and proposed mature vegetation (Coordinate with Landscape Architect). | P | U | F
PS-3.12 | Drawings |  |  |  |  | Crime Prevention Thru Environmental Design (CPTED) implementation plan. | U | U | F
PS-3.13 | Drawings |  |  | Floor Plans |  | Coordinate with architectural and engineering requirements for the following:
PS-3.14 | Drawings |  |  |  |  | Provide coordinated drawings of public entrances, lobbies, staff and service entrances, emergency management and security operations and control center. | P | F | R
PS-3.15 | Drawings |  |  |  |  | Agent cashier, cache, child care center, main computer room, COOP site, Emergency Department, emergency generator room, central energy plant, loading dock and service entrances, mail room, pharmacy, research laboratories, and vivarium. | P | F | R
PS-3.16 | Drawings |  |  | Physical Security Plan |  | Provide physical security plan showing location of security cameras, card readers, and screening equipment at a minimum scale 1/8"=1'-0" (1:100). | P | U | F
PS-3.17 | Drawings |  |  | 3D Panoramic Visualization |  | Using the Model, provide 3D visualization of interior security camera views. |  | P | F
VA SME
| Fred Lau |  |  |  | fred.lau@va.gov

## Elevator-Transport
[5 empty] | PG 18-15 VOL DB DESIGN BUILD | PROJECT NAME / PROJECT NUMBER | [7 empty] | MM/DD/YYYY | DATE | DATE | DATE
[6 empty] | CONTRACT EFFECTIVE DATE | Typical Phases |  |  | Submittal Checklist |  |  |  |  | Submittal Package - 1
Seq. No. | Type | Topic |  |  |  | Description | SD/35% | DD/65% | CD/100% | Inc. in RFP | Submitted | Pending | N/A | Comments / Location | SD/35% | DD/65% | CD/100%
|  | ELEVATOR AND LOGISTICS |  |  |  | VA submission requirements for Elevator and Logistics
|  |  | REFERENCE |  |  | The individual disciplines will use initials for identity: Vertical Transport - VT, Materials Management - MM, Waste Management - WM, Sterile Processing Services - SPS, Materials Handling - MH. Material Handling can include all or some of the following systems: Pneumatic Tube System - PTS, Automated Guided Vehicle System - AGVS, Gravity Trash and Linen Chutes - GTL, Pneumatic Trash and Linen system - PTL, and Autonomous Mobile Robot - AMR. When referencing the combination of these services as a coordinated and integrated support service it shall be referred to as: Logistics.
EL-1.0 |  |  | BASIS OF DESIGN |  |  | As a minimum, refer to and comply with all requirements noted in PG-18-3T18, PG18-10 and all Other VA Design standards including PG18-12 Chapters 284: Logistics Services and 285: Sterile Processing Service and Nutrition and Food Services (PG18-9 Chapter 224) and Environmental Management Service Laundry And Linen Operation (PG18-9 Chapter 408).
EL-1.1 | Report |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling - Logistics Report(s). |  |  | Provide studies, analysis (showing calculations) and reports on the Support Service requirements for all facilities to be serviced whether they are part of the Project in question or on the campus or not. Determine the adequacy or inadequacy of planned and existing support elements to support all of the functions and departments they are to serve. Determine the ROM space / costs for adding, expanding, enhancing, reducing or otherwise changing the combination of new and existing conditions to ensure proper MM / WM / VT / MH / SPS / Logistics support is available to the total of the combined facilities served whether on or off the local campus. | P | U | F
EL-1.2 | Report |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling - Logistics. Data Report. |  |  | Provide Data Report that will be used as the basis for the Transport / Logistics studies and recommendations. | P | U | F
EL-1.3 | Report |  | Transport / Logistics Studies and Report: Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Provide project type / size appropriate studies, analysis and reports (TLA / ETSA / MMA / WMA / MH) as noted and directed in PG18-3 Topic 18 and standards referenced therein. This includes all traffic studies, Life Cycle Cost Analysis, etc. Reports to be fully updated for each design phase to ensure it remains current with the designs, traffic, operational and physical aspects of the project throughout the design process. Designs and project narratives shall conversely be updated to reflect the contents and recommendations in the updated reports. Final Submittals to be used for the Basis of Design during the CA Phase. | P | U | F
EL-1.4 | Report |  | Study and Report - Waiver: Space for Materials Handling Systems (i.e., AGVS, AMR, PTS, etc.) |  |  | Where a MM, WM, VT, SPS, MH or Logistics system is justified and recommended in a TLA / ETSA / MMA / WMA report, the departments, functions, rooms, adjacencies etc. required for that system but are not addressed or properly represented in the VA PG-9's Space Planning Criteria; shall be immediately identified, quantified and reported. Examples of this are: specialized maintenance areas; space reductions from higher efficiencies; etc. A written waiver request for the deviation / change shall be submitted immediately with a copy of all waiver requests attached within an appendix to the design phase (updated) report such as a TLA or MMA. The VA's response to the waiver request shall be added to the appendix to the report to memorialize the response. | P | U | F
EL-1.5 | Report |  | Study and Report - Coordination: Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | The Transport / Logistics Consultant shall become familiar with the submittal requirements noted in PG18-15 for all disciplines and provide the data needed for other disciplines in a timely manner to advance the project with minimum delays and redesigns. This includes attention to "special" systems such as PTS, AGVS, Trash/Linen Chutes, etc. where they are not "standard" equipment and their design requirements may not be familiar to Other disciplines. Pay special attention to conflict resolution for PTS and AGVS and interfaces to fire / smoke alarm systems. | P | U | F
EL-1.6 | Report |  | Study and Report - Nutrition and Food Service Coordination: Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling - Logistics coordination with Nutrition and Food Service. |  |  | Where the Transport / Logistics Consultant (TLC) is not providing the Studies and Designs for Nutrition and Food Services (NFS), Patient and Non-Patient, it shall be generally understood that the activities within the NFS departments shall be studied / designed / specified by the specialized NFS designer. The MM / WM / VT / MH functions supporting NFS but outside of the department perimeters, including clean and soiled truck docks and transport, shall be the responsibility of the TLC using the criteria, data, product volume and Other relevant information supplied by the NFS designer. Where automation such as AGVS, AMR, VT and Pneumatic Systems is used, design is to be implemented into the NFS operations by the TLC with the close cooperation of the Other applicable designers including the NFS designer. | P | U | F
EL-1.7 | Report |  | Special - Technology Reports and Documents: Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | It is recognized that the Transport and Logistics industries, along with Others, are undergoing rapid, major and significant technological changes that may be unknown to non-experts in these fields. The consultant shall issue special reports / white papers in a timely manner where new and technologically advanced equipment / systems are being planned and specified that has impacts on the planning of Other designer disciplines. | P | U | F
EL-1.8 | Report |  | Seismic Retrofit Projects (Seismic EQ funded) |  |  | Analyze impact of seismic correction plan on automatic transport system. Determine minimal acceptable changes necessary to implement seismic corrections. | P | U | F
EL-2.0 |  |  | CALCULATIONS |  |  | Per PG18-10 and PG18-3 Topic 18
EL-2.1 | Calculations |  |  |  |  | Submit calculations as required in PG18-10 and PG18-3t18.for all studies. Calculations are to show the input information and relevant outcomes. | P | U | F
EL-3.0 |  |  | DRAWINGS and MODELS |  |  | As per the VA BIM STANDARD and PG18-10 AND PG18-3t18
EL-3.1 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Submit overall floor plans at a minimum of 1/16”=1’-0” (1:200) indicating location of proposed and existing MM / WM / VT / MH / SPS / Logistics devices and systems. Indicate proposed routes and non-scaled "riser diagram" sketches for automatic transport systems. | P | U | F
EL-3.2 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Floor plans at a minimum of 1/8”=1’-0” (1:100) drawings of the MM / WM / VT / MH / SPS / Logistics systems and devices. Indicate devices including but not limited to: processing and storage equipment, MH devices, door interfaces, tracking, piping, battery charging areas, blower rooms, queuing areas, cart holding areas, cart washer, central control area, maintenance areas and floor and/or wall and/or overhead mounted or recessed control units. Indicate architectural and utility elements to be used for these systems. | P | U | F
EL-3.3 | Drawings |  | Pneumatic Tube, Trash, and Linen Chute Systems: |  |  | Show station locations recommended in the PG18-3t18 studies and accepted. Develop and coordinate the horizontal / vertical (including shaft ways) routing for pneumatic systems so that there are early and continuous efforts to avoid conflicts with the building, structures, departments and utilities without compromising the related system operations. Provide weights and reactions where necessary. | P | U | F
EL-3.4 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Provide separate drawings for major MM / WM / VT / MH / SPS / Logistics systems and equipment. As a minimum provide: dimensioned H x D x W equipment drawings, show installation space requirements including necessary maintenance clearances, details of required utilities and ventilation, provide details of corridors for automated / manual transport systems showing pathways and clearances, show VT equipment locations and details, show dimensions and details for carts to be used by automated and semi-automated systems, MM / SPS storage equipment, dock equipment, PTS stations and equipment, tube routings, processing equipment, shaftways, battery chargers, hoistway enclosures, pits, cabs, machine and blower room access and railings, and entrances using larger scale than floor plans as necessary. Show dimensional locations of equipment and devices. | P | U | F
EL-3.5 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. - Fire Protection |  |  | Coordinate proactively with the Fire Protection Engineer, information on the various fire protection features and devices required for the various systems including interface to the fire / smoke system. Develop and provide fire door interfaces to relevant systems such as AGVS / AMR. Develop strategies and methodologies for all automated and semi-automated systems for compliance to all Fire Protection codes and standards. For example: Clearing obstructions from AGVS / AMR system transporter / carts from egress routes, doors and corridors; system activities where operations occur in multiple zones; etc. | P | U | F
EL-3.6 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Locate machine and equipment rooms for MM / WM / VT / MH / SPS / Logistics systems including: elevators, cart lifts, dumbwaiters, Pneumatic Chute Systems, PTS and AGV systems, mechanical / utility spaces. Indicate minimum dimensions, ventilation, structural and power requirements. | P | U | F
EL-3.7 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Provide details of elevator and other transport equipment at scales large enough to describe construction and installation requirements. Indicate size and locations of trap doors, hoist beams, divider beams, PTS blowers / diverters / exchangers, AGVS / AMR battery chargers, Pneumatic Chute diverters / turbines and similar equipment for people and materials transport systems. | P | U | F
EL-3.8 | Drawings |  | Vertical Transport, Materials Management, Waste Management, Sterile Processing, Materials Handling, Logistics. |  |  | Coordinate with Structural Engineer and provide size of machine beams and end reactions. Indicate location and detail of machine beam pockets. Show rail loadings and hydraulic elevator piston pit loads. | P | U | F
|  | AUTOMATIC GUIDED VEHICLES |  |  |  | VA submission requirements for Automatic Guided Vehicles (AGV)
AG 1.0 |  |  | NOTE 1: |  |  | For projects involving Automatic Guided Vehicles, please refer to VA Topic 18-1 AGV and AMR Submittal Schedule. | P | U | F
|  | PNUMATIC TUBES |  |  |  | VA submission requirements for Pneumatic Tube System
PT 1.0 |  |  | NOTE 1: |  |  | For projects involving Pneumatic Tube Systems, please refer to VA Topic 18-1 AGV and AMR Submittal Schedule. | P | U | F
VA SME
Brian Phillips |  |  |  | Brian.Phillips@va.gov