SECTION 28 13 53

Security Access Detection

SPECS WRITER NOTE: Delete // ________ // if not applicable to project. Also delete any other item or paragraph not applicable in the section and renumber the paragraphs. Insert additional provisions as required for this project.

PART 1 – GENERAL

1.1 DESCRIPTION

A.	Provide and install a complete Detection and Screening System, hereinafter referred to as the Security Access Detection as specified in this section.

1.2 rELATED WORK

SPECS WRITER NOTE: Delete any item or paragraph not applicable in the section and renumber the paragraphs.

A.	Section 01 00 00 - GENERAL REQUIREMENTS. For General Requirements.

B.	Section 07 84 00 - FIRESTOPPING. Requirements for firestopping application and use.

C.	Section 10 14 00 - SIGNAGE. Requirements for labeling and signs.

D.	Section 28 05 00 - COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND SECURITY. For general requirements that are common to more than one section in Division 28.

E.	Section 28 05 13 - CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND SECURITY. Requirements for conductors and cables.

F.	Section 28 05 26 - GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND SECURITY. Requirements for grounding of equipment.

G.	Section 28 05 28.33 - CONDUITS AND BOXES FOR ELECTRONIC SAFETY AND SECURITY. Requirements for infrastructure.

H.	Section 28 08 00 - COMMISIONING OF ELECTRONIC SAFETY AND SECURITY SYSTEMS. For commissioning requirements, systems readiness checklists, and training.

I.	Section 28 13 00 - PHYSICAL ACCESS CONTROL SYSTEMS (PACS). Requirements for physical access control integration.

J.	Section 28 13 16 - ACCESS CONTROL SYSTEM AND DATABASE MANAGEMENT. Requirements for control and operation of all security systems.

K.	Section 28 16 00 - INTRUSION DETECTION SYSTEM. Requirements for alarm systems.

L.	Section 28 23 00 - VIDEO SURVEILLANCE. Requirements for security camera systems.

M.	Section 28 26 00 - ELECTRONIC PERSONAL PROTECTION SYSTEM (EPPS). Requirements for emergency and interior communications.

1.3 QUALITY ASSURANCE

//A.	Refer to 28 05 00 COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND SECURITY, Part 1//

A.	The Contractor shall be responsible for providing, installing, and the operation of the Security Access Detection as shown. The Contractor shall also provide certification as required.

B.	The security system shall be installed and tested to ensure all components are fully compatible as a system and can be integrated with all associated security subsystems, whether the security system is stand-alone or a part of a complete Information Technology (IT) computer network.

C.	The Contractor or security sub-contractor shall be a licensed security Contractor as required within the state or jurisdiction of where the installation work is being conducted.

D.	Manufacturers Qualifications: The manufacturer shall regularly and presently produce, as one of the manufacturer's principal products, the equipment and material specified for this project, and shall have manufactured the item for at least three years.

E.	Product Qualification:

1.	Manufacturer's product shall have been in satisfactory operation, on three installations of similar size and type as this project, for approximately three years.

2.	The Government reserves the right to require the Contractor to submit a list of installations where the products have been in operation before approval.

F.	Contractor Qualification:

1.	The Contractor or security sub-contractor shall be a licensed security Contractor with a minimum of five (5) years experience installing and servicing systems of similar scope and complexity.  The Contractor shall be an authorized regional representative of the Security Management System’s (PACS) manufacturer.  The Contractor shall provide four (4) current references from clients with systems of similar scope and complexity which became operational in the past three (3) years.  At least three (3) of the references shall be utilizing the same system components, in a similar configuration as the proposed system.  The references must include a current point of contact, company or agency name, address, telephone number, complete system description, date of completion, and approximate cost of the project.  The owner reserves the option to visit the reference sites, with the site owner’s permission and representative, to verify the quality of installation and the references’ level of satisfaction with the system.  The Contractor shall provide copies of system manufacturer certification for all technicians.  The Contractor shall only utilize factory-trained technicians to install, program, and service the PACS.  The Contractor shall only utilize factory-trained technicians to install, terminate and service controller/field panels and reader modules.  The technicians shall have a minimum of five (5) continuous years of technical experience in electronic security systems.  The Contractor shall have a local service facility.  The facility shall be located within 60 miles of the project site.  The local facility shall include sufficient spare parts inventory to support the service requirements associated with this contract.  The facility shall also include appropriate diagnostic equipment to perform diagnostic procedures.  The COTR reserves the option of surveying the company’s facility to verify the service inventory and presence of a local service organization.

2.	The Contractor shall provide proof project superintendent with BICSI Certified Commercial Installer Level 1, Level 2, or Technician to provide oversight of the project.

3.	Cable installer must have on staff a Registered Communication Distribution Designer (RCDD) certified by Building Industry Consulting Service International.  The staff member shall provide consistent oversight of the project cabling throughout design, layout, installation, termination and testing.

SPEC WRITER NOTE: In the following paragraph use 4 hours for metropolitan areas and 8 hours for rural areas.

G.	Service Qualifications: There shall be a permanent service organization maintained or trained by the manufacturer which will render satisfactory service to this installation within // four // eight // hours of receipt of notification that service is needed. Submit name and address of service organizations.

1.4 SUBMITTALS

SPECS WRITER NOTE: Delete and/or amend all paragraphs and sub-paragraphs and information as needed to ensure that only the documentation required is requested per the Request for Proposal (RFP).

A.	Submit below items in conjunction with Master Specification Sections 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES, Section 02 41 00, DEMOLITION, and Section 28 05 00, COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND SECURITY.

B.	Provide certificates of compliance with Section 1.3, Quality Assurance.

C.	Provide a complete and thorough pre-installation and as-built design package in both electronic format and on paper, minimum size 48 x 48 inches (in.) (1220 x 1220 millimeters) (mm); drawing submittals shall be per the established project schedule.

D.	Pre-installation design and as-built packages shall include, but not be limited to:

1.	Index Sheet that shall:

a.	Clearly define each page of the design package to include facility name, building name, floor, and sheet number.

b.	Provide a complete list of all security abbreviations and symbols.

c.	Reference all general notes that are utilized within the design package.

d.	Specification and scope of work pages for all individual security systems that are applicable to the design package that will:

1)	Outline all general and job specific work required within the design package.

2)	Provide a detailed device identification table outlining device Identification (ID) and use for all security systems equipment utilized in the design package.

2.	Drawing sheets that will be plotted on the individual floor plans or site plans shall:

a.	Include a title block as defined above.

b.	Clearly define the drawings scale in both standard and metric measurements.

c.	Provide device identification and location.

d.	Address all signal and power conduit runs and sizes that are associated with the design of the electronic security system and other security elements.

e.	Identify all pull box and conduit locations, sizes, and fill capacities.

f.	Address all general and drawing specific notes for a particular drawing sheet.

3.	A detailed riser drawing for each applicable security subsystem shall:

a.	Indicate the sequence of operation.

b.	Relationship of integrated components on one (1) diagram.

c.	Include the number, size, identification, and maximum lengths of interconnecting wires.

d.	Wire/cable types shall be defined by a wire and cable schedule. The schedule shall utilize a lettering system that will correspond to the wire/cable it represents (example: A = 18 AWG/1 Pair Twisted, Unshielded). This schedule shall also provide the manufacturer’s name and part number for the wire/cable being installed.

4.	A detailed system drawing for each applicable security system shall:

a.	Clearly identify how all equipment within the system, from main panel to device, shall be laid out and connected.

b.	Provide full detail of all system components wiring from point-to-point.

c.	Identify wire types utilized for connection, interconnection with associate security subsystems.

d.	Show device locations that correspond to the floor plans.

e.	All general and drawing specific notes shall be included with the system drawings.

5.	A detailed schedule for all of the applicable security subsystems shall be included. All schedules shall provide the following information:

a.	Device ID.

b.	Device Location (e.g. site, building, floor, room number, location, and description).

c.	Mounting type (e.g. flush, wall, surface, etc.).

d.	Power supply or circuit breaker and power panel number.

e.	In addition, provide the Security Access Detection detector or screening device ID, type (e.g. walk-through screener, X-ray, explosive detector, etc.), type of technology used by system for detection and model number.

6.	Provide detail and elevation drawings for all devices that define how they were installed and mounted.

E.	The pre-installation design packages shall go through a full review process conducted by the Contractor along with a VA representative to ensure all work has been clearly defined and completed. All reviews shall be conducted in accordance with the project schedule. There shall be four (4) stages to the review process:

1.	35 percent

2.	65 percent

3.	90 percent

4.	100 percent

F.	The Contractor shall provide manufacturer security system product cut-sheets that clearly and completely indicate the description and function of each component of the security systems they are associated with. Also, indicate all termination points of devices and interconnections required for operation of the system, and between modules and devices.

G.	The Contractor shall submit for approval at least 30 days prior to commencement of formal testing, a Security System Operational Test Plan. Include detailed procedures for operational testing of each component and security subsystem, to include performance of an integrated system test.

H.	The Contractor shall submit manufacture’s certification of Underwriters Laboratories, Inc. (UL) listing for all security system devices, power sources, control panels, and monitoring equipment.

I.	The Contractor shall provide complete maintenance and operating manuals from the manufacturer that support as-builts and system design, to include all technical product sheets and overall system schematics. Two (2) weeks prior to the final inspection, four (4) copies of the maintenance and operating manuals also need to be submitted to the RE.

J.	Certifications: Two (2) weeks prior to final inspection, submit four (4) copies of the following to the RE:

1.	Complete maintenance and operating manuals from the manufacturer that support as-built and systems design, to include all technical data sheets and overall system schematics.

2.	Certification by the Contractor that the materials submitted is in accordance with the drawings and specifications.

3.	Certification by the Contractor that a complete security system installation has been installed, tested and adjusted.

K.	Completed System Readiness Checklists provided by the Commissioning Agent and completed by the contractor, signed by a qualified technician and dated on the date of completion, in accordance with the requirements of Section 28 08 00 COMMISSIONING OF ELECTRONIC SAFETY AND SECURITY SYSTEMS.

1.5 applicable publications

A.	The publications listed below (including amendments, addenda, revisions, supplement, and errata) form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

B.	American Society for Testing and Materials (ASTM)

C1238-97 (R03)	Standard Guide for Installation of Walk-Through Metal Detectors

C.	Department of Justice American Disability Act (ADA)

28 CFR Part 36-94	ADA Standards for Accessible Design

D.	Department of Veterans Affairs

VHA National CAD Standard Application Guide, 2006

VA BIM Guide, V1.0 10

E.	Federal Communications Commision (FCC):

(47 CFR 15) Part 15	Limitations on the Use of Wireless Equipment/Systems

F.	Government Accountability Office (GAO):

GAO-03-8-02	Security Responsibilities for Federally Owned and Leased Facilities

G.	Institute of Electrical and Electronics Engineers (IEEE):

C95.1-05	Standards for Safety Levels with Respect to Human Exposure in Radio Frequency Electromagnetic Fields

H.	National Fire Protection Association (NFPA):

70-11	 Article 780-National Electrical Code

I.	National Institute of Justice (NIJ)

0601.02-03	Standards for Walk-Through Metal Detectors for use in Weapons Detection

0602.02-03	Hand-Held Metal Detectors for Use in Concealed Weapon and Contraband Detection

J.	National Electrical Manufactures Association (NEMA)

250-08	Enclosures for Electrical Equipment (1000 Volts Maximum)

K.	Occupational and Safety Health Administration (OSHA):

29 CFR 1910.97	Nonionizing radiation

L.	Security Industry Association (SIA):

AG-01	Security CAD Symbols Standards

M.	Underwriters Laboratories, Inc. (UL):

187-98	Standard for X-ray Equipment

464-03	Audible Signal Appliances

N.	United States Department of Commerce:

Special Pub 500-101 	Care and Handling of Computer Magnetic Storage Media

O.	Uniform Federal Accessibility Standards (UFAS), 1984

P.	Architectural Barriers Act (ABA), 1968

1.6 cooridnation

A.	Coordinate arrangement, mounting, and support of security access detection equipment:

1.	To allow maximum possible headroom unless specific mounting heights that reduce headroom are indicated.

2.	To provide for ease of disconnecting the equipment with minimum interference to other installations.

3.	To allow right of way for piping and conduit installed at required slope.

4.	So connecting raceways, cables, wireways, cable trays, and busways will be clear of obstructions and of the working and access space of other equipment.

B.	Coordinate installation of required supporting devices and set sleeves in cast-in-place concrete, masonry walls, and other structural components as they are constructed.

C.	Coordinate location of access panels and doors for electronic safety and security items that are behind finished surfaces or otherwise concealed.

1.7 warranty of construction.

A.	Warrant Security Access Detection work subject to the Article “Warranty of Construction” of FAR clause 52.246-21.

B.	Demonstration and training shall be performed prior to system acceptance.

PART 2 – PRODUCTS

SPEC WRITER NOTE: Delete or amend all paragraphs and sub-paragraphs as needed to ensure that only the equipment required per the Request for Proposal (RFP) is provided.\

2.1 GENERAL

A.	All equipment shall operate on a 120 or 240 volts alternating current (VAC); 50 hertz (Hz) or 60 Hz alternating current (AC) power system unless documented otherwise in subsequent sections listed within this spec. All equipment shall have a battery back-up source of power that will provide 12 hours (hrs.) of run time in the event of a loss of primary power to Security Access Detection systems until a backup generator comes on-line.

B.	Walk-through metal detectors and X-ray machines shall meet the National Institute of Justice (NIJ) Standards and Safety requirements.

C.	The Security Access Detection shall be designed, installed, and programmed in a manner that will allow for easy of operation, programming, servicing, maintenance, testing, and upgrading of the system.

D.	All Security Access Detection components located in designated “HAZARDOUS ENVIRONMENT” areas where fire or explosion could occur due to the presence of natural gases or vapors, flammable liquids, combustible residue, or ignitable fibers or debris, shall be rated Class II, Division I, Group F, and installed in accordance with NFPA 70, Chapter 5.

E.	All Security Access Detection equipment and materials provided shall be new, first grade, standard, current products of the manufacturer and shall be suitable for the systems being installed and the intent of the design.

F.	All Security Access Detection equipment and materials shall be stored, adequately protected and carefully handled to prevent damage before and during installation and according to manufacture’s instructions.

G.	All Security Access Detection equipment provided with a factory finish shall be maintained free of dust, dirt and foreign matter. Dents, marred finishes and other damage shall be repaired to its original condition or shall be replaced, at no additional cost to the Owner.

H.	The Contractor shall provide the RE with written verification, that the type of wire/cable being provided is recommended and approved by the OEM. Cabling shall meet the interconnecting wiring requirements of NFPA 70 (NEC). The Contractor is responsible for providing the correct protection cable duct and/or conduit and wiring.

I.	The Contractor is responsible for interfacing Security Access Detection with other security subsystems. The Contractor shall utilize interfacing methods that are approved by the OEM and RE. At a minimum, an acceptable interfacing method requires not only a physical and mechanical connection; but also a matching of signal, voltage, and processing levels with regard to signal quality and impedance. The interface point must adhere to all standards described herein.

J.	The characteristics listed in this section will serve as a guide in selection of equipment and materials for the Security Access Detection. If updated or more suitable versions are available then the RE will approve the acceptance of prior to an installation.

K.	If any obsolete, incompatible, or damaged equipment is offered by the Contractor at the time of installation, then the equipment will be returned and replaced with equipment at no cost to the government.

2.2 Equipment Items

A.	General

1.	All specifications listed within this section are the minimum requirements to be met to ensure a working Security Access Detection is in place.

2.	Detection Sensor subsystems shall consist of sensors capable of:

a.	Locating and identifying prohibited, threatening, contraband materials and items the system is designed to detect and protect against being brought into a facility.

b.	Sensors shall be adjustable to maximize capabilities based on environmental and security requirement changes.

3.	Annunciation: Shall contain one (1) or more indicator lamps, alphanumeric displays that provide status information about a circuit or condition of the operating units. Walk-Through or conveyer pass through units must provide a uniform two-digit error code to identify different types of system failures.

4.	Audible Signal Device: Shall consist of audible sound for alarms, supervisory, and trouble signals and shall be distinctive.

5.	Assessment: Shall consist of electronic devices required to visually and audibly verify the validity and functionality of Security Access Detection. Assessment also includes providing indication of tampering, fail-safe, low battery, and power losses.

6.	Alarm Reporting: Shall consist of electronic devices to annunciate Security Access Detection information to at least two (2) separate locations. The alarms shall maintain the capability to respond with local and remote visible and audible signals upon activation of detection sensors. The alarms should have the capability of a silent mode only alerting personnel using the system.

7.	Power Supply: Security Access Detection shall be capable of continuous operation and include a battery backup module capable of 12 hrs. of backup use. All non-portable systems shall operate on 100-240 VAC. Hand-Held Security Access Detection (Metal and Explosive Detectors) shall have the capability to operate on rechargeable batteries.

2.3.	Walk-Through Metal Detectors:

A.	Shall meet NIJ Standard 0601.02 and be able to detect and locate guns, knives, and other flat and rod-shaped objects regardless of orientation.

B.	All electronics shall be modular in design for easy plug-in and replacement. The Detector shall use multiple coil circuits with dual alarm lights to indicate which side of the individual the detected item is located.

C.	Shall be capable of self-diagnostics and conduct self-test of all systems to automatically identify failures or problems with components as displayed on the control unit liquid crystal display (LCD). The detection unit shall not require re-calibration each time the system is turned off and back on.

D.	Shall provide for full body coverage: coverage on the left, center, right, front, and back of the body from head to floor, providing uniform detection.

E.	Shall include individual zones that are adjustable for customization of detection characteristics and/or compensation for metallic environmental challenges.

F.	Shall have the capability to detect and discriminate signals from two (2) or more detectable items located in close proximity that may be detected as only one (1).

G.	Shall include adjustable legs to provide for accurate leveling on uneven floors.

H.	Major components include:

1.	Walk-through portal/passage way

2.	Control Unit

3.	Test Unit

I.	Technical Characteristics:

| Operating Temperatures | -4°F (-20°C) to 158°F (70°C) 95% humidity non-condensing |
| --- | --- |
| Power Supply Unit | Fully automatic input 100 to 240 VAC 50 or 60 Hz – five (5) watts Uninterrupted Power supply (UPS) Battery Backup (12 hours) |
| Construction | Minimum 3/32 in. (2.381mm) aluminum in strength and weather resistant |
| Opening Sizes | Interior Width: 30 in. (762mm) Interior Height: 80 in.(2.032 meters) |
| Programmable | Capable of 16 independent programs settings for zones and sensitivity |
| Sensitivity Boost | Three (3) levels at ankle level |
| Detection Sensors | Multi-dimensional coil 33 distinct pin-point zones – customizable |
| Sensitivity Levels | 200 |
| Interference Protection | Faraday shielding |
| Alarms | Audible and light-emitting diode (LED) Visual |
| Testing Device | Simulate size, shape, and composition of threat objects meet FAA testing requirements |
| Traffic Flow Indicators | LED Lights |
| Infrared Sensor | Traffic control and counter |

J.	Control Unit: Shall consist of the components to constantly monitor, input settings, and verify inputs of sensors.

1.	The control unit is to be attached to the exit side of the scanner or shall be able to be detached and operational from up to 50 feet (ft.) (15.24 meters)(m) from detector.

2.	The control unit will consist of a multiple functional electronic digital keypad/touchpad. The keypad/touchpad requires human/machine interface (HMI) with numerical or function keys that can activate, deactivate, observe or change sensitivity and detector settings using secure codes.

3.	The Control Unit shall be programmed to be self-prompting for input.

4.	The LCD display shall be large, easily seen, backlit with alpha-numeric display that reports in words to regulate, control and provide self-prompt functions of the control unit.

5.	Control Unit Technical Characteristics:

| Display | LCD |
| --- | --- |
| Connection to Unit | Wired with extension of 50 ft. (15.24m) for remote use |
| Touchpad Controls | Operate, Off, Counter, Volume, +/-, Program and Access |
| Displays | LED bar-graphs for detection sensitivity Alarm lights Functionality Program in operation Errors Traffic Count Alarm activations Alarm Percentages |
| Tamper alarm | 10 seconds after access of touchpad |
| Access Control | Dual-level access codes for: Operators Supervisors |

K.	Control Unit Interface:

1.	The system shall include an interface module for network transmission of data and remote monitoring of system at the Physical Access Control System and Database Management.

2.	Integration with the Physical Access Control System and Database Management shall allow for control, real time monitoring and diagnostics capabilities.

3.	Control Unit Interface Technical Characteristics:

| Display | LCD (laptop or Desktop Monitor) |
| --- | --- |
| Connection | 10-Base T Network |
| System Capabilities | Monitor up to 4 scanners |
| Capabilities | Change settings LED bar-graph display Functionality Program in operation Errors Traffic Count Alarm activations Alarm Percentages Technician trouble-shoot |
| Access Control | Dual-level access codes Operators Supervisory |

2.4.	Hand-Held Metal Detectors:

A.	Shall meet NIJ Standard 0602.02 and be rugged in design and water-proof; lightweight to reduce stress of handling; and provide ease of freedom of movement and control.

B.	Shall be easily made operational with a one (1) switch operation that does not require any adjustments.

C.	Technical Characteristics:

| Operating Temperatures | -35°F (-37°C) to 158°F (70°C) 95% humidity non-condensing |
| --- | --- |
| Operating Frequency | 93 kHz |
| Audio Frequency | 2kHz Warble Earphone capable |
| Tuning | Automatic |
| Controls | Power switch On/Off Interference Elimination |
| LED Alert Lights | Power On, Battery Low, Alarm |
| Indicators | Silent/Vibrate Audible Speaker LED Alert Lights |
| Power | Standard 9 volt and Nickel-Metal Hydride(NiMH)rechargeable battery |
| Battery life | 60 hours continuous operations |
| Minimum Detection Capability Distances | Medium Pistol – 9 in. (228.6mm) Large Knife- 5 in. (127mm) Razor Blade- 3 in. (76.2mm) Small foil and jewelry – 1 in. |

2.5 X-ray Detectors:

A.	Shall be surface mounted, multilayer, fully integrated, high frequency, and solid state using high speed processors.

B.	Shall meet NIJ Standards including a Personal Computer (PC) based system that can be networked with other inspection systems and can transmit data.

C.	The type of X-ray unit selected shall require consideration of its application and use (i.e., used to screen items through lobby control points versus screening items, which may be larger in size, such as through mail room/shipping and receiving facility areas).

D.	The system should provide the capability to send images through a network to a central server PC where the images can be viewed, stored or printed.

E.	The conveyer belt system belts should be guaranteed to perform auto tracking for life.

F.	All x-ray systems shall be certified to be in full compliance with all international radiation safety requirements and external emissions limits.

G.	Technical Characteristics:

| X-Ray Generator | Self Contained operating at 90 kilovolts |
| --- | --- |
| Controls | Edge sharpening, variable intensity control, zoom, atomic number measurement |
| Zoom Capability | 2X to 32X penetration levels |
| Discrimination | Organic, inorganic, mixed |
| Penetration | 0.39 in. (10 mm) steel |
| Resolution capability | Detect #40 AWG |
| Color Tones | Two (2) million (Multi-Energy Colors) |
| Conveyer belt weight capabilities | 200 lbs. (90 kilograms) |
| Conveyer belt speed | Controllable – 48 fpm (24 cm/sec)- reversible |
| Network Capable | Ethernet using TCP/IP |

H.	Central Processing Unit Technical Characteristics:

| Processor | 2.4 GHz Intel Pentium IV |
| --- | --- |
| Hard Disk Size | 40 GB |
| Memory | 256 RAM |
| Network Card | 10/100 Base-T |
| CD-ROM Drive | 10X |
| Monitor/Video Adapter board | 19” (482.6mm)SVGA (1280 x 1044)Flicker Free Flat Screen .28 dot pitch |
| Floppy Drive | 1.44 MB |
| Ports | 2 serial, 1 parallel, USB |
| Backup | Tape or CDRW |

2.6 EXPLOSIVES DETECTORS:

A.	Handheld: Provide for a self-contained analytical unit, with on-board computer, printer and touch screen display. The detector shall be easy to operate by non-technical staff/operators:

1.	System will use dual vapor and particulate detection without any external carrier gas or radioactive source.

2.	Detector shall be a simple push-button automatic operation that displays go/no go results on a LCD display.

3.	Explosive Detectors Technical Characteristics:

| Power | 12 volt direct current (DC) rechargeable 12 volt External battery pack 12 volt AC adapter |
| --- | --- |
| Device Controls | Power switch, keypad, automatic vapor/particulate selector, volume control (with optional earphone, and sample switch. |
| Memory | Store a minimum of 1000 previous readings |
| Detection | Dual vapor and particulate |
| Detection Analysis | <20 seconds |
| Detection Capabilities | Nanogram levels of: C-4, TNT, Dynamite, PETN, Semtex, EGDN, DMNB, RDX, ANFO, Black Powder, Ammonium Nitrate, Urea Nitrate, Nitroglycerine and TATP |

B.	Desktop:

1.	Shall have a built-in networking and communication capability. The device shall easily interface with other screening systems and printer if it is not part of the unit.

2.	Shall be self-contained, self-cleaning, self-calibrating, and require no external gas supply.

3.	A touch screen display shall be provided that displays both alarm and compound identification information Red flashing light on unit and audible alarm Automatic “Print on Alarm” option.

4.	Contractor shall provide collection device for input of data.

5.	Technical Characteristics:

| Power | 90 to 265 volts alternating current (VAC) 50-60 Hz |
| --- | --- |
| Technology | Dual- gas chromatography and Ion mobility spectrometer |
| Power Consumption | Less than 500 watts |
| Device Controls | Touch screen display Power switch |
| Operating Modes | Continuous and Single Cycle |
| Warm up time | < 20 minutes (cold start) |
| Memory | Store a minimum of 1000 previous readings |
| Detection | Dual vapor and particulate |
| Analysis Time | < 20 seconds |
| Detection Capabilities | Nanogram levels of: 1) Explosives: PETN, RDX,TNT, NG, Dynamite, Semtex, C4 2) Narcotics: Cocaine, Opiates (heroine & morphine), Cannabis marijuana & hashish), Amphetamine-type stimulants amphetamine, ecstasy & methamphetamine. |

PART 3 - EXECUTION

3.1 GENERAL

Spec Note: Delete and/or amend this all paragraphs and sub-paragraphs to apply to only the equipment and devices that are being installed.

A.	System installation shall be in accordance with appropriate NEC, UL, NFPA, Related Work VA specifications, and appropriate installation manual for each type of Security Access Detection.

B.	The Security Access Detection system will be designed, engineered, installed, and tested to ensure all components are fully compatible as a system and can be integrated with all associated security subsystems, whether the system is a stand alone or a complete network.

C.	Components shall be configured with appropriate “service points” to pinpoint system trouble in less than 30 minutes.

D.	All Security Access Detection requiring VAC connection will be installed with surge protection and Uninterrupted Power Supply (UPS).

E.	Architectural space planning design requirements need to be considered and defined prior to the installation of metal detection, x-ray and explosive detection equipment at main lobby entrance or other security control points. This also applies to the use of x-ray and explosive detectors in mail and shipping/receiving facility areas.

F.	The Contractor shall install all system components including Government furnished equipment, and appurtenances in accordance with the manufacturer's instructions, documentation listed in Sections 1.4 and 1.5 of this document, and shall furnish all necessary connectors, terminators, interconnections, services, and adjustments required for a complete and operable system.

G.	Walk-through metal detectors will not be located on floors with high metal content that may interfere with screening without protection between the floor and detector being considered.

H.	The Contractor shall provide walk-through metal detectors with the capability for floor mounting (OEM recommended brackets) to increase stability.

3.2 WIRING

A.	Wiring Method:  Install cables in raceways[ except in accessible indoor ceiling spaces, in attics,] [in hollow gypsum-board partitions,] and as otherwise indicated.  Conceal raceways and wiring except in unfinished spaces.

SPECS WRITER NOTE: Retain paragraph above or first paragraph below.  Delete both if wiring method is indicated on Drawings.

B.	Wiring Method:  Install cables concealed in accessible ceilings, walls, and floors where possible.

C.	Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.  Provide and use lacing bars and distribution spools.

D.	Splices, Taps, and Terminations:  For power and control wiring, use numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.  Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

SPECS WRITER NOTE: Retain paragraph below only if required by manufacturer.  Show independent-signal circuit-grounding methods and details on Drawings.

E.	Grounding:  Provide independent-signal circuit grounding recommended in writing by manufacturer.

3.3 FIELD QUALITY CONTROL

A.	Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installation and supervise pretesting, testing, and adjusting of video surveillance equipment.

B.	Inspection:  Verify that units and controls are properly installed, connected, and labeled, and that interconnecting wires and terminals are identified.

C.	Test Schedule:  Schedule tests after pretesting has been successfully completed and system has been in normal functional operation for at least 14 days.  Provide a minimum of 10 days' notice of test schedule.

D.	Operational Tests:  Perform operational system tests to verify that system complies with Specifications.  Include all modes of system operation.  Test equipment for proper operation in all functional modes.

E.	Remove and replace malfunctioning items and retest as specified above.

F.	Record test results for each piece of equipment.

G.	Retest:  Correct deficiencies identified by tests and observations and retest until specified requirements are met.

3.4 adjusting

A.	Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions and to optimize performance of the installed equipment.  Tasks shall include, but are not limited to, the following:

1.	Check cable connections.

2.	Check proper operation of detectors.

3.	Recommend changes to walk trough detectors, X-ray machines, and associated equipment to improve Owner' utilization of security access detection system.

4.	Provide a written report of adjustments and recommendations.

B.	Adjustment/Alignment/Synchronization: Contractor shall prepare for system activation by following manufacturer’s recommended procedures for adjustment, alignment, programming, or synchronization.  Prepare each component in accordance with appropriate provisions of the component’s installation, operations, and maintenance instructions.

3.5 Cleaning

A.	Cleaning: Subsequent to installation, clean each system component of dust, dirt, grease, or oil incurred during installation in accordance to manufacture instructions.

3.6 INTEGRATION

A.	For integration purposes, the Security Access Detection system shall be integrated with the Physical Access Control System and Database Management via CAT-V cables and where appropriate with CCTV and EPPS. The CCTV Security System will:

1.	Provide full coverage of all lobby entrance screening areas utilizing a fixed color camera.

2.	Record activity on a 24 hours basis.

3.	The CCTV system should have facial recognition software to assist in identifying individuals for current and future purposes.

4.	For additional CCTV system requirements as they relate to the Security Access Detection, refer to Section 28 13 53, SECURITY ACCESS DETECTION.

B.	Integration with CCTV and EPPS security subsystems shall be achieved by computer programming or the direct hardwiring of the systems.

C.	For programming purposes, refer to the manufacturers requirements for correct system operations. Ensure computer hardware being utilized for system integration meets or exceeds the minimum system requirements as well as systems software requirements.

3.7 existing conditions

A.	The Contractor shall visit the site and verify that site conditions are in agreement/compliance with the design package. The Contractor shall report all changes to the site or conditions that will affect performance of the system to the Contracting Officer in the form of a report. The Contractor shall not take any corrective action without written permission received from the Contracting Officer.

B.	Existing Equipment

1.	The Contractor shall connect to and utilize existing equipment, and control signal transmission lines, and devices as outlined in the design package. Equipment and signal lines that are usable in their original configuration without modification may be reused with Contracting Officer approval.

2.	The Contractor shall perform a field survey, including testing and inspection of all existing equipment, power outlets, and signal lines intended to be used by the Security Access Detection, and furnish a report to the Contracting Officer as part of the site survey report. For those items considered nonfunctioning, provide (with the report) specification sheets, or written functional requirements to support the findings and the estimated cost to correct the deficiency. As part of the report, the Contractor shall include a schedule for connection to all existing equipment.

3.	The Contractor shall make written requests and obtain approval prior to disconnecting any signal lines and equipment, and creating equipment downtime. Such work shall proceed only after receiving Contracting Officer approval of these requests. If any device fails after the Contractor has commenced work on that device, signal or control line, the Contractor shall diagnose the failure and perform any necessary corrections to the equipment.

4.	The Contractor shall be held responsible for repair costs due to Contractor negligence, abuse, or improper installation of equipment.

5.	The Contracting Officer shall provide a full list of all equipment that is to be removed or replaced by the Contractor. The Contractor shall dispose of all equipment that has been removed or replaced. In all areas where equipment is removed or replaced the Contractor shall repair those areas to match the current existing conditions.

3.8 SYSTEM START-UP and testing

A.	System Start-Up

1.	The Contractor shall not apply power to any installed Security Access Detection until the following items have been completed:

a.	Security Access Detection equipment items have been set up in accordance with manufacturer's instructions.

b.	A visual inspection of the Security Access Detection system has been conducted to ensure that defective equipment items have not been installed and that there are no loose connections.

c.	System wiring has been tested and verified as correctly connected as indicated.

d.	All system grounding and transient protection systems have been verified as installed and connected as indicated.

e.	Power supplies to be connected to the Security Access Detection system have been verified as the correct voltage, phasing, and frequency as indicated by the manufacturer.

2.	Satisfaction of the above requirements shall not relieve the Contractor of responsibility for incorrect installation, defective equipment items, or collateral damage as a result of Contractor work efforts.

B.	Supplemental Contractor Quality Control: The following requirements supplement the Contractor quality control requirements specified elsewhere in the contract:

1.	The Contractor shall provide the services of technical representatives who are familiar with all components and installation procedures of any installed Security Access Detection; and are approved by the Contracting Officer.

2.	The Contractor will be present on the job site during the preparatory and initial phases of quality control to provide technical assistance.

3.	The Contractor shall also be available on an as needed basis to provide assistance with follow-up phases of quality control.

4.	The Contractor shall participate in the testing and validation of the system and shall provide certification that the system installed is fully operational as all construction document requirements have been fulfilled.

C.	All testing and training shall be compliant with the VA General Requirements, Section 01 00 00, GENERAL REQUIREMENTS.

D.	The Commissioning Agent will observe startup and contractor testing of selected equipment.  Coordinate the startup and contractor testing schedules with the Resident Engineer and Commissioning Agent.  Provide a minimum of 7 days prior notice.

3.9 COMMISSIONING

A.	Provide commissioning documentation in accordance with the requirements of Section 28 08 00 – COMMISSIONING OF ELECTRONIC SAFETY AND SECURITY SYSTEMS for all inspection, start up, and contractor testing required above and required by the System Readiness Checklist provided by the Commissioning Agent.

B.	Components provided under this section of the specification will be tested as part of a larger system.  Refer to Section 28 08 00 – COMMISSIONING OF ELECTRONIC SAFETY AND SECURITY SYSTEMS and related sections for contractor responsibilities for system commissioning.

-----END----