SECTION 23 05 11

COMMON WORK RESULTS FOR HVAC

SPEC WRITER NOTES:

1. Delete between //---- //if not applicable to project. Also delete any other item or paragraph not applicable in the Section and renumber the paragraphs.

2. References to pressure in this section are gauge pressure unless otherwise noted.

3. Provide the year of latest edition to each publication listed in paragraph APPLICABLE PUBLICATIONS.

4. Social cost of greenhouse gases should be included for the equipment selection process per EO 13990 section 5.

1. GENERAL
   1. DESCRIPTION
      1. The requirements of this Section apply to all sections of Division 23, HEATING, VENTILATING, AND AIR CONDITIONING (HVAC).
      2. Definitions:
         1. Exposed: Piping, ductwork, and equipment exposed to view in finished rooms.
         2. Exterior: Piping, ductwork, and equipment exposed to weather be it temperature, humidity, precipitation, wind, or solar radiation.
      3. Abbreviations/Acronyms:
         1. ac: Alternating Current
         2. AC: Air Conditioning
         3. ACU: Air Conditioning Unit
         4. ACR: Air Conditioning and Refrigeration
         5. AI: Analog Input
         6. AISI: American Iron and Steel Institute
         7. AO: Analog Output
         8. ASJ: All Service Jacket
         9. AWG: American Wire Gauge
         10. BACnet: Building Automation and Control Networking Protocol
         11. BAg: Silver-Copper-Zinc Brazing Alloy
         12. BAS: Building Automation System
         13. BCuP: Silver-Copper-Phosphorus Brazing Alloy
         14. bhp: Brake Horsepower
         15. Btu: British Thermal Unit
         16. Btu/h: British Thermal Unit Per Hour
         17. CDA: Copper Development Association
         18. C: Celsius
         19. CD: Compact Disk
         20. CFM: Cubic Foot Per Minute
         21. CH: Chilled Water Supply
         22. CHR: Chilled Water Return
         23. CLR: Color
         24. CO: Carbon Monoxide
         25. COR: Contracting Officer’s Representative
         26. CPD: Condensate Pump Discharge
         27. CPM: Cycles Per Minute
         28. CPVC: Chlorinated Polyvinyl Chloride
         29. CRS: Corrosion Resistant Steel
         30. CTPD: Condensate Transfer Pump Discharge
         31. CTPS: Condensate Transfer Pump Suction
         32. CW: Cold Water
         33. CWP: Cold Working Pressure
         34. CxA: Commissioning Agent
         35. dB: Decibels
         36. dB(A): Decibels (A weighted)
         37. DDC: Direct Digital Control
         38. DI: Digital Input
         39. DO: Digital Output
         40. DVD: Digital Video Disc
         41. DN: Diameter Nominal
         42. DWV: Drainage, Waste and Vent
         43. EPDM: Ethylene Propylene Diene Monomer
         44. EPT: Ethylene Propylene Terpolymer
         45. ETO: Ethylene Oxide
         46. F: Fahrenheit
         47. FAR: Federal Acquisition Regulations
         48. FD: Floor Drain
         49. FED: Federal
         50. FG: Fiberglass
         51. FGR: Flue Gas Recirculation
         52. FOS: Fuel Oil Supply
         53. FOR: Fuel Oil Return
         54. FSK: Foil-Scrim-Kraft facing
         55. FWPD: Feedwater Pump Discharge
         56. FWPS: Feedwater Pump Suction
         57. GC: Chilled Glycol Water Supply
         58. GCR: Chilled Glycol Water Return
         59. GH: Hot Glycol Water Heating Supply
         60. GHR: Hot Glycol Water Heating Return
         61. gpm: Gallons Per Minute
         62. HDPE: High Density Polyethylene
         63. Hg: Mercury
         64. HOA: Hands-Off-Automatic
         65. hp: Horsepower
         66. HPS: High Pressure Steam (414 kPa (60 psig) and above)
         67. HPR: High Pressure Steam Condensate Return
         68. HW: Hot Water
         69. HWH: Hot Water Heating Supply
         70. HWHR: Hot Water Heating Return
         71. Hz: Hertz
         72. ID: Inside Diameter
         73. IPS: Iron Pipe Size
         74. kg: Kilogram
         75. klb: 1000 lb
         76. kPa: Kilopascal
         77. lb: Pound
         78. lb/hr: Pounds Per Hour
         79. L/s: Liters Per Second
         80. L/min: Liters Per Minute
         81. LPS: Low Pressure Steam (103 kPa (15 psig) and below)
         82. LPR: Low Pressure Steam Condensate Gravity Return
         83. MAWP: Maximum Allowable Working Pressure
         84. MAX: Maximum
         85. MBtu/h: 1000 Btu/h
         86. MBtu: 1000 Btu
         87. MED: Medical
         88. m: Meter
         89. MFG: Manufacturer
         90. mg: Milligram
         91. mg/L: Milligrams Per Liter
         92. MIN: Minimum
         93. MJ: Megajoules
         94. ml: Milliliter
         95. mm: Millimeter
         96. MPS: Medium Pressure Steam (110 kPa (16 psig) through 414 kPa (60 psig))
         97. MPR: Medium Pressure Steam Condensate Return
         98. MW: Megawatt
         99. NC: Normally Closed
         100. NF: Oil Free Dry (Nitrogen)
         101. Nm: Newton Meter
         102. NO: Normally Open
         103. NOx: Nitrous Oxide
         104. NPT: National Pipe Thread
         105. NPS: Nominal Pipe Size
         106. OD: Outside Diameter
         107. OSD: Open Sight Drain
         108. OS&Y: Outside Stem and Yoke
         109. PC: Pumped Condensate
         110. PID: Proportional-Integral-Differential
         111. PLC: Programmable Logic Controllers
         112. PP: Polypropylene
         113. PPE: Personal Protection Equipment
         114. ppb: Parts Per Billion
         115. ppm: Parts Per Million
         116. PRV: Pressure Reducing Valve \
         117. PSIA: Pounds Per Square Inch Absolute
         118. psig: Pounds Per Square Inch Gauge
         119. PTFE: Polytetrafluoroethylene
         120. PVC: Polyvinyl Chloride
         121. PVDC: Polyvinylidene Chloride Vapor Retarder Jacketing, White
         122. PVDF: Polyvinylidene Fluoride
         123. rad: Radians
         124. RH: Relative Humidity
         125. RO: Reverse Osmosis
         126. rms: Root Mean Square
         127. RPM: Revolutions Per Minute
         128. RS: Refrigerant Suction
         129. RTD: Resistance Temperature Detectors
         130. RTRF: Reinforced Thermosetting Resin Fittings
         131. RTRP: Reinforced Thermosetting Resin Pipe
         132. SCFM: Standard Cubic Feet Per Minute
         133. SPEC: Specification
         134. SPS: Sterile Processing Services
         135. STD: Standard
         136. SDR: Standard Dimension Ratio
         137. SUS: Saybolt Universal Second
         138. SW: Soft water
         139. SWP: Steam Working Pressure
         140. TAB: Testing, Adjusting, and Balancing
         141. TDH: Total Dynamic Head
         142. TEFC: Totally Enclosed Fan-Cooled
         143. TFE: Tetrafluoroethylene
         144. THERM: 100,000 Btu
         145. THHN: Thermoplastic High-Heat Resistant Nylon Coated Wire
         146. THWN: Thermoplastic Heat & Water-Resistant Nylon Coated Wire
         147. T/P: Temperature and Pressure
         148. USDA: U.S. Department of Agriculture
         149. V: Volt
         150. VAC: Vacuum
         151. VA: Veterans Administration
         152. VAC: Voltage in Alternating Current
         153. VA CFM: VA Construction & Facilities Management
         154. VA CFM CSS: VA Construction & Facilities Management, Consulting Support Service
         155. VAMC: Veterans Administration Medical Center
         156. VHA OCAMES: Veterans Health Administration – Office of Capital Asset Management Engineering and Support
         157. VR: Vacuum condensate return
         158. WCB: Wrought Carbon Steel, Grade B
         159. WG: Water Gauge or Water Column
         160. WOG: Water, Oil, Gas
   2. RELATED WORK
      1. Section 01 00 00, GENERAL REQUIREMENTS.
      2. Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.
      3. Section 01 74 19, CONSTRUCTION WASTE MANAGEMENT.
      4. Section 01 81 13, SUSTAINABLE CONSTRUCTION REQUIREMENTS.
      5. //Section 01 91 00, GENERAL COMMISSIONING REQUIREMENTS.//
      6. //Section 02 82 11, TRADITIONAL ASBESTOS ABATEMENT.//
      7. //Section 03 30 00, CAST-IN-PLACE CONCRETE.//
      8. //Section 05 31 00, STEEL DECKING.//
      9. //Section 05 36 00, COMPOSITE METAL DECKING.//
      10. Section 05 50 00, METAL FABRICATIONS.
      11. Section 07 84 00, FIRESTOPPING.
      12. Section 07 92 00, JOINT SEALANTS.
      13. Section 09 91 00, PAINTING.
      14. //Section 13 05 41, SEISMIC RESTRAINT REQUIREMENTS FOR NON-STRUCTURAL COMPONENTS.//
      15. Section 23 05 12, GENERAL MOTOR REQUIREMENTS FOR HVAC and STEAM GENERATION EQUIPMENT.
      16. Section 23 05 41, NOISE AND VIBRATION CONTROL FOR HVAC PIPING and EQUIPMENT.
      17. Section 23 05 93, TESTING, ADJUSTING, AND BALANCING FOR HVAC.
      18. Section 23 07 11, HVAC AND BOILER PLANT INSULATION.
      19. //Section 23 08 00, COMMISSIONING OF HVAC SYSTEMS.//
      20. Section 23 09 23, DIRECT-DIGITAL CONTROL SYSTEM FOR HVAC.
      21. Section 23 36 00, AIR TERMINAL UNITS.
      22. Section 23 82 00, CONVECTION HEATING AND COOLING UNITS.
      23. Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS.
      24. Section 26 05 19, LOW-VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES.
      25. Section 26 29 11, MOTOR CONTROLLERS.
   3. APPLICABLE PUBLICATIONS

SPEC WRITER NOTES:

1. Make material requirements agree with requirements specified in the referenced Applicable Publications. Verify and update the publication list to that which applies to the project, unless the reference applies to all mechanical systems. Publications that apply to all mechanical systems may not be specifically referenced in the body of the specification, but, shall form a part of this specification.

2. Insert the year of approved latest edition of the publications between the brackets // // and delete the brackets if applicable to this project.

* + 1. The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only. Where conflicts occur these specifications and the VHA standard will govern.
    2. Air‑Conditioning, Heating, and Refrigeration Institute (AHRI):

430‑//2020// Performance Rating of Central Station Air‑Handling Unit Supply Fans

* + 1. Air Movement and Control Association (AMCA):

410-//1996// Recommended Safety Practices for Users and Installers of Industrial and Commercial Fans

* + 1. American Society of Mechanical Engineers (ASME):

B31.1-//2020// Power Piping

B31.9-//2020// Building Services Piping

ASME Boiler and Pressure Vessel Code:

BPVC Section IX-//2021// Welding, Brazing, and Fusing Qualifications

* + 1. American Society for Testing and Materials (ASTM):

A36/A36M-//2019// Standard Specification for Carbon Structural Steel

A575-//1996(2020)// Standard Specification for Steel Bars, Carbon, Merchant Quality, M-Grades

* + 1. Association for Rubber Products Manufacturers (ARPM):

IP-20-//2015// Specifications for Drives Using Classical V‑Belts and Sheaves

IP-21-//2016// Specifications for Drives Using Double-V (Hexagonal) Belts

IP-24-//2016// Specifications for Drives Using Synchronous Belts

IP-27-//2015// Specifications for Drives Using Curvilinear Toothed Synchronous Belts

* + 1. Manufacturers Standardization Society of the Valve and Fittings Industry, Inc.(MSS):

SP-58-//2018// Pipe Hangers and Supports-Materials, Design, Manufacture, Selection, Application, and Installation

SP-127-//2014a// Bracing for Piping Systems: Seismic–Wind–Dynamic Design, Selection, and Application

* + 1. Military Specifications (MIL):

MIL-P-21035B-//2021// Paint High Zinc Dust Content, Galvanizing Repair (Metric)

* + 1. National Fire Protection Association (NFPA):

70-//2020// National Electrical Code (NEC)

101-//2021// Life Safety Code

* + 1. Department of Veterans Affairs (VA):

PG-18-10-//2020(R2021)// Physical Security and Resiliency Design Manual

* 1. SUBMITTALS
     1. Submittals, including number of required copies, shall be submitted in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.
     2. Information and material submitted under this section shall be marked “SUBMITTED UNDER SECTION 23 05 11, COMMON WORK RESULTS FOR HVAC”, with applicable paragraph identification.
     3. //If the project is phased submit complete phasing plan/schedule with manpower levels prior to commencing work. The phasing plan shall be detailed enough to provide milestones in the process that can be verified.//
     4. Contractor shall make all necessary field measurements and investigations to assure that the equipment and assemblies will meet contract requirements, and all equipment that requires regular maintenance, calibration, etc are accessable from the floor or permanent work platform. It is the Contractor’s responsibility to ensure all submittals meet the VA specifications and requirements and it is assumed by the VA that all submittals do meet the VA specifications unless the Contractor has requested a variance in writing and approved by COR prior to the submittal. If at any time during the project it is found that any item does not meet the VA specifications and there was no variance approval the Contractor shall correct at no additional cost or time to the Government even if a submittal was approved.
     5. If equipment is submitted which differs in arrangement from that shown, provide documentation proving equivalent performance, design standards and drawings that show the rearrangement of all associated systems. Additionally, any impacts on ancillary equipment or services such as foundations, piping, and electrical shall be the Contractor’s responsibility to design, supply, and install at no additional cost or time to the Government. VA approval will be given only if all features of the equipment and associated systems, including accessibility, are equivalent to that required by the contract.
     6. Prior to submitting shop drawings for approval, Contractor shall certify in writing that manufacturers of all major items of equipment have each reviewed contract documents, and have jointly coordinated and properly integrated their equipment and controls to provide a complete and efficient installation.
     7. Submittals and shop drawings for interdependent items, containing applicable descriptive information, shall be furnished together. Coordinate and properly integrate materials and equipment to provide a completely compatible and efficient installation.

SPEC WRITER NOTE: Include the paragraph below if samples are required for any specified items.

* + 1. //Samples: Samples will not be required, except for insulation or where materials offered differ from specification requirements. Samples shall be accompanied by full description of characteristics different from specification. The Government, at the Government’s expense, will perform evaluation and testing if necessary. The Contractor may submit samples of additional material at the Contractor's option; however, if additional samples of materials are submitted later, pursuant to Government request, adjustment in contract price and time will be made.//

SPEC WRITER NOTE: Include the paragraph below if mock-ups are required for any specified items. Indicate and describe required mock-ups in the submittal paragraph of the individual Division 23 sections.

* + 1. //Mock-ups: Mock-ups are required for critical items and typical component installations replicated numerous times throughout the project as indicated in the individual Division 23 sections. The COR and VAMC representatives shall review and approve the mock-up prior to installation of additional applicable components.//
    2. Coordination/Shop Drawings:
       1. Submit complete consolidated and coordinated shop drawings for all new systems, and for existing systems that are in the same areas.
       2. The coordination/shop drawings shall include plan views, elevations and sections of all systems and shall be on a scale of not less than 1:32 (3/8 inch equal to one foot). Clearly identify and dimension the proposed locations of the principal items of equipment. The drawings shall clearly show locations and adequate clearance for all equipment, piping, valves, control panels and other items. Show the access means for all items requiring access for operations and maintenance. Provide detailed coordination/shop drawings of all piping and duct systems. The drawings should include all lockout/tagout points for all energy/hazard sources for each piece of equipment. Coordinate lockout/tagout procedures and practices with local VA requirements.
       3. Do not install equipment foundations, equipment or piping until coordination/shop drawings have been approved.
       4. In addition, for HVAC systems, provide details of the following:
          1. Mechanical equipment rooms.
          2. //Interstitial space.//
          3. Hangers, inserts, supports, and bracing.
          4. Pipe sleeves.
          5. Duct or equipment penetrations of floors, walls, ceilings, or roofs.
    3. Manufacturer's Literature and Data Including: Full item description and optional features and accessories. Include dimensions, weights, materials, applications, standard compliance, model numbers, size, and capacity. Submit under the pertinent section rather than under this section.
       1. Submit belt drive with the driven equipment. Submit selection data for specific drives when requested by the COR.
       2. Submit electric motor data and variable speed drive data with the driven equipment.
       3. Equipment and materials identification.
       4. Fire-stopping materials.
       5. Hangers, inserts, supports and bracing. Provide complete stress analysis for variable spring and constant support hangers.
       6. Wall, floor, and ceiling plates.
    4. Rigging Plan: Provide documentation of the capacity and weight of the rigging and equipment intended to be used. The plan shall include the path of travel of the load, the staging area and intended access, and qualifications of the operator and signal person.
    5. HVAC Maintenance Data and Operating Instructions:
       1. Maintenance and operating manuals in accordance with Section 01 00 00, GENERAL REQUIREMENTS, paragraph INSTRUCTIONS for systems and equipment.

SPEC WRITER NOTE: Coordinate O&M Manual and commissioning requirements with Section 01 00 00, GENERAL REQUIREMENTS and Section 01 91 00, GENERAL COMMISSIONING REQUIREMENTS. O&M Manuals shall be submitted for content review as part of closeout documents.

* + - 1. Complete operating and maintenance manuals including wiring diagrams, technical data sheets, information for ordering replacement parts, and troubleshooting guide:
         1. Include complete list indicating all components of the systems.
         2. Include complete diagrams of the internal wiring for each item of equipment.
         3. Diagrams shall have their terminals identified to facilitate installation, operation, and maintenance.
      2. Provide a listing of recommended replacement parts for keeping in stock supply, including sources of supply for equipment. Include in the listing for belts: Belt manufacturer, model number, size and style, and distinguished whether of multiple belt sets.
    1. Provide copies of approved HVAC equipment submittals to the TAB //and Commissioning// Subcontractor.
    2. //Completed System Readiness Checklist provided by the CxA and completed by the Contractor, signed by a qualified technician, and dated on the date of completion, in accordance with the requirements of Section 23 08 00, COMMISSIONING OF HVAC SYSTEMS.//
    3. //Submit training plans and instructor qualifications in accordance with the requirements of Section 23 08 00, COMMISSIONING OF HVAC SYSTEMS.//
  1. QUALITY ASSURANCE
     1. Mechanical, electrical and associated systems shall be safe, reliable, efficient, durable, easily and safely operable and maintainable, easily and safely accessible, and in compliance with applicable codes as specified. The systems shall be comprised of high quality institutional-class and industrial-class products of manufacturers that are experienced specialists in the required product lines. All construction firms and personnel shall be experienced and qualified specialists in industrial and institutional HVAC.
     2. Flow Rate Tolerance for HVAC Equipment: Section 23 05 93, TESTING, ADJUSTING, AND BALANCING FOR HVAC.
     3. Equipment Vibration Tolerance:
        1. Refer to Section 23 05 41, NOISE AND VIBRATION CONTROL FOR HVAC PIPING and EQUIPMENT. Equipment shall be factory-balanced to this tolerance and re-balanced onsite, as necessary.
        2. After HVAC air balance work is completed and permanent drive sheaves are in place, perform field mechanical balancing and adjustments required to meet the specified vibration tolerance.
     4. Products Criteria:
        1. Standard Products: Material and equipment shall be the standard products of a manufacturer regularly engaged in the manufacture of the products for at least 3 years (or longer as specified elsewhere). The design, model and size of each item shall have been in satisfactory and efficient operation on at least three installations for approximately three years. However, digital electronics devices, software and systems such as controls, instruments, computer work station, shall be the current generation of technology and basic design that has a proven satisfactory service record of at least three years. See other specification sections for any exceptions and/or additional requirements.
        2. Refer to all other sections for quality assurance requirements for systems and equipment specified therein.
        3. All items furnished shall be free from defects that would adversely affect the performance, maintainability and appearance of individual components and overall assembly.
        4. The products and execution of work specified in Division 23 sections shall conform to the referenced codes and standards as required by the specifications. Local codes and amendments shall be enforced, along with requirements of local utility companies. The most stringent requirements of these specifications, local codes, or utility company requirements shall always apply. Any conflicts shall be brought to the attention of the COR.
        5. Multiple Units: When two or more units of materials or equipment of the same type or class are required, these units shall be of the same manufacturer and model number, or if different models are required they shall be of the same manufacturer and identical to the greatest extent possible (i.e., same model series).
        6. Assembled Units: Performance and warranty of all components that make up an assembled unit shall be the responsibility of the manufacturer of the completed assembly.
        7. Nameplates: Nameplate bearing manufacturer's name or identifiable trademark shall be securely affixed in a conspicuous place on equipment, or name or trademark cast integrally with equipment, stamped or otherwise permanently marked on each item of equipment.
        8. Use of asbestos products or equipment or materials containing asbestos is prohibited.
     5. HVAC Equipment Service Providers: Service providers shall be authorized and trained by the manufacturers of the equipment supplied. These providers shall be capable of responding onsite and provide acceptable service to restore equipment operations within //4// // // hours of receipt of notification by phone, e-mail or fax in event of an emergency, such as the shutdown of equipment; or within //24// // // hours in a non-emergency. Submit names, mail and e-mail addresses and phone numbers of service personnel and companies providing service under these conditions for (as applicable to the project): fans, air handling units, chillers, cooling towers, control systems, pumps, critical instrumentation, computer workstation and programming.
     6. HVAC Mechanical Systems Welding: Before any welding is performed, Contractor shall submit a certificate certifying that welders comply with the following requirements:
        1. HVAC mechanical systems welding shall meet ASME BPVC Section IX. Provide proof of current certification.
        2. Comply with provisions of ASME B31 series "Code for Pressure Piping".
        3. Certify that each welder and welding operator has passed American Welding Society (AWS) qualification tests for the welding processes involved, and that certification is current.
        4. All welds shall be stamped according to the provisions of the AWS or ASME as required herein and by the associated code.
     7. Manufacturer's Recommendations: Where installation procedures or any part thereof are required to be in accordance with the recommendations of the manufacturer of the material being installed, printed copies of these recommendations shall be furnished to the COR with submittals. Installation of the item will not be allowed to proceed until the recommendations are received. Failure to furnish these recommendations can be cause for rejection of the material and removal by the Contractor and no additional cost or time to the Government.
     8. Execution (Installation, Construction) Quality:
        1. Apply and install all items in accordance with manufacturer's written instructions. Refer conflicts between the manufacturer's instructions and the contract documents to the COR for resolution. Provide written hard copies and computer files on CD or DVD of manufacturer’s installation instructions to the COR with submittals prior to commencing installation of any item. Installation of the item will not be allowed to proceed until the recommendations are received and approved by the VA. Failure to furnish these recommendations is a cause for rejection of the material.
        2. All items that require access, such as for operating, cleaning, servicing, maintenance, and calibration, shall be easily and safely accessible by persons standing at floor level, or standing on permanent platforms, without the use of portable ladders. Examples of these items include, but are not limited to, all types of valves, filters and strainers, transmitters, control devices. Prior to commencing installation work, refer conflicts between this requirement and contract documents to the COR for resolution. Failure of the Contractor to resolve, or point out any issues will result in the Contractor correcting at no additional cost or time to the Government.
        3. Complete coordination/shop drawings shall be required in accordance with paragraph SUBMITTALS. Construction work shall not start on any system until the coordination/shop drawings have been approved by VA.
        4. Workmanship/craftsmanship will be of the highest quality and standards. The VA reserves the right to reject any work based on poor quality of workmanship this work shall be removed and done again at no additional cost or time to the Government.
     9. Upon request by Government, provide lists of previous installations for selected items of equipment. Include contact persons who will serve as references, with current telephone numbers and e-mail addresses.
     10. Guaranty: Warranty of Construction, FAR Clause 52.246-21.
     11. Bio‑Based Materials: For products designated by the USDA’s Bio‑Preferred Program, provide products that meet or exceed USDA recommendations for bio‑based content, so long as products meet all performance requirements in this specification section. For more information regarding the product categories covered by the Bio‑Preferred Program, visit [http://www.biopreferred.gov](http://www.biopreferred.gov/).
     12. Refer to Section 01 81 13, SUSTAINABLE CONSTRUCTION REQUIREMENTS for additional sustainable design requirements.
  2. DELIVERY, STORAGE AND HANDLING
     1. Protection of Equipment:
        1. Equipment and material placed on the job site shall remain in the custody of the Contractor until phased acceptance, whether or not the Government has reimbursed the Contractor for the equipment and material. The Contractor is solely responsible for the protection of such equipment and material against any damage or theft.
        2. Large equipment such as boilers, chillers, cooling towers, fans, and air handling units if shipped on open trailer trucks shall be covered with shrink on plastics or water proof tarpaulins that provide protection from exposure to rain, road salts and other transit hazards. Protection shall be kept in place until equipment is moved into a building or installed as designed.
        3. Repair damaged equipment in first class, new operating condition and appearance; or, replace same as determined and directed by the COR. Such repair or replacement shall be at no additional cost or time to the Government.
        4. Protect interiors of new equipment and piping systems against entry of foreign matter. Clean both inside and outside before painting or placing equipment in operation.
        5. Existing equipment and piping being worked on by the Contractor shall be under the custody and responsibility of the Contractor and shall be protected as required for new work.
        6. Protect plastic piping and tanks from ultraviolet light (sunlight).
     2. Cleanliness of Piping and Equipment Systems:
        1. Exercise care in storage and handling of equipment and piping material to be incorporated in the work. Remove debris arising from cutting, threading and welding of piping.
        2. Piping systems shall be flushed, blown or pigged as necessary to deliver clean systems.
        3. Clean interior of all tanks prior to delivery for beneficial use by the Government.
        4. Boilers shall be left clean following final internal inspection by Government, insurance representative, or inspector.
        5. Contractor shall be fully responsible for all costs, damage, and delay arising from failure to provide clean systems.
  3. AS-BUILT DOCUMENTATION
     1. Submit manufacturer’s literature and data updated to include submittal review comments and any equipment substitutions.
     2. Submit operation and maintenance data updated to include submittal review comments, VA approved substitutions and construction revisions shall be //in electronic version on CD or DVD// inserted into a three-ring binder. All aspects of system operation and maintenance procedures, including applicable piping isometrics, wiring diagrams of all circuits, a written description of system design, control logic, and sequence of operation shall be included in the operation and maintenance manual. The operations and maintenance manual shall include troubleshooting techniques and procedures for emergency situations. Notes on all special systems or devices shall be included. A List of recommended spare parts (manufacturer, model number, and quantity) shall be furnished. Information explaining any special knowledge or tools the owner will be required to employ shall be inserted into the As-Built documentation.

SPEC WRITER NOTE: Select and edit one of the bracketed options after the paragraph below to indicate the format in which the contractor shall provide record drawing files. Select the hand-marked option only when the designer has been separately contracted to provide the record drawings from the contractor’s mark-ups. Select the BIM option only when a BIM model will be generated, which is typically only performed by the designer on some Design-Bid-Build projects or by the contractor on some Design-Build projects.

* + 1. The installing Contractor shall maintain as-built drawings of each completed phase for verification; and, shall provide the complete set at the time of final systems certification testing. Should the installing Contractor engage the testing company to provide as-built or any portion thereof, it shall not be deemed a conflict of interest or breach of the ‘third party testing company’ requirement. Provide record drawings as follows:
       1. //Red-lined, hand-marked drawings are to be provided, with one paper copy and a scanned PDF version of the hand-marked drawings provided on CD or DVD.//
       2. //As-built drawings are to be provided, with a copy of them on AutoCAD version // // provided on CD or DVD. The CAD drawings shall use multiple line layers with a separate individual layer for each system.//
       3. //As-built drawings are to be provided, with a copy of them in three-dimensional Building Information Modeling (BIM) software version // // provided on CD or DVD.//
    2. The as-built drawings shall indicate the location and type of all lockout/tagout points for all energy sources for all equipment and pumps to include breaker location and numbers, valve tag numbers, etc. Coordinate lockout/tagout procedures and practices with local VA requirements.
    3. Certification documentation shall be provided to COR 21 working days prior to submitting the request for final inspection. The documentation shall include all test results, the names of individuals performing work for the testing agency on this project, detailed procedures followed for all tests, and provide documentation/certification that all results of tests were within limits specified. Test results shall contain written sequence of test procedure with written test results annotated at each step along with the expected outcome or setpoint. The results shall include all readings, including but not limited to data on device (make, model and performance characteristics), normal pressures, switch ranges, trip points, amp readings, and calibration data to include equipment serial numbers or individual identifications, etc.
  1. //JOB CONDITIONS – WORK IN EXISTING BUILDING
     1. Building Operation: Government employees will be continuously operating and managing all facilities, including temporary facilities that serve the VAMC.
     2. Maintenance of Service: Schedule all work to permit continuous service as required by the VAMC.
     3. Steam and Condensate Service Interruptions: Limited steam and condensate service interruptions, as required for interconnections of new and existing systems, will be permitted by the COR during periods when the demands are not critical to the operation of the VAMC. These non-critical periods are limited to between 8 pm and 5 am in the appropriate off-season (if applicable). Provide at least 10 working days advance notice to the COR. The request shall include a detailed plan on the proposed shutdown and the intended work to be done along with manpower levels. All equipment and materials shall be onsite and verified with plan //5// // // days prior to the shutdown or it will need to be rescheduled.
     4. //Phasing of Work: Comply with all requirements shown on contract documents. Contractor shall submit a complete detailed phasing plan/schedule with manpower levels prior to commencing work. The phasing plan shall be detailed enough to provide milestones in the process that can be verified.//
     5. Building Working Environment: Maintain the architectural and structural integrity of the building and the working environment at all times. Maintain the interior of building at 18 degrees C (65 degrees F) minimum. Limit the opening of doors, windows or other access openings to brief periods as necessary for rigging purposes. Storm water or ground water leakage is prohibited. Provide daily clean-up of construction and demolition debris on all floor surfaces and on all equipment being operated by VA. Maintain all egress routes and safety systems/devices.
     6. Acceptance of Work for Government Operation: As new equipment, systems and facilities are made available for operation and these items are deemed of beneficial use to the Government, inspections will be made and tests will be performed. Based on the inspections, a list of contract deficiencies will be issued to the Contractor. After correction of deficiencies as necessary for beneficial use, the Contracting Officer will process necessary acceptance and the equipment will then be under the control and operation of Government personnel.

SPEC WRITER NOTE: Delete the following paragraph if not applicable to project.

* + 1. //Temporary Facilities: Refer to paragraph TEMPORARY PIPING AND EQUIPMENT in this section.// **//**

1. PRODUCTS
   1. FACTORY ASSEMBLED PRODUCTS
      1. Provide maximum standardization of components to reduce spare part requirements.
      2. Performance and warranty of all components that make up an assembled unit shall be the responsibility of the manufacturer of the completed assembly.
         1. All components of an assembled unit need not be products of same manufacturer.
         2. Constituent parts that are alike shall be products of a single manufacturer.
         3. Components shall be compatible with each other and with the total assembly for intended service.
         4. Contractor shall guarantee performance of assemblies of components, and shall repair or replace elements of the assemblies as required to deliver specified performance of the complete assembly.
      3. Equipment and components of equipment shall bear manufacturer's name and trademark, model number, serial number and performance data on a nameplate securely affixed in a conspicuous place, or cast integral with, stamped or otherwise permanently marked upon the components of the equipment.
      4. Major items of equipment, which serve the same function, shall be the same make and model. Exceptions must be approved by the VA, but may be permitted if performance requirements cannot be met.
   2. COMPATIBILITY OF RELATED EQUIPMENT
      1. Equipment and materials installed shall be compatible in all respects with other items being furnished and with existing items so that the result will be a complete and fully operational plant that conforms to contract requirements.
   3. V-BELT DRIVES
      1. Type: ARPM standard V-belts with proper motor pulley and driven sheave. Belts shall be constructed of reinforced cord and rubber.
      2. Dimensions, Rating and Selection Standards: ARPM IP‑20 and ARPM IP‑21.
      3. Minimum Horsepower Rating: Motor horsepower plus recommended ARPM service factor (not less than 20 percent) in addition to the ARPM allowances for pitch diameter, center distance, and arc of contact.
      4. Maximum Speed: 25 m/s (5000 feet per minute).
      5. Adjustment Provisions: For alignment and ARPM standard allowances for installation and take-up.
      6. Drives may utilize a single V-Belt (any cross section) when it is the manufacturer's standard.
      7. Multiple Belts: Matched to ARPM specified limits by measurement on a belt measuring fixture. Seal matched sets together to prevent mixing or partial loss of sets. Replacement, when necessary, shall be an entire set of new matched belts.
      8. Sheaves and Pulleys:
         1. Material: Pressed steel, or close-grained cast-iron.
         2. Bore: Fixed or bushing type for securing to shaft with keys.
         3. Balanced: Statically and dynamically.
         4. Groove spacing for driving and driven pulleys shall be the same.
      9. Drive Types, Based on AHRI 430:
         1. Provide adjustable-pitch //or fixed-pitch// drive as follows:
            1. Fan Speeds Up To 1800 RPM: 7.5 kW (10 horsepower) and smaller.
            2. Fan Speeds Over 1800 RPM: 2.2 kW (3 horsepower) and smaller.
         2. Provide fixed-pitch drives for drives larger than those listed above.
         3. The final fan speeds required to just meet the system CFM and pressure requirements, without throttling the design air flow branch, shall be determined by adjustment of a temporary adjustable-pitch motor sheave or by fan law calculation if a fixed-pitch drive is used initially.
      10. Final Drive Set: If adjustment is required beyond the capabilities of the factory drive set, the final drive set shall be provided as part of this contract at no additional cost or time to the Government.
   4. SYNCHRONOUS BELT DRIVES
      1. Type: ARPM synchronous belts with proper motor pulley and driven sheave. Belts shall be constructed of reinforced cord and rubber.
      2. Dimensions, Rating and Selection Standards: ARPM IP‑24 and ARPM IP‑27.
      3. Minimum Horsepower Rating: Motor horsepower plus recommended ARPM service factor (not less than 20 percent) in addition to the ARPM allowances for pitch diameter, center distance, and arc of contact.
      4. Maximum Speed: 25 m/s (5000 feet per minute).
      5. Adjustment Provisions: For alignment and ARPM standard allowances for installation and take-up.
      6. Drives may utilize a single belt of manufacturer’s standard width for the application.
      7. Multiple Belts: Matched to ARPM specified limits by measurement on a belt measuring fixture. Seal matched sets together to prevent mixing or partial loss of sets. Replacement, when necessary, shall be an entire set of new matched belts.
      8. Sheaves and Pulleys:
         1. Material: Pressed steel, or close-grained cast-iron.
         2. Bore: Fixed or bushing type for securing to shaft with keys.
         3. Balanced: Statically and dynamically.
      9. Final Drive Set: The final fan speeds required to just meet the system CFM and pressure requirements, without throttling the design air flow branch, shall be determined by fan law calculation. If adjustment is required beyond the capabilities of the factory drive set, the final drive set shall be provided as part of this contract at no additional cost or time to the Government.
   5. DRIVE GUARDS
      1. For machinery and equipment, provide guards as shown in AMCA 410 for belts, chains, couplings, pulleys, sheaves, shafts, gears and other moving parts regardless of height above the floor to prevent damage to equipment and injury to personnel. Drive guards may be excluded where motors and drives are inside factory-fabricated air handling unit casings.
      2. Pump shafts and couplings shall be fully guarded by a sheet steel guard, covering coupling and shaft but not bearings. Material shall be minimum 16-gauge sheet steel; all edges shall be hemmed and ends shall be bent into flanges and the flanges shall be drilled and attached to pump base with minimum of four 6 mm (1/4 inch) bolts. Reinforce guard as necessary to prevent side play forcing guard onto couplings.
      3. V-belt and sheave assemblies shall be totally enclosed, firmly mounted, non-resonant. Guard shall be an assembly of minimum 22-gauge sheet steel and expanded or perforated metal to permit observation of belts. 25 mm (1 inch) diameter hole shall be provided at each shaft centerline to permit speed measurement.
      4. Materials: Sheet steel, expanded metal or wire mesh rigidly secured so as to be removable without disassembling pipe, duct, or electrical connections to equipment.
      5. Access for Speed Measurement: 25 mm (1 inch) diameter hole at each shaft center.
   6. LIFTING ATTACHMENTS
      1. Provide equipment with suitable lifting attachments to enable equipment to be lifted in its normal position. Lifting attachments shall withstand any handling conditions that might be encountered, without bending or distortion of shape, such as rapid lowering and braking of load.
   7. ELECTRIC MOTORS

SPEC WRITER NOTE: Verify that special motor requirements when required, such as two-speed or explosion proof, are shown on the drawings in the equipment schedules.

* + 1. All material and equipment furnished, and installation methods shall conform to the requirements of Section 23 05 12, GENERAL MOTOR REQUIREMENTS FOR HVAC AND STEAM GENERATION EQUIPMENT; Section 26 29 11, MOTOR CONTROLLERS; and, Section 26 05 19, LOW-VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES. Provide all electrical wiring, conduit, and devices necessary for the proper connection, protection and operation of the systems. Provide special energy efficient premium efficiency type motors as scheduled.
  1. VARIABLE SPEED MOTOR CONTROLLERS
     1. Refer to Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS and Section 26 29 11, MOTOR CONTROLLERS for specifications.
     2. Coordinate variable speed motor controller communication protocol with Section 23 09 23, DIRECT-DIGITAL CONTROL SYSTEM FOR HVAC.

SPEC WRITER NOTE: Verify that drawings indicate “with bypass contactor” or “without bypass contactor” on all variable frequency drives shown.

* + 1. Provide variable speed motor controllers with or without a bypass contactor as indicated in the contract documents.
    2. The combination of controller and motor shall be provided by the manufacturer of the driven equipment, such as pumps and fans, and shall be rated for 100 percent output performance. Multiple units of the same class of equipment, i.e., air handlers, fans, pumps, shall be product of a single manufacturer.
    3. Motors shall be premium efficiency type and be approved by the motor controller manufacturer. The controller-motor combination shall be guaranteed to provide full motor nameplate horsepower in variable frequency operation. Both driving and driven motor/fan sheaves shall be fixed pitch.
    4. Controller shall not add any current or voltage transients to the input ac power distribution system, DDC controls, sensitive medical equipment, etc., nor shall be affected from other devices on the ac power system.
  1. EQUIPMENT AND MATERIALS IDENTIFICATION

SPEC WRITER NOTE: Choose paragraph “A” or “B”, whichever is appropriate for the project.

* + 1. //Use symbols, nomenclature and equipment numbers specified, shown in the contract documents, and shown in the maintenance manuals. Identification for piping is specified in Section 09 91 00, PAINTING.//
    2. //Use symbols, nomenclature and equipment numbers specified, shown in the contract documents, and shown in the maintenance manuals. In addition, provide bar code identification nameplate for all equipment which will allow the equipment identification code to be scanned into the system for maintenance and inventory tracking. Identification for piping is specified in Section 09 91 00, PAINTING.//
    3. Interior (Indoor) Equipment: Engraved nameplates, with letters not less than 5 mm (3/16 inch) high of brass with black-filled letters, or rigid black plastic with white letters specified in Section 09 91 00, PAINTING permanently fastened to the equipment. Identify unit components such as coils, filters, fans, etc.
    4. Exterior (Outdoor) Equipment: Brass nameplates, with engraved black filled letters, not less than 5 mm (3/16 inch) high riveted or bolted to the equipment.
    5. Control Items: Label all instrumentation, temperature and humidity sensors, controllers and control dampers. Identify and label each item as they appear on the control diagrams.
    6. Valve Tags and Lists:
       1. HVAC and Mechanical Rooms: Provide for all valves other than for equipment in Section 23 82 00, CONVECTION HEATING AND COOLING UNITS and Section 23 36 00, AIR TERMNAL UNITS.
       2. Valve Tags: Engraved black filled numbers and letters not less than 13 mm (1/2 inch) high for number designation, and not less than 6 mm (1/4 inch) for service designation on 19-gauge 38 mm (1‑1/2 inches) round brass disc, attached with brass "S" hook or brass chain.
       3. Valve Lists: Typed or printed plastic coated card(s), sized 216 mm (8‑1/2 inches) by 279 mm (11 inches) showing tag number, valve function and area of control, for each service or system. Punch sheets for a 3-ring notebook.
       4. Provide detailed plan for each floor of the building indicating the location and valve number for each valve. Identify location of each valve with a color-coded thumb tack in ceiling.
    7. Ceiling Grid Labels:
       1. 50 mm (2 inch) long by 13 mm (1/2 inch) wide by 0.025 mm (1 mil) thick UV resistant metalized polyester label with red border color and black custom lettering on white background interior. Peel and stick adhesive backing. Label and adhesive manufactured specifically for use in equipment inventory tagging.
       2. Custom print labels with above ceiling HVAC equipment numbers.
  1. FIRESTOPPING
     1. Section 07 84 00, FIRESTOPPING specifies an effective barrier against the spread of fire, smoke and gases where penetrations occur for piping and ductwork. Refer to Section 23 07 11, HVAC AND BOILER PLANT INSULATION, for firestop pipe and duct insulation.
  2. GALVANIZED REPAIR COMPOUND
     1. Mil-P-21035B, paint form.
  3. HVAC PIPE AND EQUIPMENT SUPPORTS AND RESTRAINTS
     1. Vibration Isolators: Refer to Section 23 05 41, NOISE AND VIBRATION CONTROL FOR HVAC PIPING AND EQUIPMENT.
     2. Supports for Roof Mounted Items:
        1. Equipment: Equipment rails shall be galvanized steel, minimum 1.3 mm (18 gauge), with integral baseplate, continuous welded corner seams, factory‑installed 50 by 100 mm (2 by 4 inches) treated wood nailer, 1.3 mm (18 gauge) galvanized steel counter flashing cap with screws, built-in cant strip, (except for gypsum or tectum deck), minimum height 279 mm (11 inches). For surface insulated roof deck, provide raised cant strip to start at the upper surface of the insulation.
        2. Pipe/Duct Pedestals: Provide a galvanized Unistrut channel welded to U-shaped mounting brackets which are secured to side of rail with galvanized lag bolts.
     3. Pipe Supports: Comply with MSS SP-58. Type Numbers specified refer to this standard. For selection and application comply with MSS SP-58. Refer to Section 05 50 00, METAL FABRICATIONS, for miscellaneous metal support materials and prime coat painting requirements.
     4. Attachment to Concrete Building Construction:
        1. Concrete Insert: MSS SP-58, Type 18.
        2. Self-Drilling Expansion Shields and Machine Bolt Expansion Anchors: Permitted in concrete not less than 100 mm (4 inches) thick when approved by the COR for each job condition.
        3. Power-Driven Fasteners: Permitted in existing concrete or masonry not less than 100 mm (4 inches) thick when approved by the COR for each job condition.
     5. Attachment to Steel Building Construction:
        1. Welded Attachment: MSS SP-58, Type 22.
        2. Beam Clamps: MSS SP-58, Types 20, 21, 28 or 29. Type 23 C-clamp shall be used for individual copper tubing up to 22 mm (7/8 inch) outside diameter.

SPEC WRITER NOTE: Include paragraph below if for new construction (roof deck) only.

* + 1. //Attachment to Metal Pan or Deck: As required for materials specified in //Section 05 31 00, STEEL DECKING// //Section 05 36 00, COMPOSITE METAL DECKING//.//

SPEC WRITER NOTE: Include paragraph below for renovations of existing facilities.

* + 1. //Attachment to Existing Structure: Support from existing floor/roof frame.//
    2. Attachment to Wood Construction: Wood screws or lag bolts.
    3. Hanger Rods: Hot-rolled steel, ASTM A36/A36M or ASTM A575 for allowable load listed in MSS SP-58. For piping, provide adjustment means for controlling level or slope. Types 13 or 15 turn-buckles shall provide 38 mm (1‑1/2 inches) minimum of adjustment and incorporate locknuts. All-thread rods are acceptable.
    4. Hangers Supporting Multiple Pipes (Trapeze Hangers): Galvanized, cold formed, lipped steel channel horizontal member, not less than 41 by 41 mm (1‑5/8 by 1‑5/8 inches), 2.7 mm (12 gauge), designed to accept special spring held, hardened steel nuts. Trapeze hangers are prohibited for use for steam supply and condensate piping.
       1. Allowable Hanger Load: Manufacturers rating less 91 kg (200 pounds).
       2. Guide individual pipes on the horizontal member of every other trapeze hanger with 6 mm (1/4 inch) U-bolt fabricated from steel rod. Provide Type 40 insulation shield, secured by two 13 mm (1/2 inch) galvanized steel bands, or preinsulated calcium silicate shield for insulated piping at each hanger.
    5. Supports for Piping Systems:
       1. Select hangers sized to encircle insulation on insulated piping. Refer to Section 23 07 11, HVAC AND BOILER PLANT INSULATION for insulation thickness. To protect insulation, provide Type 39 saddles for roller type supports or preinsulated calcium silicate shields. Provide Type 40 insulation shield or preinsulated calcium silicate shield at all other types of supports and hangers including those for preinsulated piping.
       2. Piping Systems Except High and Medium Pressure Steam (MSS SP-58):
          1. Standard Clevis Hanger: Type 1; provide locknut.
          2. Riser Clamps: Type 8.
          3. Wall Brackets: Types 31, 32 or 33.
          4. Roller Supports: Type 41, 43, 44 and 46.
          5. Saddle Support: Type 36, 37 or 38.
          6. Turnbuckle: Types 13 or 15. Preinsulate.
          7. U-bolt Clamp: Type 24.
          8. Copper Tube:

Hangers, clamps and other support material in contact with tubing shall be painted with copper colored epoxy paint, plastic coated or taped with non-adhesive isolation tape to prevent electrolysis.

For vertical runs use epoxy painted or plastic-coated riser clamps.

For Supporting Tube to Strut: Provide epoxy painted pipe straps for copper tube or plastic inserted vibration isolation clamps.

Insulated Lines: Provide pre-insulated calcium silicate shields sized for copper tube.

* + - * 1. Supports for Plastic Piping: As recommended by the pipe manufacturer with black rubber tape extending one inch beyond steel support or clamp.
      1. High and Medium Pressure Steam (MSS SP-58):
         1. Provide eye rod or Type 17 eye nut near the upper attachment.
         2. Piping 50 mm (2 inches) and Greater: Type 43 roller hanger. //For roller hangers requiring seismic bracing provide a Type 1 clevis hanger with Type 41 roller attached by flat side bars.//
         3. //Piping with Vertical Expansion and Contraction:

Movement Up To 19 mm (3/4 inch): Type 51 or 52 variable spring unit with integral turn buckle and load indicator.

Movement More Than 19 mm (3/4 inch): Type 54 or 55 constant support unit with integral adjusting nut, turn buckle and travel position indicator.//

* + - 1. Convertor and Expansion Tank Hangers: May be Type 1 sized for the shell diameter. Insulation where required will cover the hangers.

SPEC WRITER NOTE: Include paragraph below for pipe sizes greater than 50 mm (2 inches).

* + 1. //Pre-Insulated Calcium Silicate Shields:
       1. Provide 360-degree water resistant high density 965 kPa (140 psig) compressive strength calcium silicate shields encased in galvanized metal.
       2. Pre-insulated calcium silicate shields to be installed at the point of support during erection.
       3. Shield thickness shall match the pipe insulation.
       4. The type of shield is selected by the temperature of the pipe, the load it must carry, and the type of support it will be used with.
          1. Shields for supporting chilled or cold water shall have insulation that extends a minimum of 25 mm (1 inch) past the sheet metal. Provide for an adequate vapor barrier in chilled lines.
          2. The pre-insulated calcium silicate shield shall support the maximum allowable water filled span as indicated in MSS SP-58. To support the load, the shields may have one or more of the following features: structural inserts 4138 kPa (600 psig) compressive strength, an extra bottom metal shield, or formed structural steel (ASTM A36/A36M) wear plates welded to the bottom sheet metal jacket.
       5. Shields may be used on steel clevis hanger type supports, roller supports or flat surfaces.//
    2. //Seismic Restraint and Bracing of Piping and Ductwork: Refer to Section 13 05 41, SEISMIC RESTRAINT REQUIREMENTS FOR NON-STRUCTURAL COMPONENTS. Comply with MSS SP-127. Refer to Seismic Design Requirements VA Handbook 18-8.//
  1. PIPE PENETRATIONS
     1. Install sleeves during construction for other than blocked out floor openings for risers in mechanical bays.
     2. To prevent accidental liquid spills from passing to a lower level, provide the following:
        1. For Sleeves: Extend sleeve 25 mm (1 inch) above finished floor and provide sealant for watertight joint.
        2. For Blocked Out Floor Openings: Provide 38 mm (1‑1/2 inch) angle set in silicone adhesive around opening.
        3. For Drilled Penetrations: Provide 38 mm (1‑1/2 inch) angle ring or square set in silicone adhesive around penetration.
     3. Penetrations through beams or ribs are prohibited but may be installed in concrete beam flanges. Any deviation from these requirements shall receive prior approval of COR.
     4. Sheet Metal, Plastic, or Moisture-Resistant Fiber Sleeves: Provide for pipe passing through floors, interior walls, and partitions, unless brass or steel pipe sleeves are specifically called for below.
     5. Cast-Iron or Zinc Coated Pipe Sleeves: Provide for pipe passing through exterior walls below grade. Make space between sleeve and pipe watertight with a modular or link rubber seal. Seal shall be applied at both ends of sleeve.
     6. Galvanized Steel or an Alternate Black Iron Pipe with Asphalt Coating Sleeves: Provide for pipe passing through concrete beam flanges, except where brass pipe sleeves are called for. Provide sleeve for pipe passing through floor of mechanical rooms, laundry work rooms, and animal rooms above basement. Except in mechanical rooms, connect sleeve with floor plate.
     7. Brass Pipe Sleeves: Provide for pipe passing through quarry tile, terrazzo or ceramic tile floors. Connect sleeve with floor plate.
     8. Sleeves are not required for wall hydrants for fire department connections or in drywall construction.
     9. Sleeve Clearance: Sleeve through floors, walls, partitions, and beam flanges shall be one inch greater in diameter than external diameter of pipe. Sleeve for pipe with insulation shall be large enough to accommodate the insulation. Interior openings shall be caulked tight with fire stopping material and sealant to prevent the spread of fire, smoke, and gases.
     10. Sealant and Adhesives: Shall be as specified in Section 07 92 00, JOINT SEALANTS.
  2. DUCT PENETRATIONS
     1. Provide curbs for roof mounted piping, ductwork and equipment. Curbs shall be 457 mm (18 inches) high with continuously welded seams, built-in cant strip, interior baffle with acoustic insulation, curb bottom, hinged curb adapter.
     2. Provide firestopping for openings through fire and smoke barriers, maintaining minimum required rating of floor, ceiling or wall assembly. See section 07 84 00, FIRESTOPPING.
  3. SPECIAL TOOLS AND LUBRICANTS
     1. Furnish, and turn over to the COR, tools not readily available commercially, that are required for disassembly or adjustment of equipment and machinery furnished.
     2. Grease Guns with Attachments for Applicable Fittings: One for each type of grease required for each motor or other equipment.
     3. Refrigerant Tools: Provide system charging/Evacuation equipment, gauges, fittings, and tools required for maintenance of furnished equipment.
     4. Tool Containers: Hardwood or metal, permanently identified for intended service and mounted, or located, where directed by the COR.
     5. Lubricants: A minimum of 0.95 L (1 quart) of oil, and 0.45 kg (1 pound) of grease, of equipment manufacturer's recommended grade and type, in unopened containers and properly identified as to use for each different application.
  4. WALL, FLOOR AND CEILING PLATES

SPEC WRITER NOTE: Coordinate penetration details with Architect and Fire Protection Engineer.

* + 1. Material and Type: Chrome plated brass or chrome plated steel, one piece or split type with concealed hinge, with set screw for fastening to pipe, or sleeve. Use plates that fit tight around pipes, cover openings around pipes and cover the entire pipe sleeve projection.
    2. Thickness: Not less than 2.4 mm (3/32 inch) for floor plates. For wall and ceiling plates, not less than 0.64 mm (0.025 inch) for up to 75 mm (3 inch pipe), 0.89 mm (0.035 inch) for larger pipe.
    3. Locations: Use where pipe penetrates floors, walls and ceilings in exposed locations, in finished areas only. Provide a watertight joint in spaces where brass or steel pipe sleeves are specified.
  1. ASBESTOS
     1. Materials containing asbestos are prohibited.

1. EXECUTION
   1. GENERAL
      1. If an installation is unsatisfactory to the COR, the Contractor shall correct the installation at no additional cost or time to the Government.
   2. ARRANGEMENT AND INSTALLATION OF EQUIPMENT AND PIPING
      1. Location of piping, sleeves, inserts, hangers, and equipment, access provisions shall be coordinated with the work of all trades. The coordination/shop drawings shall be submitted for review. Locate piping, sleeves, inserts, hangers, ductwork and equipment clear of windows, doors, openings, light outlets, and other services and utilities. Equipment coordination/shop drawings shall be prepared to coordinate proper location and personnel access of all facilities. The drawings shall be submitted for review. Follow manufacturer's published recommendations for installation methods not otherwise specified.
      2. Operating Personnel Access and Observation Provisions: Select and arrange all equipment and systems to provide clear view and easy access, without use of portable ladders, for maintenance and operation of all devices including, but not limited to, all equipment items, valves, filters, strainers, transmitters, sensors, control devices. All gauges and indicators shall be clearly visible by personnel standing on the floor or on permanent platforms. Do not reduce or change maintenance and operating space and access provisions that are shown in the contract documents.
      3. Equipment and Piping Support: Coordinate structural systems necessary for pipe and equipment support with pipe and equipment locations to permit proper installation.
      4. Location of pipe sleeves, trenches and chases shall be accurately coordinated with equipment and piping locations.
      5. Cutting Holes:
         1. Cut holes through concrete and masonry by rotary core drill. Pneumatic hammer, impact electric, and hand or manual hammer type drill is prohibited, except as permitted by COR where working area space is limited.
         2. Locate holes to avoid interference with structural members such as slabs, columns, ribs, beams or reinforcing. Holes shall be laid out in advance and drilling done only after approval by COR. If the Contractor considers it necessary to drill through structural members, this matter shall be referred to COR for approval.
         3. Do not penetrate membrane waterproofing.
      6. Minor Piping: Generally, small diameter pipe runs from drips and drains, water cooling, and other service are not shown but shall be provided.
      7. Electrical Interconnection of Instrumentation or Controls: This generally not shown but shall be provided. This includes interconnections of sensors, transmitters, transducers, control devices, control and instrumentation panels, instruments and computer workstations. Devices shall be located so they are easily accessible for testing, maintenance, calibration, etc. The COR has the final determination on what is accessible and what is not. Comply with NFPA 70.
      8. Protection and Cleaning:
         1. Equipment and materials shall be carefully handled, properly stored, and adequately protected to prevent damage before and during installation, in accordance with the manufacturer's recommendations and as approved by the COR. Damaged or defective items in the opinion of the COR, shall be replaced.
         2. Protect all finished parts of equipment, such as shafts and bearings where accessible, from rust prior to operation by means of protective grease coating and wrapping. Close pipe openings with caps or plugs during installation. Tightly cover and protect fixtures and equipment against dirt, water chemical, or mechanical injury. At completion of all work thoroughly clean fixtures, exposed materials and equipment.
      9. Concrete and Grout: Use concrete and non-shrink grout 20 MPa (3000 psig) minimum, specified in Section 03 30 00, CAST-IN-PLACE CONCRETE.
      10. Install gauges, thermometers, valves and other devices with due regard for ease in reading or operating and maintaining said devices. Locate and position thermometers and gauges to be easily read by operator or staff standing on floor or walkway provided. Servicing shall not require dismantling adjacent equipment or pipe work.
      11. Install steam piping expansion joints as per manufacturer’s recommendations.
      12. Work in Existing Building:
          1. Perform as specified in paragraphs OPERATIONS AND STORAGE AREAS, paragraph ALTERATIONS, and paragraph RESTORATION of the Section 01 00 00, GENERAL REQUIREMENTS for relocation of existing equipment, alterations and restoration of existing building(s).
          2. As specified in Section 01 00 00, GENERAL REQUIREMENTS, paragraph OPERATIONS AND STORAGE AREAS, make alterations to existing service piping at times that will least interfere with normal operation of the facility.
      13. Work in Animal Research Areas: Seal all pipe and duct penetrations with silicone sealant to prevent entrance of insects.
      14. Switchgear/Electrical Equipment Drip Protection: Every effort shall be made to eliminate the installation of pipe above electrical and data/telephone switchgear. If this is not possible, encase pipe in a second pipe with a minimum of joints. Installation of piping, ductwork, leak protection apparatus or other installations foreign to the electrical installation shall not be located in the space equal to the width and depth of the equipment and extending from to a height of 1.8 m (6 feet) above the equipment or to ceiling structure, whichever is lower (NFPA 70).
      15. Inaccessible Equipment:
          1. Where the Government determines that the Contractor has installed equipment not conveniently accessible for operation and maintenance or inspections, equipment shall be removed and reinstalled or remedial action performed as directed at no additional cost or time to the Government.
          2. The term "conveniently accessible" is defined as capable of being reached without the use of ladders, or without climbing or crawling under or over obstacles such as, but not limited to motors, fans, pumps, belt guards, transformers, high voltage lines, conduit and raceways, piping, hot surfaces, and ductwork. The COR has final determination on whether an installation meets this requirement or not.
   3. TEMPORARY PIPING AND EQUIPMENT
      1. Continuity of operation of existing facilities will generally require temporary installation or relocation of equipment, ducts, and piping.
      2. The Contractor shall provide all required facilities in accordance with the requirements of phased construction and maintenance of service. All piping and equipment shall be properly supported, sloped to drain, operate without excessive stress, and shall be insulated where injury can occur to personnel by contact with operating facilities. The requirements of paragraph ARRANGEMENT AND INSTALLATION OF EQUIPMENT AND PIPING apply.
      3. Temporary facilities and piping shall be completely removed and any openings in structures sealed. Provide necessary blind flanges and caps to seal open piping remaining in service.
   4. RIGGING
      1. Design is based on application of available equipment. Openings in building structures are planned to accommodate design scheme.
      2. Alternative methods of equipment delivery may be offered by Contractor and will be considered by Government under specified restrictions of phasing and maintenance of service requirements as well as structural integrity of the building.
      3. Close all openings in the building when not required for rigging operations to maintain proper environment in the facility for Government operation and maintenance of service.
      4. Contractor shall provide all facilities required to deliver specified equipment and place on foundations. Attachments to structures for rigging purposes and support of equipment on structures shall be Contractor's full responsibility. Upon request, the Government will check structure adequacy and advise Contractor of recommended restrictions.
      5. Contractor shall check all clearances, weight limitations and shall offer a rigging plan designed by a Registered Professional Engineer. All modifications to structures, including reinforcement thereof, shall be at Contractor's cost, time and responsibility.
      6. Follow approved rigging plan.
      7. Restore building to original condition upon completion of rigging work.
   5. PIPE AND EQUIPMENT SUPPORTS

SPEC WRITER NOTE: Review the following paragraph with the project structural engineer and confirm that the structural system is adequate for piping and equipment support.

* + 1. Where hanger spacing does not correspond with joist or rib spacing, use structural steel channels designed by a structural engineer, secured directly to joist and rib structure that will correspond to the required hanger spacing, and then suspend the equipment and piping from the channels. Drill or burn holes in structural steel only with the prior approval of the COR.
    2. Use of chain pipe supports; wire or strap hangers; wood for blocking, stays and bracing; or, hangers suspended from piping above are prohibited. Replace or thoroughly clean rusty products and paint with zinc primer.
    3. Hanger rods shall be used that are straight and vertical. Turnbuckles for vertical adjustments may be omitted where limited space prevents use. Provide a minimum of 13 mm (1/2 inch) clearance between pipe or piping covering and adjacent work.
    4. HVAC Horizontal Pipe Support Spacing: Refer to MSS SP-58. Provide additional supports at valves, strainers, inline pumps and other heavy components. Provide a support within one foot of each elbow.
    5. HVAC Vertical Pipe Supports:
       1. Up to 152 mm (6 inch pipe), 9 m (30 feet) long, bolt riser clamps to the pipe below couplings, or welded to the pipe and rests supports securely on the building structure.
       2. Vertical pipe larger than the foregoing, support on base elbows or tees, or substantial pipe legs extending to the building structure.

SPEC WRITER NOTE: Ensure the following has been verified by the A/E structural engineer.

* + 1. Overhead Supports:
       1. //The basic structural system of the building is designed to sustain the loads imposed by equipment and piping to be supported overhead.//
       2. Provide steel structural members, in addition to those shown, of adequate capability to support the imposed loads, located in accordance with the final approved layout of equipment and piping.
       3. Tubing and capillary systems shall be supported in channel troughs.
    2. Floor Supports:
       1. Provide concrete bases, concrete anchor blocks and pedestals, and structural steel systems for support of equipment and piping. Concrete bases and structural systems shall be anchored and doweled to resist forces under operating and seismic conditions (if applicable) without excessive displacement or structural failure.
       2. Bases and supports shall not be located and installed until equipment mounted thereon has been approved. Bases shall be sized to match equipment mounted thereon plus 50 mm (2 inch) excess on all edges. Chiller foundations shall have horizontal dimensions that exceed chiller base frame dimensions by at least 152 mm (6 inches) on all sides. Structural contract documents shall be reviewed for additional requirements. Bases shall be neatly finished and smoothed, shall have chamfered edges at the top, and shall be suitable for painting.
       3. All equipment shall be shimmed, leveled, firmly anchored, and grouted with epoxy grout. Anchor bolts shall be placed in sleeves, anchored to the bases. Fill the annular space between sleeves and bolts with a granular material to permit alignment and realignment.
       4. //For seismic anchoring, refer to Section 13 05 41, SEISMIC RESTRAINT REQUIREMENTS FOR NON-STRUCTURAL COMPONENTS.//
  1. MECHANICAL DEMOLITION
     1. Rigging access, other than indicated in the contract documents, shall be provided by the Contractor after approval for structural integrity by the COR. Such access shall be provided without additional cost or time to the Government. Where work is in an operating plant, provide approved protection from dust and debris at all times for the safety of plant personnel and maintenance of plant operation and environment of the plant.
     2. In an operating facility, maintain the operation, cleanliness and safety. Government personnel will be carrying on their normal duties of operating, cleaning and maintaining equipment and plant operation. Confine the work to the immediate area concerned; maintain cleanliness and wet down demolished materials to eliminate dust. Debris accumulated in the area to the detriment of plant operation is prohibited. Perform all flame cutting to maintain the fire safety integrity of this plant. Adequate fire extinguishing facilities shall be available at all times. Perform all work in accordance with recognized fire protection standards. Inspection will be made by personnel of the VAMC, and Contractor shall follow all directives of the COR with regard to rigging, safety, fire safety, and maintenance of operations.
     3. Unless specified otherwise, all piping, wiring, conduit, and other devices associated with the equipment not re-used in the new work shall be completely removed from Government property per Section 01 74 19, CONSTRUCTION WASTE MANAGEMENT. This includes all concrete pads, pipe, valves, fittings, insulation, and all hangers including the top connection and any fastenings to building structural systems. All openings shall be sealed after removal of equipment, pipes, ducts, and other penetrations in roof, walls, floors, in an approved manner and in accordance with contract documents where specifically covered. Structural integrity of the building system shall be maintained. Reference shall also be made to the contract documents of the other disciplines in the project for additional facilities to be demolished or handled.

SPEC WRITER NOTE: Coordinate and identify salvage equipment to be retained by the Government.

* + 1. All indicated valves including gate, globe, ball, butterfly and check, all pressure gauges and thermometers with wells shall remain Government property and shall be removed and delivered to COR and stored as directed. The Contractor shall remove all other material and equipment, devices and demolition debris under these contract documents. Such material shall be removed from Government property expeditiously and shall not be allowed to accumulate.

SPEC WRITER NOTE: Delete the following paragraph if there is no asbestos removal.

* + 1. //Asbestos Insulation Removal: Conform to Section 02 82 11, TRADITIONAL ASBESTOS ABATEMENT.//
  1. CLEANING AND PAINTING
     1. Prior to final inspection and acceptance of the plant and facilities for beneficial use by the Government, the plant facilities, equipment and systems shall be thoroughly cleaned and painted. Refer to Section 09 91 00, PAINTING.
     2. In addition, the following special conditions apply:
        1. Cleaning shall be thorough. Solvents, cleaning materials and methods recommended by the manufacturers shall be used for the specific tasks. All rust shall be removed prior to painting and from surfaces to remain unpainted. Repair scratches, scuffs, and abrasions prior to applying prime and finish coats.
        2. The following material and equipment shall not be painted:
           1. Motors, controllers, control switches, and safety switches.
           2. Control and interlock devices.
           3. Regulators.
           4. Pressure reducing valves.
           5. Control valves and thermostatic elements.
           6. Lubrication devices and grease fittings.
           7. Copper, brass, aluminum, stainless-steel and bronze surfaces.
           8. Valve stems and rotating shafts.
           9. Pressure gauges and thermometers.
           10. Glass.
           11. Nameplates.
        3. Control and instrument panels shall be cleaned, damaged surfaces repaired, and shall be touched-up with matching paint obtained from panel manufacturer.
        4. Pumps, fans, motors, steel and cast-iron bases, and coupling guards shall be cleaned, and shall be touched-up with the same paint type and color as utilized by the pump and fan manufacturer.
        5. Temporary Facilities: Apply paint to surfaces that do not have existing finish coats. This may include painting exposed metals where hangers were removed or where equipment was moved or removed.
        6. Paint shall withstand the following temperatures without peeling or discoloration:
           1. Condensate and Feedwater: 38 degrees C (100 degrees F) on insulation jacket surface and 121 degrees C (250 degrees F) on metal pipe surface.
           2. Steam: 52 degrees C (125 degrees F) on insulation jacket surface and 190 degrees C (374 degrees F) on metal pipe surface.
        7. Final result shall be smooth, even-colored, even-textured factory finish on all items. Completely repaint the entire piece of equipment if necessary to achieve this.
        8. Lead based paints are prohibited.
  2. IDENTIFICATION SIGNS
     1. Provide laminated plastic signs, with engraved lettering not less than 5 mm (3/16 inch) high, designating functions, for all equipment, switches, motor controllers, relays, meters, control devices, including automatic control valves. Nomenclature and identification symbols shall correspond to that used in maintenance manual, and in diagrams specified elsewhere. Attach by chain, adhesive, or screws.
     2. Factory Built Equipment: Metal plate, securely attached, with name and address of manufacturer, serial number, model number, size, performance.
     3. Pipe Identification: Refer to Section 09 91 00, PAINTING.
     4. Attach ceiling grid label on ceiling grid location directly underneath above ceiling air terminal, control system component, valve, filter unit, fan etc.
  3. MOTOR AND DRIVES
     1. Use synchronous belt drives only on equipment controlled by soft starters or variable frequency drive motor controllers without a bypass contactor. Use V-belt drives on all other applications.
     2. Alignment of V-Belt Drives: Set driving and driven shafts parallel and align so that the corresponding grooves are in the same plane.
     3. Alignment of Synchronous Belt Drives: Set driving and driven shafts parallel and align so that the corresponding pulley flanges are in the same plane.
     4. Alignment of Direct-Connect Drives: Securely mount motor in accurate alignment so that shafts are per coupling manufacturer’s tolerances when both motor and driven machine are operating at normal temperatures.
  4. LUBRICATION
     1. All equipment and devices requiring lubrication shall be lubricated prior to initial operation. Field-check all devices for proper lubrication.
     2. All devices and equipment shall be equipped with required lubrication fittings or devices. A minimum of 0.95 liter (1 quart) of oil and 0.45 kg (1 pound) of grease of manufacturer's recommended grade and type for each different application shall be provided; also provide 12 grease sticks for lubricated plug valves. Deliver all materials to COR in unopened containers that are properly identified as to application.
     3. All lubrication points shall be accessible without disassembling equipment, except to remove access plates.
     4. All lubrication points shall be extended to one side of the equipment.
  5. STARTUP, TEMPORARY OPERATION AND TESTING
     1. Perform tests as recommended by product manufacturer and listed standards and under actual or simulated operating conditions and prove full compliance with design and specified requirements. Tests of the various items of equipment shall be performed simultaneously with the system of which each item is an integral part.
     2. When any defects are detected, correct defects and repeat test at no additional cost or time to the Government.
     3. //The CxA will observe startup and Contractor testing of selected equipment. Coordinate the startup and Contractor testing schedules with COR and CxA. Provide a minimum notice of 10 working days prior to startup and testing.//
     4. Startup of equipment shall be performed as described in equipment specifications. Vibration within specified tolerance shall be verified prior to extended operation. Temporary use of equipment is specified in Section 01 00 00, GENERAL REQUIREMENTS, paragraph TEMPORARY USE OF MECHANICAL AND ELECTRICAL EQUIPMENT.
  6. OPERATING AND PERFORMANCE TESTS
     1. Prior to the final inspection, perform required tests as specified in Section 01 00 00, GENERAL REQUIREMENTS paragraph TESTS, and in individual Division 23 sections and submit the test reports and records to the COR.
     2. Should evidence of malfunction in any tested system, or piece of equipment or component part thereof, occur during or as a result of tests, make proper corrections, repairs or replacements, and repeat tests at no additional cost or time to the Government.
     3. When completion of certain work or system occurs at a time when final control settings and adjustments cannot be properly made to make performance tests, then conduct such performance tests and finalize control settings for heating systems and for cooling systems respectively during first actual seasonal use of respective systems following completion of work. Rescheduling of these tests shall be requested in writing to COR for approval.
     4. No adjustments shall be made during the acceptance inspection. All adjustments shall have been made by this point.
     5. //Perform tests as required for commissioning provisions in accordance with Section 23 08 00, COMMISSIONING OF HVAC SYSTEMS and Section 01 91 00, GENERAL COMMISSIONING REQUIREMENTS.//
  7. //COMMISSIONING
     1. Provide commissioning documentation in accordance with the requirements of Section 23 08 00, COMMISSIONING OF HVAC SYSTEMS.
     2. Components provided under this section of the specification will be tested as part of a larger system.//
  8. DEMONSTRATION AND TRAINING
     1. Provide services of manufacturer’s technical representative for //4// // // hour//s// to instruct each VA personnel responsible in operation and maintenance of the system.
     2. //Submit training plans and instructor qualifications in accordance with the requirements of Section 23 08 00, COMMISSIONING OF HVAC SYSTEMS.//

‑ ‑ ‑ E N D ‑ ‑ ‑