## Sheet1
|  | 2015-09-29 |  |  | Summary of Selected Characteristics of Fire Extinguishing Clean Agents
Based on information provided by Rolf Jensen & Associates, Inc., 3/2014
A0 | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | T | U | V |  | W | X | Y | Z | B | C
Original Item # | Item # | Agents in Yellow Recommended by RJA |  |  | Min Design Concentration for Class A Fire (MDCA) MDCA vs. NOAEL MDCA vs. LOAEL (See Notes 1 and 2) |  |  |  |  | Min Design Concentration for Class C Fire (MDCC) MDCC vs. NOAEL MDCC vs. LOAEL (See Notes 1 and 2) |  |  |  |  | No Observable Adverse Effects Level (NOAEL) | Lowest Observable Adverse Effects Level (NOAEL) | Application (as determined by RJA evaluation) | Global Warming Potential (See Note 3) | Ozone Depletion Potential (See Note 3) | Atmos-pheric Lifetime |  | Assume 3,000 sf area, 10' ceilings, 70 deg F | Cost, based on assumed volume | Assume 3,000 sf area, 10' ceilings |  |  |  |  | Agents in Yellow Recommended by RJA
|  | Agent | Trade Name | Type | MDCA (%) | MDCA ≤ NOAEL | MDCA > NOAEL | MDCA ≤ LOAEL | MDCA > LOAEL | MDCC (%) | MDCC ≤ NOAEL | MDCC > NOAEL | MDCC ≤ LOAEL | MDCC > LOAEL | NOAEL (%) | LOAEL (%) | (See NFPA 2001, sections 1.5.1.2 and 1.5.1.3, per RJA summary) | GWP (CO2 = 1) | ODP | This is included in determining the GWP (Note 6) | Environ-mental Regulation (See Note 7) | Number Cylinders Req'd | Combined Cost of Agent, Equip, Misc (Note 15) | Agent Calculator from Orr Protection (Note 5a) | Chemical Reactivity (High, Low, Inert) | Corrosive (Yes, No) | Recom-mended by RJA? (Yes, No) | Reasons by RJA for not recommending agent (See Note 20) | Agent | Trade Name
| 1 | CBrF3 | Halon 1301 | Halon | N/A |  |  |  |  | N/A |  |  |  |  | N/A | N/A | N/A | 7140 | 10 | 65 yrs | No New | [7 empty] | CBrF3 | Halon 1301
1 | 2 | FIC-13I1 | CF3I | Iodofluorocarbons (IFC) | 3.8 |  | X |  | X | 4.3 |  | X |  | X | 0.2 | 0.4 | Not suitable for occupied areas | 0.4 | 0 (See Note 4) | 1.8 days | O3 Depleting | Not sold (Note 8) | Not sold (Note 8) |  | High (Note 17) | No | No | A3: Not avail for total flooding sys, A4: Used mainly for aircraft sys E1: Ozone Depletion Potential, H1: Not suitable for occupied areas | FIC-13I1 | CF3I
2 | 3 | FK-5-1-12 | Novec 1230 Sapphire | Perfluorinated ketones (F-ketone) | 5.4 | X |  | X |  | 6.1 | X |  | X |  | 10 | >10.0 | Permissible for normally occupied areas | 1 | 0 | 5 days | Not Regulated | 5 | 59350 | 1,278 lbs in 2 tanks | High (Note 18) | No (Note 12) | Yes |  | FK-5-1-12 | Novec 1230 Sapphire
| 4 | HCFC-124 | HCFC-124 | Hydrochlorofluorocarbon (HCFC) | 7.9 |  | X |  | X | 8.9 |  | X |  | X | 1 | 2.5 | Not suitable for occupied areas | 609 | 0.022 | 6.1 yrs | O3 Depleting No New 2015 | Not sold (Note 8) | Not sold (Note 8) |  | (Note 13) | (Note 13) | No | A1: Not available, E1: Ozone Depletion Potential H1: Not suitable for occupied areas | HCFC-124 | HCFC-124
3 | 5 | HCFC Blend A | NAF S-III | Hydrochlorofluorocarbon (HCFC) | 11.9 |  | X |  | X | 13.4 |  | X |  | X | 10 | >10.0 | Not suitable for occupied areas | 1550 | 0.048 | 11.9 yrs | O3 Depleting No New 2015 | Not sold (Note 8) | Not sold (Note 8) |  | Low | No | No | A1: Not available, H4: Design concentration greater than NOAEL E1: Ozone Depletion Potential, H1: Not suitable for occupied areas | HCFC Blend A | NAF S-III
| 6 | HFC Blend B | Halotron 2 | Hydrofluorocarbon (HFC) | 13.6 |  | X |  | X | 15.3 |  | X |  | X | 5 | 7.5 | Not suitable for occupied areas | 1540 | 0 | 29 yrs | Not Regulated | (Note 9) | (Note 9) |  | Low | No | No | A2: Not readily available, H1: Not suitable for occupied areas N2: Sold primarily in Sweden and Finland | HFC Blend B | Halotron 2
4 | 7 | HFC-125 | FE-25 Ecaro-25 NAF S 125 | Hydrofluorocarbon (HFC) | 10.4 |  | X |  | X | 11.7 |  | X |  | X | 7.5 | 10 | Not suitable for occupied areas | 3500 | 0 | 29 yrs | Not Regulated | 5 | 46850 | 936 lbs in 2 tanks | Low | No | No | H1: Not suitable for occupied areas, H4: Design concentration greater than NOAEL | HFC-125 | FE-25 Ecaro-25 NAF S 125
5 | 8 | HFC-227ea | FM-200 MH227 NAF S 227 | Hydrofluorocarbon (HFC) | 8 | X |  | X |  | 9 | X Note 19 |  | X |  | 9 | 10.5 | Permissible for normally occupied areas | 3220 | 0 | 34.2 yrs | Not Regulated | 4 | 53625 | 1,023 lbs in 2 tanks | Low | No | Yes |  | HFC-227ea | FM-200 MH227 NAF S 227
6 | 9 | HFC-23 | FE-13 | Hydrofluorocarbon (HFC) | 15.5 | X |  | X |  | 17.4 | X |  | X |  | 30 | >30 | Permissible for normally occupied areas | 14800 | 0 | 270 yrs | Not Regulated | 11 | (Note 14) |  | Low | No | No | A2: Not readily available, E2: High Global Warming Potential | HFC-23 | FE-13
7 | 10 | HFC-236fa | FE-36 | Hydrofluorocarbon (HFC) | 7.7 | X |  | X |  | 8.6 | X |  | X |  | 10 | 15 | Permissible for normally occupied areas | 9810 | 0 | 220 yrs | Not Regulated | (Note 10) | (Note 10) |  | Low | No | No | A5: Typically for fire extinguishers or local application systems E2: High Global Warming Potential | HFC-236fa | FE-36
8 | 11 | IG-01 | Argon, Argonfire, Argotec | Inert Gas | 50.4 |  | X | X |  | 56.7 |  | X |  | X | 43 | 52 | Not suitable for occupied areas | 0 | 0 | N/A | Not Regulated | (Note 9) | (Note 9) |  | Chemically Inert | No | No | H2: Not suitable for occupied areas, H5: Design concentration greater than 52% N1: Non-US product | IG-01 | Argon, Argonfire, Argotec
9 | 12 | IG-100 | NN100 | Inert Gas | 37.2 | X |  | X |  | 41.9 | X |  | X |  | 43 | 52 | Permissible for normally occupied areas | 0 | 0 | N/A | Not Regulated | 31 | (Note 11) |  | Chemically Inert | No | No | N1: Non-US product | IG-100 | NN100
10 | 13 | IG-541 | Inergen | Inert Gas | 37.2 | X |  | X |  | 41.9 | X |  | X |  | 43 | 52 | Permissible for normally occupied areas | 0 | 0 | N/A | Not Regulated | 27 | 45800 | 14,580 cf in 34 tanks | Chemically Inert | No | Yes |  | IG-541 | Inergen
11 | 14 | IG-55 | Argonite, Pro lnert | Inert Gas | 42 | X |  | X |  | 47.3 |  | X | X |  | 43 | 52 | Permissible for normally occupied areas | 0 | 0 | N/A | Not Regulated | 50 | (Note 11) | 16,710 cf in 42/30 tanks | Chemically Inert | No | No | A2: Not readily available, H3: Exposure time limited to 3 minutes H4: Design concentration greater than NOAEL | IG-55 | Argonite, Pro lnert
|  | Note 1: Halocarbon systems for spaces that are normally occupied and designed to concentrations up to the NOAEL [see Table 1.5.1.2.1(a)] shall be permitted. | [17 empty] | Note 16: Costs do not include additional infrastructure necessary, such as additional space for cylinders or pressure relief dampers,
|  | The maximum exposure in any case shall not exceed 5 minutes. Ref: NFPA 2001-2012, 1.5.1.2.1(1) | [17 empty] | if necessary (RJA Note 9)
|  | Note 2: Inert gas systems designed to concentrations below 43 percent (corresponding to an oxygen concentration of 12 percent, sea level equivalent of oxygen) | [17 empty] | Note 17: Higher reactivity for FIC-13I1 is a result of its reaction with active metals (RJA Note 18)
|  | shall be permitted where means are provided to limit exposure to no longer than 5 minutes. Ref: NFPA 2001-2012, 1.5.1.3(1) | [17 empty] | Note 18: Higher reactivity for NOVEC 1230 is a result of its reaction with strong bases (RJA Note 7)
|  | Note 3: The impact of HFC emissions from fire protection applications represents less than 0.01 percent of the impact of all greenhouse gas emissions. Ref: NFPA 2001-2012, A.1.6 | [17 empty] | Note 19: For HFC-227ea (FM-200), the Minimum Design Concentration for Class C fires is equal to, but does not exceed, the NOAEL
|  | Note 4: Ozone Depletion Potential for FIC-13I1 might be non-zero if agent is released at altitude high above ground level. Ref: NFPA 2001-2012, Table A.1.6(a) (RJA Note 5) | [17 empty] | Note 20: RJA reasons for not recommending agents:
|  | Note 5: Text in orange is additional information from 10NA8 | [17 empty] | Availability or Use
Note 5a: Some results were provided in cubic feet and some in pounds. Argonite and Pro Inert had different number tanks. http://www.orrprotection.com/agent-calculator/
Note 6: GWP depends on infrared radiation absorption, spectral location of absorbing wavelengths, and atmospheric lifetime (ref: NFPA 2001, A.1.6)
Note 7: No New: No new systems permitted. No New 2015: Cannot be used in new systems beginning in 2015. O3 Depleting: Classified as an ozone depleting substance.
Note 8: Not sold due to non-zero ODP (RJA Note 13).
Note 9: Not suitable for occupied spaces (RJA Notes 14, 16).
|  | Note 10: Only distributed as fire extinguishers or local application systems (RJA Note 15). | [17 empty] | Environment
Note 11: RJA could not obtain vendor pricing (RJA Note 17).
|  | Note 12: Non-corrosive for typical data center fires. | [17 empty] | Hazard
Note 13: Information not provided in RJA summary matrix.
Note 14: High GWP and not readly available (per RJA notes)
Note 15: Costs include installation, testing, engineering, do not include controls (RJA Notes 8, 10)
Note 16: Costs do not include additional infrastructure necessary, such as additional space for cylinders or pressure relief dampers,
|  | if necessary (RJA Note 9) | [17 empty] | Not Domestic
Note 17: Higher reactivity for FIC-13I1 is a result of its reaction with active metals (RJA Note 18)
Note 18: Higher reactivity for NOVEC 1230 is a result of its reaction with strong bases (RJA Note 7)
Note 19: For HFC-227ea (FM-200), the Minimum Design Concentration for Class C fires is equal to, but does not exceed, the NOAEL
Note 20: RJA reasons for not recommending agents:
|  | Availability or Use |  | A1: Not available
A2: Not readily available
A2: Not readily available
A3: Not available for total flooding systems
A4: Used mainly on aircraft systems
A5: Typically available only for fire extinguishers or local application systems
|  | Environment |  | E1: Ozone Depletion Potential
E2: High Global Warming Potential
|  | Hazard |  | H1: Not suitable for occupied areas per NFPA 2001 Section 1.5.1.2
H2: Not suitable for occupied areas per NFPA 2001 Section 1.5.1.3
H3: Exposure limited to 3 minutes per NFPA 2001 Section 1.5.1.3
H4: Design Concentration greater than NOAEL
H5: Design Concentration exceeds 52%
|  | Not Domestic |  | N1: Non-US product
N2: Sold primarily in Sweden and Finland

## Sheet3
Note 20: RJA reasons for not recommending agents:
Availability or Use | A1: Not available
A2: Not readily available
A3: Not available for total flooding systems
A4: Used mainly on aircraft systems
A5: Typically available only for fire extinguishers or local application systems
Environment | E1: Ozone Depletion Potential
E2: High Global Warming Potential
Hazard | H1: Not suitable for occupied areas per NFPA 2001 Section 1.5.1.2
H2: Not suitable for occupied areas per NFPA 2001 Section 1.5.1.3
H3: Exposure limited to 3 minutes per NFPA 2001 Section 1.5.1.3
H4: Design Concentration greater than NOAEL
H5: Design Concentration exceeds 52%
Not Domestic | N1: Non-US product
N2: Sold primarily in Sweden and Finland